## About
SGC 120 Mk II Parameter list
Software Version
The information contained in this parameter list (Revision A) is applicable to software version R18 of the SGC 120 Mk II.
See the SGC 120 Mk II User manual for more information.
Tip: Use the column filters to quickly narrow down parameters.

## Parameter list
Menu | Sub-Menu | Parameter | Value | Data Type | Range | Unit | ToolTips
Module | General | Name for the configuration set. | Profile 1 | string | - | - | Name for the configuration set.
Module | General | Power On Mode | 0 | enum | 0:manual, 1:auto | - | On Power ON, the controller switches to the selected operating mode.
Module | General | Power On Lamp Test | 0 | bool | Enable or Disable | - | If enabled, the controller glows all LEDs for 2 seconds after a power reset.
Module | General | Deep Sleep Mode | 0 | bool | Enable or Disable | - | If enabled, device enters the deep sleep mode when the controller is idle for the set duration
Module | General | Auto-Clear Warning Alarm | 0 | bool | Enable or Disable | - | If enabled, controller auto clears the 'Warning' type alarm, once the condition for the parameter is healthy again.
Module | General | Language | 0 | enum | 0:english, 1:spanish, 2:chinese | - | The display language of the controller can be changed only if controller supports multiple languages.
Module | Display | Contrast | 80 | uint8 | 0 to 100 | % | Sets the contrast of the controller's LCD
Module | Display | Power Save Mode | 0 | bool | Enable or Disable | - | If enabled, the controller switches off the LCD's backlight after a delay, while the engine is off. This delay can be configured in Timers -> General
Module | Display | Filter Enable | 0 | bool | Enable or Disable | - | Filter Enable
Module | Display | Filter Constant | 50 | uint8 | 0 to 99 | - | Set constant value for the filter .
Module | Communication | Communication Mode | 0 | enum | 0:none, 1:modbus | - | Sets a communication mode
Module | Communication | Slave ID | 2 | uint8 | 1 to 247 | - | Sets the slave device identification
Module | Communication | Baud rate | 3 | enum | 0:1200, 1:2400, 2:4800, 3:9600, 4:19200, 5:38400, 6:57600, 7:115200 | bps | Sets the baud rate for the serial communication
Module | Communication | Parity Bit | 0 | enum | 0:none, 1:even, 2:odd | - | Parity setting for the serial communication
Module | Auto Exercise 1 | Auto Exercise | 0 | bool | Enable or Disable | - | If enabled in Auto Mode, the controller executes exerciser mode as per the defined schedule
Module | Auto Exercise 1 | Event Occurrence | 0 | enum | 0:daily, 1:weekly, 2:monthly | - | Configures the frequency of the exerciser event
Module | Auto Exercise 1 | Event Day | 0 | enum | 0:sunday, 1:monday, 2:tuesday, 3:wednesday, 4:thursday, 5:friday, 6:saturday | - | Configures the day on which the event starts, applicable only if the Event Occurrence is Weekly or Monthly
Module | Auto Exercise 1 | Start Time | 1000 | time | - | - | Schedules the time at which the exercise starts on the Event Day For both Event 1 and Event 2 Start Time should not be same.
Module | Auto Exercise 1 | Duration | 1010 | duration | 0 to 99 | - | Time duration for which the genset continues to run in the exercise mode
Module | Auto Exercise 1 | Load Transfer | 0 | bool | Enable or Disable | - | If enabled, the load is on the genset. If disabled, the load transfers to mains if the mains is healthy
Module | Auto Exercise 2 | Auto Exercise | 0 | bool | Enable or Disable | - | If enabled in Auto Mode, the controller executes exerciser mode as per the defined schedule
Module | Auto Exercise 2 | Event Occurrence | 0 | enum | 0:daily, 1:weekly, 2:monthly | - | Configures the frequency of the exerciser event
Module | Auto Exercise 2 | Event Day | 0 | enum | 0:sunday, 1:monday, 2:tuesday, 3:wednesday, 4:thursday, 5:friday, 6:saturday | - | Configures the day on which the event starts, applicable only if the Event Occurrence is Weekly or Monthly
Module | Auto Exercise 2 | Start Time | 1000 | time | - | - | Schedules the time at which the exercise starts on the Event Day For both Event 1 and Event 2 Start Time should not be same
Module | Auto Exercise 2 | Duration | 1010 | duration | 0 to 99 | - | Time duration for which the genset continues to run in the exercise mode
Module | Auto Exercise 2 | Load Transfer | 0 | bool | Enable or Disable | - | If enabled, the load Is on the genset. If disabled, the load transfers to mains if the mains Is healthy
Digital Inputs | Digital Input A | Source | 0 | enum | 0:notused, 1:userconfigureda, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input A | Dig In A | Click here to update Language pack | label | Enable or Disable | - | Dig In A
Digital Inputs | Digital Input A | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input A | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input A | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input A | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input B | Source | 0 | enum | 0:notused, 1:userconfiguredb, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input B | Dig In B | Click here to update Language pack | label | Enable or Disable | - | Dig In B
Digital Inputs | Digital Input B | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input B | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input B | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input B | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input C | Source | 0 | enum | 0:notused, 1:userconfiguredc, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input C | Dig In C | Click here to update Language pack | label | Enable or Disable | - | Dig In C
Digital Inputs | Digital Input C | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input C | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input C | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input C | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input D | Source | 0 | enum | 0:notused, 1:userconfiguredd, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input D | Dig In D | Click here to update Language pack | label | Enable or Disable | - | Dig In D
Digital Inputs | Digital Input D | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input D | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input D | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input D | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input E | Source | 0 | enum | 0:notused, 1:userconfigurede, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input E | Dig In E | Click here to update Language pack | label | Enable or Disable | - | Dig In E
Digital Inputs | Digital Input E | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input E | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input E | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input E | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input F | Source | 0 | enum | 0:notused, 1:userconfiguredf, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input F | Dig In F | Click here to update Language pack | label | Enable or Disable | - | Dig In F
Digital Inputs | Digital Input F | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input F | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input F | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input F | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input G | Source | 0 | enum | 0:notused, 1:userconfiguredg, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input G | Dig In G | Click here to update Language pack | label | Enable or Disable | - | Dig In G
Digital Inputs | Digital Input G | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input G | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input G | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input G | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input H | Source | 0 | enum | 0:notused, 1:userconfiguredh, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input H | Dig In H | Click here to update Language pack | label | Enable or Disable | - | Dig In H
Digital Inputs | Digital Input H | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input H | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input H | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input H | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Inputs | Digital Input I | Source | 0 | enum | 0:notused, 1:userconfiguredi, 2:lowfuellevelswitch, 3:lowlubeoilpressureswitch, 4:highengcoolanttempswitch, 5:lowwaterlevelswitch, 6:emergencyswitch, 7:remotestartstop, 8:simulatestart, 9:simulatestop, 10:simulateauto, 11:closegenopenmainsswitch, 12:closemainsopengenswitch, 13:simulatemains, 14:vbeltbrokenswitch, 15:sourceneutralswitchsignal, 16:regenerationswinhibitsignal, 17:mainscontactorlatched, 18:gensetcontactorlatched, 19:idlemodeenable, 20:alternatenominalswitch, 21:egrdigitalin, 22:optionkohlerecureset, 23:loadtakeover, 24:remotealarmacknowledge, 25:automode, 26:manualmode | - | Select an input source from the list
Digital Inputs | Digital Input I | Dig In I | Click here to update Language pack | label | Enable or Disable | - | Dig In I
Digital Inputs | Digital Input I | Polarity | 0 | enum | 0:closetoactive, 1:opentoactive | - | The input is detected as active depending upon the set configuration (Close/Open) with respect to ground
Digital Inputs | Digital Input I | Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken once input is detected as active
Digital Inputs | Digital Input I | Activation | 3 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the digital input
Digital Inputs | Digital Input I | Activation Delay | 1 | uint8 | 0 to 60 | s | Time duration after which the controller takes the set action, when the input is sensed continuously active
Digital Outputs | Digital Output A | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output A | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Digital Outputs | Digital Output B | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output B | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Digital Outputs | Digital Output C | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output C | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Digital Outputs | Digital Output D | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output D | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Digital Outputs | Digital Output E | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output E | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Digital Outputs | Digital Output F | Source | 0 | enum | 0:disable, 1:sounderalarm, 2:batteryovervolt, 3:batteryundervolt, 4:chargealtshutdown, 5:chargealtwarning, 6:closegencontactor, 7:closemainscontactor, 8:mainsfailure, 9:commonalarm, 10:commonelectricaltrip, 11:commonshutdown, 12:commonwarning, 13:coolingdown, 14:digina, 15:diginb, 16:diginc, 17:digind, 18:digine, 19:diginf, 20:diging, 21:diginh, 22:digini, 23:emergencystop, 24:stopsolenoid, 25:failtostart, 26:failtostop, 27:fuelrelay, 28:genavailable, 29:l1phaseovshutdown, 30:l1phaseuvshutdown, 31:l2phaseovshutdown, 32:l2phaseuvshutdown, 33:l3phaseovshutdown, 34:l3phaseuvshutdown, 35:genovercurrent, 36:highenginecoolanttemp, 37:lowfuellvl, 38:lowlop, 39:mainshighvolt, 40:mainslowvolt, 41:pressureopencircuit, 42:opengencontactor, 43:openmainscontactor, 44:overfreqshutdown, 45:overspeedshutdown, 46:grossoverspeedshutdown, 47:startrelay, 48:tempsensoropencircuit, 49:underfreqshutdown, 50:underspeedshutdown, 51:maintenancedue, 52:stopmode, 53:automode, 54:manualmode, 55:preheatoutput, 56:autofueltransfer, 57:isvpullsignal, 58:isvholdsignal, 59:idlemodeon, 60:coolanttemperaturecontrol, 61:keyswitch, 62:opengenbreakerpulse, 63:closegenbreakerpulse, 64:openmainsbreakerpulse, 65:closemainsbreakerpulse, 66:idlemodeonpulse, 67:idlemodeoffpulse, 68:inducementbuzzer, 69:customlogicout1, 70:customlogicout2, 71:customlogicout3, 72:customlogicout4, 73:customlogicout5, 74:kohlerecupower, 75:louvrecontrol, 76:prelubpump | - | Select an output source from the list
Digital Outputs | Digital Output F | Polarity | 1 | enum | 0:deenergise, 1:energise | - | In energised condition, the output terminal supplies battery voltage due to high side driver topology
Analog Inputs | Analog Input 1 | Use Input As | 5 | enum | 0:notused, 1:digitalinputi, 2:enginecoolanttemperature, 3:fuellevelmonitoring, 4:lubeoilpressure, 5:customsensor | - | Select input as none/analog/digital
Analog Inputs | Analog Input 1 | Sensor Type | 1 | enum | 0:voltagetype, 1:currenttype | -
Analog Inputs | Analog Input 1 | Sensor Curve |  | loadandsavebutton | Enable or Disable | - | Sensor Curve
Analog Inputs | Analog Input 1 | Value(X) | Current(mA) (Min = 4, Max = 20) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 1 | Value(Y) | Value (Min = -3000, Max = 3000) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 1 | X1 | 6 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y1 | -2400.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X2 | 7 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y2 | -1800.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X3 | 9 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y3 | -1200.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X4 | 10 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y4 | -600.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X5 | 12 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y5 | 0.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X6 | 14 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y6 | 600.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X7 | 15 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y7 | 1200.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X8 | 17 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y8 | 1800.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X9 | 18 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y9 | 2400.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | X10 | 20 | float | 0 to 5000 | -
Analog Inputs | Analog Input 1 | Y10 | 3000.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 1 | analoginput1graph |  | graph | Enable or Disable | -
Analog Inputs | Analog Input 2 | Use Input As | 0 | enum | 0:notused, 1:digitalinputg, 2:enginecoolanttemperature, 3:fuellevelmonitoring, 4:lubeoilpressure, 5:customsensor | - | Select input as none/analog/digital
Analog Inputs | Analog Input 2 | Sensor Curve |  | loadandsavebutton | Enable or Disable | - | Sensor Curve
Analog Inputs | Analog Input 2 | Value(X) | (Min = 0, Max = 5000) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 2 | Value(Y) | (Min = 0, Max = 10) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 2 | X1 | 500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y1 | -8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X2 | 1000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y2 | -6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X3 | 1500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y3 | -4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X4 | 2000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y4 | -2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X5 | 2500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y5 | 0.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X6 | 3000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y6 | 2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X7 | 3500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y7 | 4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X8 | 4000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y8 | 6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X9 | 4500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y9 | 8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | X10 | 5000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 2 | Y10 | 10000 | float | 0 to 10 | -
Analog Inputs | Analog Input 2 | analoginput2graph |  | graph | Enable or Disable | -
Analog Inputs | Analog Input 3 | Use Input As | 0 | enum | 0:notused, 1:digitalinputh, 2:enginecoolanttemperature, 3:fuellevelmonitoring, 4:lubeoilpressure, 5:customsensor | - | Select input as none/analog/digital
Analog Inputs | Analog Input 3 | Sensor Type | 0 | enum | 0:resistancetype, 1:voltagetype | -
Analog Inputs | Analog Input 3 | Sensor Curve |  | loadandsavebutton | Enable or Disable | - | Sensor Curve
Analog Inputs | Analog Input 3 | Value(X) | Resistance(Ohm) (Min = 0, Max = 5000) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 3 | Value(Y) | (Min = 0, Max = 10) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 3 | X1 | 500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y1 | -8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X2 | 1000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y2 | -6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X3 | 1500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y3 | -4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X4 | 2000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y4 | -2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X5 | 2500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y5 | 0.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X6 | 3000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y6 | 2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X7 | 3500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y7 | 4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X8 | 4000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y8 | 6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X9 | 4500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y9 | 8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | X10 | 5000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 3 | Y10 | 10000 | float | 0 to 10 | -
Analog Inputs | Analog Input 3 | analoginput3graph |  | graph | Enable or Disable | -
Analog Inputs | Analog Input 4 | Use Input As | 0 | enum | 0:notused, 1:digitalinputf, 2:enginecoolanttemperature, 3:fuellevelmonitoring, 4:lubeoilpressure, 5:customsensor | - | Select input as none/analog/digital
Analog Inputs | Analog Input 4 | Sensor Curve |  | loadandsavebutton | Enable or Disable | - | Sensor Curve
Analog Inputs | Analog Input 4 | Value(X) | (Min = 0, Max = 5000) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 4 | Value(Y) | (Min = 0, Max = 10) | label | Enable or Disable | - | 0
Analog Inputs | Analog Input 4 | X1 | 500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y1 | -8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X2 | 1000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y2 | -6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X3 | 1500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y3 | -4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X4 | 2000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y4 | -2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X5 | 2500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y5 | 0.0 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X6 | 3000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y6 | 2000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X7 | 3500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y7 | 4000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X8 | 4000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y8 | 6000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X9 | 4500 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y9 | 8000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | X10 | 5000 | float | 0 to 5000 | -
Analog Inputs | Analog Input 4 | Y10 | 10000 | float | 0 to 10 | -
Analog Inputs | Analog Input 4 | analoginput4graph |  | graph | Enable or Disable | -
Engine | Crank Disconnect | Start Attempts | 3 | uint8 | 1 to 9 | - | Number of attempts to crank the engine
Engine | Crank Disconnect | Disconnect on Oil Pressure Sensor | 0 | bool | Enable or Disable | - | If enabled, the crank Is disconnected depending on the Lube Oil Pressure sensor set value
Engine | Crank Disconnect | Monitor Pressure Sensor Before Crank | 0 | bool | Enable or Disable | - | If enabled, in case pressure Is detected high before starting the engine, the High Oil Pressure Detected
Engine | Crank Disconnect | Pressure Sensor Monitoring Threshold | 4.0 | float | 0.5 to 10 | bar | The crank Is disconnected, if Lube Oil Pressure Is above the set threshold
Engine | Crank Disconnect | Monitor Pressure Switch Before Crank | 0 | bool | Enable or Disable | - | If enabled, in case pressure switch Is open before starting the engine, the controller raises High Oil Pressure Detected
Engine | Crank Disconnect | Disconnect on Oil Pressure Switch | 0 | bool | Enable or Disable | - | If enabled, in case pressure switch Is active (high pressure) while cranking
Engine | Crank Disconnect | Pressure Switch Transient Time | 1.5 | float | 0 to 3 | s | The controller monitors LLOP switch for the set duration before disconnecting crank
Engine | Crank Disconnect | Crank Disconnect At Alt Frequency | 20 | uint8 | 10 to 70 | Hz | During cranking, if alternator frequency is more than the set threshold, the controller disconnects the crank and declares engine on.
Engine | Crank Disconnect | Crank Disconnect At Engine Speed | 600 | uint16 | 150 to 4000 | RPM | During cranking, if engine RPM is more than the set threshold, the controller disconnects the crank and declares engine on.
Engine | Crank Disconnect | Disconnect On Charging Alt Voltage | 0 | bool | Enable or Disable | - | If enabled, during crank rest time, if the charging alternator voltage Is above the set threshold, the controller disconnects the crank
Engine | Crank Disconnect | Charging Alt Disconnect Volt Threshold | 5.0 | float | 5 to 30 | V | During cranking, if charging alternator voltage is more than the set threshold, then charging alternator is disconnected.
Engine | Preheat | Preheat Timer | 10 | uint16 | 1 to 900 | s | Time for which the preheat output remains active before cranking.
Engine | Preheat | Engine Coolant Temperature | 0 | bool | Enable or Disable | - | If enabled, the controller deactivates the preheat output if the set temperature is reached.
Engine | Preheat | Engine Coolant Temp Threshold | 25 | uint16 | 10 to 300 | °C | Sets the temperature to be achieved during the preheat
Engine | Speed Monitoring | Engine Speed Sense Source | 0 | enum | 0:alternatorfrequency, 1:magneticpickup, 2:wpoint | - | Configures the source from where the engine speed is detected
Engine | Speed Monitoring | Flywheel Teeth / W-point Frequency | 110 | uint16 | 0 to 500 | - | Configures the number of teeth on the engine flywheel
Engine | Speed Monitoring | Under-speed Shutdown | 0 | bool | Enable or Disable | - | If enabled, the controller monitors the engine speed and if it is lower than the set threshold,
Engine | Speed Monitoring | Under-speed Threshold | 90 | uint16 | 10 to 100 | % | Sets the lower threshold for the engine speed
Engine | Speed Monitoring | Under-speed Delay | 3 | uint16 | 1 to 60 | s | The delay for which the controller monitors the engine speed before declaring an under-speed alarm
Engine | Speed Monitoring | Over-speed Threshold | 110 | uint16 | 100 to 200 | % | Sets the upper threshold for the engine speed
Engine | Speed Monitoring | Over-speed Delay | 3 | uint16 | 1 to 20 | s | Time duration for which the controller monitors the engine speed before declaring a over-speed alarm
Engine | Speed Monitoring | Gross Over-speed Threshold | 130 | uint16 | 100 to 200 | % | The percentage value above the set nominal speed which results in an instant engine shutdown action
Engine | Speed Monitoring | Initial Low Speed | 600 | uint16 | 500 to 1800 | RPM | Initial target speed for smoke reduction. It is set lower than the regular operating speed
Engine | Speed Monitoring | Idle to Rated Delay Time | 10 | uint16 | 0 to 1200 | s | Maximum time for idle speed to rated
Engine | Speed Monitoring | Startup Idle Mode Time | 0 | uint16 | 0 to 1200 | s | Time duration for which the engine initially runs at lower speed to cause smoke reduction .
Engine | Speed Monitoring | Stopping Idle Time | 0 | uint16 | 0 to 1200 | s | Time duration for which the engine will run at lower speed in idle mode before shutdown .
Engine | Speed Monitoring | Idle Mode Pulse Time | 2 | uint8 | 0 to 60 | s | Maximum allowable pulse time for idle mode output .
Engine | Battery Monitoring | Low Battery Voltage Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Sets the action to be taken if the battery voltage drops below the set threshold.
Engine | Battery Monitoring | Low Battery Voltage Threshold | 8.0 | float | 8 to 31 | V | Sets the lower threshold for the engine battery voltage
Engine | Battery Monitoring | Low Battery Voltage Delay | 30 | uint16 | 5 to 1800 | s | Time duration for which the controller monitors the battery voltage before declaring a low battery alarm.
Engine | Battery Monitoring | High Battery Voltage Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Sets the action to be taken if the battery voltage rises above the set threshold
Engine | Battery Monitoring | High Battery Voltage Threshold | 15.0 | float | 9 to 32 | V | Sets the upper threshold for the engine battery voltage
Engine | Battery Monitoring | High Battery Voltage Delay | 10 | uint16 | 5 to 1800 | s | Time duration for which the controller monitors the battery voltage before declaring a high battery alarm.
Engine | Lube Oil Pressure | Shutdown | 0 | bool | Enable or Disable | - | If enabled and the oil pressure is detected below the set threshold then the controller raises an alarm.
Engine | Lube Oil Pressure | Shutdown Threshold | 2.0 | float | 0 to 98.8 | bar | If oil pressure is detected below the set threshold then the controller will raise an alarm.
Engine | Lube Oil Pressure | Warning | 0 | bool | Enable or Disable | - | If enabled and oil pressure is detected below the set threshold then the controller raises an alarm.
Engine | Lube Oil Pressure | Warning Threshold | 3.0 | float | 0.2 to 99.0 | bar | If oil pressure is detected below the set threshold then the controller will raise an alarm.
Engine | Lube Oil Pressure | LOP Sensor Reference | 0 | enum | 0:enginebody, 1:batterynegative | - | LOP Sensor Reference
Engine | Lube Oil Pressure | Circuit Fault Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | If enabled , the controller raises an alarm if an open circuit is detected
Engine | Fuel Level Monitoring | Low Fuel Level Shutdown | 0 | bool | Enable or Disable | - | If enabled , the controller shuts down the genset if fuel (%) is detected below the set threshold and raises an alarm
Engine | Fuel Level Monitoring | Shutdown Threshold | 10 | uint8 | 0 to 78 | % | The threshold level below which the controller raises an alarm and shutdown the genset.
Engine | Fuel Level Monitoring | Low Fuel Level Warning | 0 | bool | Enable or Disable | - | If enabled , the controller shuts down the genset if fuel (%) is detected below the set threshold and raises an alarm
Engine | Fuel Level Monitoring | Warning Threshold | 12 | uint8 | 2 to 80 | % | The threshold level below which the controller raises an alarm.
Engine | Fuel Level Monitoring | Fuel Tank Capacity | 100 | uint16 | 2 to 6000 | L | Capacity of the fuel tank in liters.
Engine | Fuel Level Monitoring | Fuel Theft Warning | 0 | bool | Enable or Disable | - | If enabled, the controller raises an alarm for fuel theft.
Engine | Fuel Level Monitoring | Fuel Theft Alarm Threshold | 50 | uint8 | 1 to 100 | %/h | If percentage fuel consumption per hour is greater than the set threshold, the fuel theft alarm is raised in engine off condition.
Engine | Fuel Level Monitoring | Circuit Fault Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | If enabled , the controller raises an alarm if an open circuit is detected
Engine | Fuel Level Monitoring | Fuel Sensor Reference | 0 | enum | 0:enginebody, 1:batterynegative | - | Option to select sensor common reference for fuel sensor.
Engine | Engine Coolant Temperature | Shutdown | 0 | bool | Enable or Disable | - | If enabled and the engine temperature is detected above the set threshold then the controller raises an alarm.
Engine | Engine Coolant Temperature | Shutdown Threshold | 27 | uint16 | 27 to 300 | °C | If engine temperature is detected above the set threshold then the controller will raise an alarm.
Engine | Engine Coolant Temperature | Warning | 0 | bool | Enable or Disable | - | If enabled and the engine temperature is detected above the set threshold then the controller raises an alarm
Engine | Engine Coolant Temperature | Warning Threshold | 25 | uint16 | 25 to 298 | °C | If engine temperature is detected above the set threshold then the controller will raise an alarm.
Engine | Engine Coolant Temperature | Temp. Threshold Type | 1 | enum | 0:lessthanthreshold, 1:greaterthanthreshold | - | The switch to change between Greater than & Less than threshold types.
Engine | Engine Coolant Temperature | Engine Coolant Temp Sensor Reference | 0 | enum | 0:enginebody, 1:batterynegative | - | Engine Coolant Temp Sensor Reference
Engine | Engine Coolant Temperature | Circuit Fault Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | If enabled , the controller raises an alarm if an open circuit is detected
Engine | Coolant Temperature Control | Enable | 0 | bool | Enable or Disable | - | If enable, Coolant Temperature Control can be configured.
Engine | Coolant Temperature Control | Temperature Control | 0 | enum | 0:heatercontrol, 1:coolercontrol | - | Option for selection of temperature control that need to be execute.
Engine | Coolant Temperature Control | ON Threshold | 49 | uint16 | 0 to 250 | °C | If Temperature Control: Cooler Control ON Threshold value is above to set threshold then 'Coolant Temperature Control Output' output will be on
Engine | Coolant Temperature Control | OFF Threshold | 50 | uint16 | 0 to 250 | °C | If Temperature Control: Cooler Control OFF Threshold value is below to set threshold then 'Coolant Temperature Control Output' output will be off
Engine | Charging Alternator | Charging Alternator Fail Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | The controller takes an action in-case a charging alternator coil is disconnected from the controller or shorted to the ground.
Engine | Charging Alternator | Charging Alternator Fail Threshold | 10.0 | float | 0 to 35 | V | Sets the fail threshold for the alternator voltage.
Engine | Charging Alternator | Charging Alternator Fail Delay | 20 | uint16 | 5 to 60 | s | Time duration for which the controller monitors the alternator voltage before declaring the alternator fail alarm.
Engine | Automatic Fuel Transfer | AFT Activation Threshold | 40 | uint8 | 0 to 99 | % | If fuel level is detected below the set threshold then activate the Auto Fuel transfer output.
Engine | Automatic Fuel Transfer | AFT De-activation Threshold | 80 | uint8 | 1 to 100 | % | If fuel level is detected above the set threshold then de-activate the Auto Fuel transfer output.
Engine | Automatic Fuel Transfer | Timeout After Activation | 600 | uint16 | 1 to 1200 | s | After this timeout if the fuel level does not reach the AFT de-activation threshold then SGC raises the AFT Timeout alarm and de-activates AFT output.
Engine | Automatic Fuel Transfer | Monitor AFT From Engine On | 0 | bool | Enable or Disable | - | If enabled SGC monitors the AFT function after engine on.
Engine | Custom Sensor | Custom Sensor 1 Name | Click here to update Language pack | label | Enable or Disable | - | Custom Sensor 1 Name
Engine | Custom Sensor | Shutdown | 0 | bool | Enable or Disable | - | Shutdown
Engine | Custom Sensor | Shutdown Threshold | 2.0 | float | -3000.0 to 3000.0 | - | Shutdown Threshold
Engine | Custom Sensor | Warning | 0 | bool | Enable or Disable | - | Warning
Engine | Custom Sensor | Warning Threshold | 3.0 | float | -3000.0 to 3000.0 | - | Warning Threshold
Engine | Custom Sensor | Threshold Type | 0 | enum | 0:lessthanthreshold, 1:greaterthanthreshold | - | Threshold Type
Engine | Custom Sensor | A1 Sensor Reference | 0 | enum | 0:enginebody, 1:batterynegative | - | A1 Sensor Reference
Engine | Custom Sensor | Activation | 2 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | -
Engine | Custom Sensor | Activation Delay | 1 | uint8 | 0 to 60 | s
Engine | Custom Sensor | Circuit Fault Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Circuit Fault Action
Timers | Cranking | Crank Hold Time | 5 | uint16 | 1 to 255 | s | Time duration for which the starter motor turns on after receiving a start command.
Timers | Cranking | Crank Rest Time | 5 | uint16 | 2 to 60 | s | Time duration between two cranks for which the starter motor remains off.
Timers | Cranking | Manual Start Delay | 3 | uint16 | 0 to 300 | s | Time duration taken by the controller before cranking, when a start command is issued in Manual Mode.
Timers | Cranking | Auto Start Delay | 3 | uint16 | 0 to 43200 | s | Time duration taken by the controller before cranking, when a start command is issued in Auto Mode
Timers | Cranking | Run Coil Time | 1.0 | float | 0 to 900 | s | The timer for the Run Coil is a set point for how long the Run Coil will be activated before cranking the engine. This gives the ECU time to start up before cranking
Timers | Cranking | Louvre Control Time | 1 | uint16 | 0 to 120 | s
Timers | Cranking | Pre-lub Time | 1 | uint16 | 0 to 120 | min
Timers | Start/Stop | Safety Monitoring Delay | 5 | uint16 | 5 to 60 | s | Time duration for which the engine safety parameters (e.g. ,LOP, Eng Temp) are not monitored after the crank disconnect event
Timers | Start/Stop | Warm-Up Delay | 3 | uint16 | 0 to 60 | s | The delay between, (a) the alternator developing healthy voltage and frequency, and (b) the load transferred onto the alternator by suitably actuating the contactors
Timers | Start/Stop | Return To Mains Delay | 5 | uint16 | 0 to 600 | s | Time duration after which the controller latches the mains contactor after detecting the mains is healthy
Timers | Start/Stop | Engine Cooling Time | 5 | uint16 | 0 to 300 | s | Time duration for which engine runs on no-load before shutting off. It is skipped in case of shutdown alarm, emergency stop, repeated stop key input
Timers | Start/Stop | Stop Action Time | 30 | uint16 | 10 to 120 | s | Time duration for which engine executes stop action.
Timers | Start/Stop | Additional Stopping Time | 10 | uint16 | 0 to 120 | s | Additional time duration for which the engine stop action continues when the engine is detected as stopped
Timers | Start/Stop | Load Transfer Delay | 1 | uint16 | 1 to 60 | s | Time duration after which the load transfers on the mains or genset
Timers | General | Power Save Mode Delay | 30 | uint16 | 5 to 1800 | s | Time duration after which the LCD backlight turns off automatically, if the controller is idle
Timers | General | Screen Changeover Time | 3 | uint16 | 0 to 1800 | s | Time duration after which the monitoring screen on the controller auto scrolls, in case of no manual intervention
Timers | General | Deep Sleep Mode Delay | 10 | uint16 | 5 to 1800 | s | Time duration after which the controller enters the deep sleep mode, when the controller is idle
Timers | General | Sounder Alarm Time | 5 | uint16 | 1 to 300 | s | Time duration for which the sounder alarm output is active
Timers | General | Auto Exit Config Mode | 10 | uint16 | 10 to 1800 | s | Time duration for which if the controller is idle, it saves the changes and automatically exits the configuration mode
Timers | General | Inlet shutoff Valve Pull Signal | 0.1 | float | 0.1 to 2 | s | Time duration for which ISV pull output is active
Timers | General | Gen Breaker Pulse Timer | 0.5 | float | 0.1 to 5 | s | Time for which Generator Breaker close/open command will active
Timers | General | Mains Breaker Pulse Timer | 0.5 | float | 0.1 to 5 | s | Time for which Mains Breaker close/open command will active
Timers | General | Breaker feedback Timer | 2.0 | float | 1 to 10 | s | Time within which breaker feedback should recieve after activation of command to avoid trigger
Timers | General | Breaker Close Delay | 2.0 | float | 0.1 to 30 | s | Time delay between two Breaker Close Command
Generator | Alternator Configuration | Alternator Present | 1 | bool | Enable or Disable | - | If configured No, all the generator related parameters are disabled
Generator | Alternator Configuration | Number of Poles | 1 | enum | 0:2, 1:4, 2:6, 3:8 | - | Number of poles on the alternator
Generator | Alternator Configuration | Nominal AC System | 1 | enum | 0:1phl1_n, 1:3phl1_l2_l3_n, 2:splitph_l1_n_l2, 3:splitph_l1_n_l3, 4:2ph3w_l1_l2_n, 5:2ph3w_l1_l3_n, 6:3ph3w_l1_l2_l3 | - | Selection of a single phase or three phase genset
Generator | Alternator Configuration | Min Healthy Voltage | 80 | uint16 | 70 to 100 | % | A threshold above which the genset is considered healthy to enter the warm-up state
Generator | Alternator Configuration | Min Healthy Frequency | 80 | uint16 | 70 to 100 | % | A threshold above which the genset is considered healthy to enter the warm-up state
Generator | Alternator Configuration | Phase Reversal Detection | 0 | bool | Enable or Disable | - | If enabled, the phase sequence other than R-Y-B is considered as phase reversal
Generator | Alternator Configuration | Phase Reversal Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken, if phase reversal is detected
Generator | Alternator Configuration | Auto Generator Breaker Close In Manual | 0 | bool | Enable or Disable | - | If enabled in manual mode, the load automatically gets transferred on the genset while it is running and healthy
Generator | Alternator Configuration | GEN PT Enable | 0 | bool | Enable or Disable | - | Enable Generator Voltage through Potential Transformer
Generator | Alternator Configuration | GEN PT Primary Voltage | 100 | uint16 | 100 to 27000 | - | Generator Voltage Transformer value Primary Side
Generator | Alternator Configuration | GEN PT Secondary Voltage | 100 | uint16 | 100 to 520 | - | Generator Voltage Transformer value Secondary Side
Generator | Nominal Values | Nominal Voltage Ph-N | 231 | label |  | V (phase‑neutral) | Nominal Generator Voltage Value Ph-N
Generator | Nominal Values | Nominal Voltage Ph-Ph | 400 | uint16 | 80 to 27000 | V (phase‑phase) | Nominal Generator Voltage Value Ph-Ph
Generator | Nominal Values | Nominal Frequency | 50.0 | float | 5 to 75 | Hz | Nominal Generator Frequency Value
Generator | Nominal Values | Nominal Load Current | 350 | uint16 | 0 to 8000 | A | Nominal Load Current
Generator | Nominal Values | Nominal Speed | 1500 | uint16 | 100 to 4000 | RPM | Nominal Speed
Generator | Nominal Values | Nominal Power | 200 | uint16 | 1 to 20000 | kW | Nominal Power
Generator | Nominal Values | Alternate Nominal Voltage Ph-N | 231 | label |  | V (phase‑neutral) | Alternate Nominal Generator Voltage Value Ph-N
Generator | Nominal Values | Alternate Nominal Voltage Ph-Ph | 400 | uint16 | 80 to 27000 | V (phase‑phase) | Alternate Nominal Generator Voltage Value Ph-Ph
Generator | Nominal Values | Alternate Nominal Frequency | 60.0 | float | 5 to 75 | Hz | Alternate Nominal Generator Frequency Value
Generator | Nominal Values | Alternate Nominal Load Current | 350 | uint16 | 0 to 8000 | A | Alternate Nominal Load Current
Generator | Nominal Values | Alternate Nominal Speed | 1800 | uint16 | 100 to 4000 | RPM | Alternate Nominal Speed
Generator | Nominal Values | Alternate Nominal Power | 200 | uint16 | 1 to 20000 | kW | Alternate Nominal Power
Generator | Voltage Monitoring | Under-voltage Shutdown | 0 | bool | Enable or Disable | - | If enabled, the controller takes under voltage shutdown action
Generator | Voltage Monitoring | Shutdown Threshold | 80 | uint16 | 10 to 95 | % | The controller takes shutdown action if voltage is below the set threshold
Generator | Voltage Monitoring | Under-Voltage Shutdown Delay | 10.0 | float | 0.1 to 100 | s | Under-Voltage shutdown Delay
Generator | Voltage Monitoring | Under-Voltage Warning | 0 | bool | Enable or Disable | - | If enabled, the controller gives under voltage warning
Generator | Voltage Monitoring | Warning Threshold | 90 | uint16 | 15 to 100 | % | The controller gives warning if voltage is below the set threshold
Generator | Voltage Monitoring | Under-Voltage Warning Delay | 10.0 | float | 0.1 to 100 | s | Under-Voltage Warning Delay
Generator | Voltage Monitoring | Over-voltage Shutdown | 0 | bool | Enable or Disable | - | If enabled, the controller takes over voltage shutdown action
Generator | Voltage Monitoring | Shutdown Threshold | 120 | uint16 | 105 to 200 | % | The controller takes shutdown action if voltage exceeds the set threshold
Generator | Voltage Monitoring | Over-Voltage Shutdown Delay | 10.0 | float | 0.1 to 100 | s | Over-Voltage shutdown Delay
Generator | Voltage Monitoring | Over-voltage Warning | 0 | bool | Enable or Disable | - | If enabled, the controller gives over voltage warning
Generator | Voltage Monitoring | Warning Threshold | 110 | uint16 | 100 to 195 | % | The controller gives warning if voltage exceeds the set threshold
Generator | Voltage Monitoring | Over-Voltage Warning Delay | 10.0 | float | 0.1 to 100 | s | Over-Voltage Warning Delay
Generator | Frequency Monitoring | Under-frequency Shutdown | 0 | bool | Enable or Disable | - | If enabled, the controller takes under frequency shutdown action
Generator | Frequency Monitoring | Shutdown Threshold | 80 | uint16 | 10 to 95 | % | The controller takes shutdown action if frequency is below the set threshold
Generator | Frequency Monitoring | Under-Frequency Shutdown Delay | 10.0 | float | 0.1 to 100 | s | Under-Frequency Shutdown Delay
Generator | Frequency Monitoring | Under-frequency Warning | 0 | bool | Enable or Disable | - | If enabled, the controller gives under frequency warning
Generator | Frequency Monitoring | Warning Threshold | 90 | uint16 | 15 to 100 | % | The controller gives warning if frequency is below the set threshold
Generator | Frequency Monitoring | Under-Frequency Warning Delay | 10.0 | float | 0.1 to 100 | s | Under-Frequency Warning Delay
Generator | Frequency Monitoring | Over-frequency Shutdown | 0 | bool | Enable or Disable | - | If enabled, the controller takes over frequency shutdown action
Generator | Frequency Monitoring | Shutdown Threshold | 120 | uint16 | 105 to 200 | % | The controller takes shutdown action if frequency exceeds the set threshold
Generator | Frequency Monitoring | Over-Frequency Shutdown Delay | 10.0 | float | 0.1 to 100 | s | Over-Frequency Shutdown Delay
Generator | Frequency Monitoring | Over-frequency Warning | 0 | bool | Enable or Disable | - | If enabled, the controller takes over frequency warning
Generator | Frequency Monitoring | Warning Threshold | 110 | uint16 | 100 to 195 | % | The controller gives warning if frequency exceeds the set threshold
Generator | Frequency Monitoring | Over-Frequency Warning Delay | 10.0 | float | 0.1 to 100 | s | Over-Frequency Warning Delay
Generator | Current Monitoring | Primary CT Ratio | 150 | uint16 | 0 to 8000 | - | Current Monitoring Primary CT Ratio
Generator | Current Monitoring | Secondary CT Ratio | 1 | enum | 0:1, 1:5 | - | Current Monitoring Secondary CT Ratio
Generator | Current Monitoring | Over-current Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken by controller when over current is detected
Generator | Current Monitoring | Over-current Threshold | 120 | uint16 | 100 to 200 | % | The controller takes set action if the current exceeds the set threshold
Generator | Current Monitoring | Over-current Delay | 1 | uint16 | 1 to 600 | s | Time duration for which the controller monitors over current before raising an alarm
Generator | Current Monitoring | CT Location | 1 | enum | 0:onaltoutputcable, 1:onloadcable | - | CT Location
Generator | Load Monitoring | Over-load Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken by controller when overload is detected
Generator | Load Monitoring | Over-load Threshold | 110 | uint16 | 100 to 200 | % | The controller takes set action if the load exceeds the set threshold (100 * instantaneous load / Gen kW rating)
Generator | Load Monitoring | Over-load Delay | 1 | uint16 | 1 to 3600 | s | Time duration for which the controller monitors percentage overload before raising an alarm
Generator | Load Monitoring | Unbalanced Load Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken by controller when unbalanced load is detected
Generator | Load Monitoring | Unbalanced Load Threshold | 5 | uint16 | 5 to 200 | % | The unbalanced load event gets triggered when 100*[((max KW from R,Y,B)-(min KW from R,Y,B))/(max KW load allowed per phase assuming 100% rated load)] is greater than this parameter .
Generator | Load Monitoring | Unbalanced Load Delay | 1 | uint16 | 1 to 600 | s | Time duration for which the controller monitors percentage unbalanced load before raising an alarm
Generator | Load Monitoring | Reverse Power Enable | 0 | bool | Enable or Disable | - | Enable Reverse Power Protection (ANSI 32)
Generator | Load Monitoring | Reverse Power Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken when reverse power is detected
Generator | Load Monitoring | Reverse Power Activation | 1 | enum | 0:never, 1:always, 2:frommonitoringon | - | Select intance to start monitoring reverse power
Generator | Load Monitoring | Reverse Power Threshold | -5.0 | float | -200 to -5 | % | Reverse Power Value at which alarm will trigger
Generator | Load Monitoring | Reverse Power Delay | 5 | uint16 | 1 to 100 | s | Time duration for which controller will monitor the threshold value before triggering the alarm
Generator | Load Monitoring | Low Load Enable | 0 | bool | Enable or Disable | - | If enabled, the controller will take low load action if the load is below load tr
Generator | Load Monitoring | Low Load Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Set action to be taken by controller when low load is detected
Generator | Load Monitoring | Low Load Trip | 50 | uint16 | 1 to 99 | - | If load detected is below this threshold, low load action will be taken
Generator | Load Monitoring | Low Load Return | 51 | uint16 | 2 to 100 | % | If load detected rises above this threshold, low load action is configured as warning, the controller will exit low load monitoring
Generator | Load Monitoring | Low Load Delay | 1 | uint16 | 1 to 3600 | s | The duration for which controller monitors the low load before raising an alarm
Mains | Configuration | Mains Monitoring | 1 | bool | Enable or Disable | - | If enabled, the controller monitors mains voltage and frequency
Mains | Configuration | Mains AC System | 1 | enum | 0:1phl1_n, 1:3phl1_l2_l3_n, 2:splitph_l1_n_l2, 3:splitph_l1_n_l3, 4:2ph3w_l1_l2_n, 5:2ph3w_l1_l3_n, 6:3ph3w_l1_l2_l3 | - | Selection of single phase or three phase system
Mains | Configuration | Phase Reversal Detection | 0 | bool | Enable or Disable | - | If enabled, the phase sequence other than R-Y-B is considered as phase reversal
Mains | Configuration | Phase Reversal Action | 0 | enum | 0:none, 1:notification | - | Set action to be taken, if phase reversal is detected
Mains | Configuration | Partial Healthy Detection | 0 | bool | Enable or Disable | - | If enabled, the mains is treated as healthy even if any one of the phase is healthy in case of three phase
Mains | Configuration | Mains PT Enable | 0 | bool | Enable or Disable | - | Enable mains potential transformer setting for voltage measurement .
Mains | Configuration | Mains PT Primary Ratio | 100 | uint16 | 100 to 27000 | - | Mains potential transformer value primary side .
Mains | Configuration | Mains PT Secondary Ratio | 100 | uint16 | 100 to 520 | - | Mains potential transformer value secondary side .
Mains | Configuration | Mains Auto Load Transfer | 0 | bool | Enable or Disable | -
Mains | Configuration | Nominal voltage | 400 | uint16 | 80 to 27000 | V (phase‑phase) | Mains nominal voltage value
Mains | Configuration | Nominal frequency | 50.0 | float | 5 to 75 | Hz | Mains nominal frequency value
Mains | Configuration | Alternate nominal voltage | 400 | uint16 | 80 to 27000 | V (phase‑phase) | Mains alternate nominal voltage value
Mains | Configuration | Alternate nominal frequency | 60.0 | float | 5 to 75 | Hz | Mains alternate nominal frequency
Mains | Voltage Monitoring | Under-voltage | 1 | bool | Enable or Disable | - | If enabled, the controller monitors mains voltage for under voltage condition.
Mains | Voltage Monitoring | Under-Voltage Trip | 80 | uint16 | 10 to 100 | % | If the voltage falls below the set threshold for Mains Detect Delay, then mains is declared unhealthy
Mains | Voltage Monitoring | Under-Voltage Return | 90 | uint16 | 10 to 100 | % | If the voltage rises above the set threshold for Mains Detect Delay, then mains is declared healthy
Mains | Voltage Monitoring | Over-voltage | 1 | bool | Enable or Disable | - | If enabled, the controller monitors mains voltage for over voltage condition
Mains | Voltage Monitoring | Over-Voltage Trip | 120 | uint16 | 100 to 200 | % | If the voltage rises above the set threshold for Mains Detect Delay, then mains is declared unhealthy
Mains | Voltage Monitoring | Over-Voltage Return | 110 | uint16 | 100 to 200 | % | If the voltage falls below the set threshold for Mains Detect Delay, then mains is declared healthy
Mains | Voltage Monitoring | Delay | 10.0 | float | 0.1 to 100 | s | Voltage Trip Delay
Mains | Frequency Monitoring | Under-frequency | 1 | bool | Enable or Disable | - | If enabled, the controller monitors mains under frequency
Mains | Frequency Monitoring | Under-Frequency Trip | 80 | uint16 | 10 to 100 | % | If the frequency falls below the set threshold for Mains Detect Delay, then mains is declared unhealthy
Mains | Frequency Monitoring | Under-Frequency Return | 90 | uint16 | 10 to 100 | % | If the frequency rises above the set threshold for Mains Detect Delay, then mains is declared healthy
Mains | Frequency Monitoring | Over-Frequency | 1 | bool | Enable or Disable | - | If enabled, the controller monitors mains over frequency
Mains | Frequency Monitoring | Over-Frequency Trip | 120 | uint16 | 100 to 200 | % | If the frequency rises above the set threshold for Mains Detect Delay, then mains is declared unhealthy
Mains | Frequency Monitoring | Over-Frequency Return | 110 | uint16 | 100 to 200 | % | If the frequency falls belove the set threshold for Mains Detect Delay, then mains is declared healthy
Mains | Frequency Monitoring | Delay | 10.0 | float | 0.1 to 100 | s | Frequency Trip Delay
ECU Configuration | Engine Control Unit (ECU) | Engine Type | 0 | enum | 0:conventional, 1:genericj1939, 2:scania, 3:volvo1500, 4:volvo1800, 5:iveco, 6:deutzEMR, 7:mtu, 8:kubota, 9:hatz, 10:perkinsADEM4, 11:yuchaiYCGCUECU, 12:cummins, 13:cummins500, 14:cummins558, 15:cummins570, 16:cummins850, 17:cummins2150, 18:cummins2250, 19:DCECcummins, 20:yuchaiBOSCH, 21:doosand18, 22:ddec, 23:scanias8, 24:kohlerkdi3404, 25:boschedc17cv54, 26:scanias8industrial, 27:fptstagev, 28:perkinsstagev, 29:cumminskta19, 30:cumminscm2850, 31:yanmarstagev, 32:volvostagev, 33:volvoems2, 34:mtuj1939, 35:deutz_emr_4, 36:doosan_g2_edc17, 37:fpt_edc17, 38:hatz_edc17, 39:man_edc17, 40:perkins_edc17c49, 41:sdec, 42:steyr_edc17, 43:xichai_gas, 44:yanmar_edc17, 45:yuchai_yc, 46:angle, 47:baudouin_wise15, 48:iveco_cursor, 49:iveco_edc7, 50:iveco_nef, 51:iveco_vector8, 52:cummins_cm2350, 53:cummins_cm2880, 54:cummins_cm2358, 55:ddec_iii, 56:ddec_iv, 57:deutz_emr_2, 58:deutz_emr_3, 59:deutz_emr_5, 60:doosan_md1, 61:kubota_stage_v, 62:mtu_ecu8, 63:mtu_ecu9, 64:caterpillar_adem_4, 65:caterpillar_adem_3, 66:caterpillar_adem_generic, 67:perkins_adem_4, 68:perkins_generic, 69:perkins_stv_1200, 70:perkins_stv_400, 71:volvo_penta_edc_3_1500, 72:volvo_penta_edc_4_1500, 73:volvo_penta_edc_3_1800, 74:volvo_penta_edc_4_1800, 75:volvo_penta_ems_2p3, 76:volvo_penta_ems_2p4, 77:yuchai_diesel, 78:yuchai_gas, 79:volvo_e483_e694_cpcb_iv, 80:generic_cpcb_iv, 81:scania_ems2_s6, 82:baudouin_gas, 83:perkins_cpcb_iv, 84:weichai, 85:johndeere, 86:johndeerestagev, 87:psi, 88:isuzu, 89:kohler, 90:jcb, 91:jcb430448stagev, 92:man, 93:yuchaistagev, 94:perkinsstagev1204j, 95:jichaijc15dweifu, 96:jichaiwys, 97:jichaijc190, 98:jichaijc15tjg, 99:deutzemr5stagev, 100:doosanstagev, 101:weichaie6gas, 102:catadem6, 103:ivecostagev, 104:jingguan, 105:man_emc_step_2p0, 106:man_emc_step_2p5, 107:weichai_gas, 108:baudouin_wise10b, 109:weichai_wise10b, 110:weichai_wise15, 111:boschmd1ce101, 112:motorpal, 113:cumminscm2670, 114:yunnei | - | Select the type of ECU that will communicate with SGC.
ECU Configuration | Engine Control Unit (ECU) | Lube Oil Pressure | 0 | bool | Enable or Disable | - | An option to read and monitor the value of lube oil pressure from ECU.
ECU Configuration | Engine Control Unit (ECU) | Coolant Temperature | 0 | bool | Enable or Disable | - | An option to read and monitor the value of coolant temperature from ECU.
ECU Configuration | Engine Control Unit (ECU) | Engine Speed | 0 | bool | Enable or Disable | - | An option to read and monitor the value of Engine Speed from ECU.
ECU Configuration | Engine Control Unit (ECU) | Running Hours | 0 | bool | Enable or Disable | - | An option to read and monitor the value of Engine Run Hours from ECU.
ECU Configuration | Engine Control Unit (ECU) | Battery Voltage | 0 | bool | Enable or Disable | - | An option to read and monitor the value of Battery Voltage from ECU.
ECU Configuration | Engine Control Unit (ECU) | Speed | 0 | bool | Enable or Disable | - | If enabled, SGC will transmit the set engine requested speed to the ECU.
ECU Configuration | Engine Control Unit (ECU) | Start/Stop | 0 | bool | Enable or Disable | - | If enabled, SGC will transmit the start/stop command to the ECU.
ECU Configuration | Engine Control Unit (ECU) | Preheat | 0 | bool | Enable or Disable | - | If enabled, SGC will take the preheat delay even if the preheat output is not configured.
ECU Configuration | Engine Control Unit (ECU) | Engine Gain | 5.0 | float | 0 to 10 | - | Engine Gain for Cummins Engines.
ECU Configuration | Engine Control Unit (ECU) | Requested Droop | 4.0 | float | 0.0 to 25.0 | % | Requested Droop
ECU Configuration | Engine Control Unit (ECU) | Speed Control | 0 | enum | 0:standardj1939, 1:volvoproprietaryprimaryspeed50hz, 2:volvoproprietaryprimaryspeed60hz | - | Speed Control
ECU Configuration | Engine Control Unit (ECU) | Live Link Enable | 0 | bool | Enable or Disable | - | Live Link Enable
ECU Configuration | Engine Control Unit (ECU) | Remote Display Config | 0 | enum | 0:disable, 1:viewmode, 2:controlmode | -
ECU Configuration | ECU Communication | Action | 2 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken when communication failure alarm is raised.
ECU Configuration | ECU Communication | Activation | 4 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always, 4:whilefuelrelayon | - | Select instance to start monitoring the communication failure.
ECU Configuration | ECU Communication | Activation Delay | 1 | uint16 | 1 to 60 | s | Time duration after which controller takes the set action for communication failure alarm.
ECU Configuration | ECU Communication | SGC Source Address | 3 | uint16 | 0 to 253 | - | Source address of SGC.
ECU Configuration | ECU Communication | ECU Source Address | 0 | uint16 | 0 to 253 | - | Source address of ECU.
ECU Configuration | ECU Communication | Child Source Address | -1 | float | -1 to 253 | -
ECU Configuration | ECU Communication | CAN baud rate | 0 | enum | 0:250, 1:500 | kbps
ECU Configuration | Configurable Source Address | TSC1 Source Address | -1 | float | -1 to 253 | - | 0
ECU Configuration | Configurable Source Address | CM1 Source Address | -1 | float | -1 to 253 | - | 0
ECU Configuration | Configurable Source Address | GC1 Source Address | -1 | float | -1 to 253 | - | 0
ECU Configuration | ECU Diagnostic Lamps | Action | 2 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken when amber lamp alarm is raised.
ECU Configuration | ECU Diagnostic Lamps | Activation | 0 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the amber lamp.
ECU Configuration | ECU Diagnostic Lamps | Activation Delay | 0 | uint16 | 0 to 60 | s | Time duration after which controller takes the set action for amber lamp alarm.
ECU Configuration | ECU Diagnostic Lamps | Action | 2 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken when malfunction lamp alarm is raised.
ECU Configuration | ECU Diagnostic Lamps | Activation | 0 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the malfunction lamp.
ECU Configuration | ECU Diagnostic Lamps | Activation Delay | 0 | uint16 | 0 to 60 | s | Time duration after which controller takes the set action for malfunction lamp alarm.
ECU Configuration | ECU Diagnostic Lamps | Action | 4 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken when red lamp alarm is raised.
ECU Configuration | ECU Diagnostic Lamps | Activation | 0 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the red lamp.
ECU Configuration | ECU Diagnostic Lamps | Activation Delay | 0 | uint16 | 0 to 60 | s | Time duration after which controller takes the set action for red lamp alarm.
ECU Configuration | ECU Diagnostic Lamps | Action | 2 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | Action to be taken when protect lamp alarm is raised.
ECU Configuration | ECU Diagnostic Lamps | Activation | 0 | enum | 0:never, 1:fromenginestart, 2:frommonitoringon, 3:always | - | Select instance to start monitoring the protect lamp.
ECU Configuration | ECU Diagnostic Lamps | Activation Delay | 0 | uint16 | 0 to 60 | s | Time duration after which controller takes the set action for protect lamp alarm.
ECU Configuration | Kohler ECU Reset | Kohler ECU Reset | 0 | bool | Enable or Disable | - | 0
ECU Configuration | Kohler ECU Reset | Kohler ECU Reset Time | 5 | uint16 | 0 to 300 | s | 0
Maintenance | Maintenance | Alarm Action | 0 | enum | 0:none, 1:notification, 2:warning, 3:electricaltrip, 4:shutdown | - | The controller takes a set action if filter maintenance thresholds are reached
Maintenance | Maintenance | Due At Engine Hours | 250 | uint16 | 10 to 65000 | h | Threshold for filter maintenance alarm based on engine run hours
Maintenance | Maintenance | Ash Load Enable | 0 | bool | Enable or Disable | - | Ash Load Enable
Maintenance | Maintenance | Maintenance Alarm By Due Date | 0 | bool | Enable or Disable | - | Maintenance Alarm By Due Date
Maintenance | Maintenance | Set Maintenance Alarm Due Date | 01-01-2017 | date | 01-01-2017 to 31-12-2999 | - | Set Date at which Maintence Alarm will trigger once due
Maintenance | Maintenance | Alarm Due Day | 1 | uint8 | 1 to 31 | - | Alarm Due Day
Maintenance | Maintenance | Alarm Due Month | 1 | uint8 | 1 to 12 | - | Alarm Due Month
Maintenance | Maintenance | Alarm Due Year | 2017 | uint16 | 2017 to 2999 | - | Alarm Due Year