## About
iE 250 Premium Parameter lists
Software version
The information contained in these parameter lists (Revision A) are applicable to software version 2.0.17.x of the iE 250 Premium.
Controller types
This document includes parameter lists for these controller types:
SINGLE genset controller (with GB and MB)
GENSET controller
MAINS controller (with MB and TB)
BUS TIE breaker controller
More information
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
See the iE 250 Premium Designer's handbook for more information.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include I/O functions, and Fieldbus settings. These are not included in the parameter lists.

## SINGLE GENSET
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40030110 | Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40175110 | Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40180110 | Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40185110 | Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
100010002 | Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11200030 | Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
11200040 | Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
11200010 | Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
11200000 | Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
11200100 | Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
11200070 | Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
11200020 | Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
11200090 | Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
11200052 | Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
11200053 | Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000182 | Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
11000183 | Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000184 | Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
11000000 | Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1
11000050 | Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 600 | 1
11000030 | Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 600 | 1
11000040 | Engine > Start sequence > Run coil | During start attempts | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous
11000010 | Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
11000020 | Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 99 | 1
11200060 | Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
11000210 | Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 100 | 0
11000220 | Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 7 |  | 1 | 10 | 0
11000113 | Engine > Start sequence > Start failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000120 | Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 0
11000122 | Engine > Start sequence > Crank failure | Delay | FLOAT | 2 | s | 0 | 20 | 1
11000123 | Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000270 | Engine > Start sequence > Run detection not reached | Run detection not reached | FLOAT | 10 | s | 1 | 1200 | 0
11100000 | Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0
11120000 | Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
11100100 | Engine > Idle run start > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
11100110 | Engine > Idle run start > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
11000060 | Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 0 | 9900 | 0
11000080 | Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 99 | 1
11000102 | Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 10 | 120 | 1
11000103 | Engine > Stop sequence > Stop failure | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000192 | Engine > Stop sequence > Externally stopped | Delay | FLOAT | 10 | s | 1 | 1200 | 0
11000193 | Engine > Stop sequence > Externally stopped | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11110100 | Engine > Idle run stop > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
11110110 | Engine > Idle run stop > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
11000140 | Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
11000141 | Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000142 | Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000143 | Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000150 | Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
11000151 | Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000152 | Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000153 | Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000160 | Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
11000161 | Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000162 | Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000163 | Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000164 | Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
11000170 | Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
11000171 | Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000172 | Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000173 | Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000174 | Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
11001000 | Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
11001001 | Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
11001002 | Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001003 | Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001004 | Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
11001010 | Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
11001011 | Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
11001012 | Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
11001013 | Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001014 | Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
11001020 | Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
11001021 | Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001022 | Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001023 | Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001030 | Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
11001031 | Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001032 | Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001033 | Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001040 | Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
11001041 | Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001042 | Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001043 | Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001050 | Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
11001051 | Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001052 | Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001053 | Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001060 | Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
11001061 | Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001062 | Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001063 | Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001070 | Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
11001071 | Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001072 | Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001073 | Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001080 | Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
11001081 | Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001082 | Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001083 | Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001090 | Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
11001091 | Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001092 | Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001093 | Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40600500 | Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11300330 | Engine > Maintenance > Service timer > Service timer 1 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300333 | Engine > Maintenance > Service timer > Service timer 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300340 | Engine > Maintenance > Service timer > Service timer 2 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300343 | Engine > Maintenance > Service timer > Service timer 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300350 | Engine > Maintenance > Service timer > Service timer 3 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300353 | Engine > Maintenance > Service timer > Service timer 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300360 | Engine > Maintenance > Service timer > Service timer 4 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300363 | Engine > Maintenance > Service timer > Service timer 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
170000610 | Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
11000280 | Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
11000290 | Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
11000300 | Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
11000310 | Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
11800000 | Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
11800010 | Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
11800020 | Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
11800030 | Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
40310000 | Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40310010 | Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40310030 | Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
40500010 | Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
40410130 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
40410140 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0 |  | X
40410150 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2 |  | X
40410160 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2 |  | X
40410102 | Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40410070 | Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40030000 | Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40030020 | Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40030010 | Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40030090 | Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40030070 | Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40030080 | Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40175000 | Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40175020 | Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40175010 | Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40175090 | Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40175070 | Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40175080 | Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40180000 | Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40180020 | Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40180010 | Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40180090 | Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40180070 | Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40180080 | Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40185000 | Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40185020 | Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40185010 | Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40185090 | Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40185070 | Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40185080 | Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
46010010 | Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46010004 | Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Fault ride through active
46010110 | Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
46010101 | Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46010104 | Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Fault ride through active
46000010 | Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000004 | Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
46000110 | Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000104 | Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
46000210 | Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000201 | Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000203 | Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000204 | Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
46020010 | Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46020004 | Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage
46030200 | Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46030204 | Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
46030000 | Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46030100 | Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040000 | Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
46040001 | Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040100 | Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040101 | Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040103 | Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040200 | Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040201 | Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040202 | Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040203 | Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040300 | Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040301 | Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040302 | Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040303 | Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46050000 | Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
46050001 | Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46050003 | Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46050100 | Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
46050101 | Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
46050103 | Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46060000 | Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46060100 | Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
46060101 | Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46070000 | Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
46070001 | Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46070100 | Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
46070101 | Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45300070 | Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46080000 | Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46080100 | Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090000 | Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
46090001 | Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090100 | Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090101 | Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090103 | Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090200 | Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090201 | Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090202 | Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090203 | Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100000 | Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
46100001 | Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100004 | Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46100100 | Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100101 | Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100103 | Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100104 | Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46100200 | Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100201 | Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100202 | Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100203 | Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100204 | Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46110000 | Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
46110001 | Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110100 | Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110101 | Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110103 | Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110200 | Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110201 | Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110203 | Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110300 | Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110301 | Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110302 | Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110303 | Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110400 | Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110401 | Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110402 | Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110403 | Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46120000 | Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
46120001 | Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46120003 | Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46120100 | Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
46120101 | Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120103 | Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46130000 | Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46130100 | Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46140000 | Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
46140001 | Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140003 | Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46140100 | Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140101 | Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140103 | Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101070 | Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
45300950 | Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300960 | Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001110 | Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001111 | Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001112 | Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
45001113 | Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101080 | Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
45300970 | Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300980 | Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001120 | Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001121 | Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001122 | Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
45001123 | Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101030 | Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
45301020 | Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001130 | Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
45001131 | Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001132 | Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001133 | Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101040 | Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
45301040 | Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001140 | Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
45001141 | Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001142 | Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001143 | Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40210010 | Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
40300000 | Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40300010 | Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40510030 | Mains > AC setup > Mains power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
86035000 | Mains > AC setup > Connection point voltage measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: External, 2: Analogue input
86035010 | Mains > AC setup > Connection point voltage measurement | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
90800070 | Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
90800000 | Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
90800010 | Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
90800020 | Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
90800030 | Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
90800040 | Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
90800050 | Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
90800060 | Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
90800083 | Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40400000 | Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
90800110 | Mains > AC setup > Voltage and frequency OK | Measurement configuration | INT32 | Phase-phase |  |  |  |  | 0: Phase-phase, 1: Phase-neutral, 2: Phase-phase or phase-neutral
40400070 | Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Mains > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40010000 | Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40010110 | Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40010090 | Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40010100 | Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40010030 | Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40010070 | Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40010080 | Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40160000 | Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40160110 | Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160090 | Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40160100 | Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40160030 | Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40160070 | Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40160080 | Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40165000 | Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40165110 | Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165090 | Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40165100 | Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40165030 | Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40165070 | Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40165080 | Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40170000 | Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40170110 | Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170090 | Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40170100 | Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40170030 | Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40170070 | Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40170080 | Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
46150010 | Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150004 | Mains > Voltage protections > Over-voltage 1 | Inhibit |  | Fault ride through active
46150110 | Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150104 | Mains > Voltage protections > Over-voltage 2 | Inhibit |  | Fault ride through active
46150210 | Mains > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Mains > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Mains > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Mains > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150203 | Mains > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150204 | Mains > Voltage protections > Over-voltage 3 | Inhibit |  | Fault ride through active
46160010 | Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160004 | Mains > Voltage protections > Under-voltage 1 | Inhibit |  | Fault ride through active
46160110 | Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160104 | Mains > Voltage protections > Under-voltage 2 | Inhibit |  | Fault ride through active
46160210 | Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160201 | Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160203 | Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160204 | Mains > Voltage protections > Under-voltage 3 | Inhibit |  | Fault ride through active
46160310 | Mains > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160300 | Mains > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160301 | Mains > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160302 | Mains > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160303 | Mains > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160304 | Mains > Voltage protections > Under-voltage 4 | Inhibit |  | Fault ride through active
46170010 | Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46200200 | Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46200204 | Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
46200000 | Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46200100 | Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180000 | Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180100 | Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180200 | Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180201 | Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180202 | Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180203 | Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190000 | Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190100 | Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190200 | Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190201 | Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190202 | Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190203 | Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190300 | Mains > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190301 | Mains > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190302 | Mains > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190303 | Mains > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101060 | Mains > Additional protections > Vector shift | AC setup | INT32 | Mains |  |  |  |  | 34: Mains, 35: Generator
45300050 | Mains > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
45001020 | Mains > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
45001023 | Mains > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45001024 | Mains > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
45101050 | Mains > Additional protections > ROCOF | AC setup | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
45301100 | Mains > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
45301110 | Mains > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
45301120 | Mains > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
45001012 | Mains > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
45001013 | Mains > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45001014 | Mains > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
70000780 | Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU
70000560 | Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0
70001590 | Regulators > GOV > General configuration > Frequency recovery | Frequency recovery | INT32 | Off |  |  |  |  | 0: Off, 1: Volvo Penta EMS 2.4, 2: Frequency measurement
70001600 | Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery limit | FLOAT | 3 | Hz | 0 | 20 | 1
70001610 | Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery duration | FLOAT | 1 | s | 0 | 10 | 1
90100210 | Regulators > GOV > Regulation set points > Base load | Return mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto
90100310 | Regulators > GOV > Regulation set points > Base load | Base load | INT32 | 0 |  | 0 | 1 | 0
90100320 | Regulators > GOV > Regulation set points > Base load | Set point | FLOAT | 90 | % | 10 | 120 | 0
70200040 | Regulators > GOV > Regulation set points > Active power ramp configuration | Warm up set point | FLOAT | 10 | % | 0.1 | 100 | 1
70200060 | Regulators > GOV > Regulation set points > Active power ramp configuration | Island ramping | INT32 | 0 |  | 0 | 1 | 0
70200100 | Regulators > GOV > Regulation set points > Active power ramp configuration | Enter operation ramp enable | INT32 | 0 |  | 0 | 1 | 0
70200110 | Regulators > GOV > Regulation set points > Active power ramp configuration | Deload ramp enable | INT32 | 0 |  | 0 | 1 | 0
70200120 | Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 2 | INT32 | 0 |  | 0 | 1 | 0
70200130 | Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 3 | INT32 | 0 |  | 0 | 1 | 0
70200140 | Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 4 | INT32 | 0 |  | 0 | 1 | 0
40030120 | Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175120 | Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180120 | Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185120 | Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000100 | Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000110 | Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000120 | Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000130 | Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000140 | Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000150 | Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000160 | Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000180 | Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000190 | Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000200 | Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000040 | Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000050 | Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000060 | Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000070 | Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 0.5 |  | 0 | 60 | 2
70000080 | Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 3 | s | 0 | 60 | 2
70000090 | Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
30000010 | Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000000 | Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2500 | ms | 250 | 32500 | 0
70000010 | Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 500 | ms | 10 | 6500 | 0
70001620 | Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
70000230 | Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000240 | Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000270 | Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000290 | Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000280 | Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000300 | Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000250 | Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000260 | Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000210 | Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000220 | Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
30000000 | Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000520 | Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000522 | Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
70000523 | Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
70000770 | Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Relay, 1: Analogue / Digital AVR
86140010 | Regulators > AVR > General configuration > Limiting type | AVR limiting type | INT32 | Droop curve |  |  |  |  | 0: Off, 1: Droop curve, 2: Capability curve Q
70200090 | Regulators > AVR > Regulation set points > Reactive power operation ramp | Enable ramping | INT32 | Linear |  |  |  |  | 1: Linear, 2: Time constant
70200150 | Regulators > AVR > Regulation set points > Reactive power operation ramp | Time constant | FLOAT | 2 | s | 1 | 30 | 1 |  | X
40030130 | Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175130 | Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180130 | Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185130 | Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000350 | Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000360 | Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000370 | Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000320 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000330 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000340 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000170 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
70000380 | Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000390 | Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000400 | Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
30000030 | Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000020 | Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 500 | ms | 50 | 15000 | 0
70000030 | Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 100 | ms | 10 | 3000 | 0
70001630 | Regulators > AVR > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
70000410 | Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000420 | Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
70000430 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000440 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1
70000470 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1
70000310 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
70000450 | Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000460 | Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
30000020 | Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000530 | Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000532 | Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
70000533 | Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100010 | Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000050 | Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1
3300070 | Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
90100170 | Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
90100200 | Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
20100082 | Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100092 | Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
20100093 | Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
3300090 | Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100052 | Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100042 | Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100062 | Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100072 | Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
20100123 | Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100133 | Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
33000000 | Breakers > Close before excitation > Configuration | Breaker close set point | FLOAT | 400 | RPM | 0 | 4000 | 0
33000010 | Breakers > Close before excitation > Configuration | Timer crank release to AVR on | FLOAT | 5 | s | 0 | 999 | 1
33000020 | Breakers > Close before excitation > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
33000060 | Breakers > Close before excitation > Configuration | Breakers to close | INT32 | Close GB |  |  |  |  | 0: Close GB, 1: Close GB and TB
33000070 | Breakers > Close before excitation > Configuration | Soft-start timer | FLOAT | 5 | s | 0 | 999 | 1
33000080 | Breakers > Close before excitation > Configuration | Minimum RPM for excitation | FLOAT | 1450 | RPM | 0 | 4000 | 0
33000090 | Breakers > Close before excitation > Configuration | Voltage discharge timer for GB close | FLOAT | 5 | s | 1 | 20 | 1
33000100 | Breakers > Close before excitation > Configuration | Maximum rerun voltage for GB close | FLOAT | 30 | % | 30 | 100 | 0
33000110 | Breakers > Close before excitation > Configuration | Excitation control during cooldown | INT32 | Excitation follow U busbar |  |  |  |  | 0: Excitation follow U busbar, 1: Excitation constant ON, 2: Excitation OFF
33000122 | Breakers > Close before excitation > CBE failure | Delay | FLOAT | 5 | s | 0 | 999 | 1
33000123 | Breakers > Close before excitation > CBE failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
33000052 | Breakers > Close before excitation > CBE rerun failure | Delay | FLOAT | 120 | s | 0 | 999 | 1
33000053 | Breakers > Close before excitation > CBE rerun failure | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
25000150 | Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
25000160 | Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
20200010 | Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20200020 | Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20200030 | Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
3310070 | Breakers > Mains breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3310080 | Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3310000 | Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
3310010 | Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
3310020 | Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3310030 | Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3310040 | Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3310050 | Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3310060 | Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20200082 | Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20200083 | Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200092 | Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20200093 | Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
3310090 | Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3310092 | Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3310093 | Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200052 | Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200053 | Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200042 | Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200043 | Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200062 | Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20200063 | Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200072 | Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20200073 | Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
20200123 | Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20200133 | Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000232 | Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
110000233 | Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110002250 | Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
110002260 | Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
110002270 | Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
25000060 | Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
110002210 | Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
110002220 | Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
110002290 | Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
110002300 | Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
110002310 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
110002320 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
40410170 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
40410180 | Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
40410190 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410200 | Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410210 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410220 | Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410230 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
40410250 | Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
40410260 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine, 2: Open MB at ready engine
40410270 | Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
40410280 | Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410290 | Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410300 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
40410310 | Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
90200040 | Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1
90600010 | Local power management > Genset test > Settings | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
90600020 | Local power management > Genset test > Settings | Base load | FLOAT | 80 | % | 1 | 100 | 0
90600030 | Local power management > Genset test > Settings | Mode | INT32 | No mode change |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change, 3: No regulation
90600040 | Local power management > Genset test > Settings | Test time | FLOAT | 300 | s | 0 | 59940 | 0
110002160 | Power management rules > Plant/genset mode > Modes | Genset mode | INT32 | Power management |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over, 6: Power management
150000170 | Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
110000600 | Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
110000610 | Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
110000620 | Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
110000270 | Power management rules > Mains power > Peak shaving | Start generator | FLOAT | 80 | % | 5 | 100 | 0
110000280 | Power management rules > Mains power > Peak shaving | Minimum load | FLOAT | 5 | % | 0 | 100 | 0
110000290 | Power management rules > Mains power > Peak shaving | Stop generator | FLOAT | 60 | % | 0 | 80 | 0
110000370 | Power management rules > Mains power > Peak shaving | Start delay | FLOAT | 10 | s | 0 | 990 | 1
110000380 | Power management rules > Mains power > Peak shaving | Stop delay | FLOAT | 30 | s | 0 | 990 | 1
110000310 | Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
110000320 | Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000340 | Power management rules > Mains power > Common power factor control | Controller settings Q | FLOAT | 0 | % | -100 | 100 | 0
110000350 | Power management rules > Mains power > Common power factor control | Controller settings cos phi or Q | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 3: Superior, 4: Fixed Q
110000510 | Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
110000520 | Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
110000530 | Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
110000540 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
110000550 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000560 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
110000570 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000580 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
110000590 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
150000020 | Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
150000040 | Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
150000032 | Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
150000033 | Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
32000040 | Power management rules > Ground relay > Enable | Ground relay | INT32 | 0 |  | 0 | 1 | 0 |  | X
32000000 | Power management rules > Ground relay > Ground relay configuration | Relay type | INT32 | Continuous |  |  |  |  | 0: Continuous, 1: Pulse | X
32000010 | Power management rules > Ground relay > Ground relay configuration | Close configuration | INT32 | Hz/V OK |  |  |  |  | 0: Hz/V OK, 1: RPM MPU level, 2: RPM EIC level, 3: Start active | X
32000020 | Power management rules > Ground relay > Ground relay configuration | Open configuration | INT32 | After cooldown |  |  |  |  | 0: After cooldown, 1: After extended stop | X
32000050 | Power management rules > Ground relay > Ground relay configuration | RPM level | FLOAT | 1000 | RPM | 0 | 4000 | 0 |  | X
32000032 | Power management rules > Ground relay > Ground relay general failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
32000033 | Power management rules > Ground relay > Ground relay general failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
32000062 | Power management rules > Ground relay > Ground relay open failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
32000063 | Power management rules > Ground relay > Ground relay open failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
32000072 | Power management rules > Ground relay > Ground relay close failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
32000073 | Power management rules > Ground relay > Ground relay close failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
32000082 | Power management rules > Ground relay > Ground relay position failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
32000083 | Power management rules > Ground relay > Ground relay position failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
150100330 | Power management rules > Number of gensets connected > Minimum set 1 | Set point | FLOAT | 1 |  | 0 | 32 | 0
150200330 | Power management rules > Number of gensets connected > Minimum set 2 | Set point | FLOAT | 1 |  | 0 | 32 | 0
153120040 | Power management rules > Number of gensets connected > Automatic start | Multi-start set 1 | INT32 | Auto calculation |  |  |  |  | 0: Auto calculation, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32
153120050 | Power management rules > Number of gensets connected > Automatic start | Multi-start set 2 | INT32 | 16 |  | 0 | 32 | 0 | 0: Auto calculation, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32
153120060 | Power management rules > Number of gensets connected > Selection | Multi-start selection | INT32 | Multi-start set 1 |  |  |  |  | 0: Multi-start set 1, 1: Multi-start set 2
90200000 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
90200010 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0
110000360 | Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0
150100100 | Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA
150100110 | Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100000 | Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
150100010 | Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
150100020 | Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1
150100050 | Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
150100060 | Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
150100070 | Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1
150100120 | Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
150100130 | Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
150100140 | Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1
150100160 | Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
150100180 | Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
150100190 | Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1
150100210 | Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100300 | Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0
150000210 | Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1, 2, 3, 4, 5, 6, 7, 8
110600010 | System power management > Priority > Selection | Method | INT32 | Manual absolute |  |  |  |  | 0: Manual absolute, 1: Total running hours, 2: Fuel optimisation, 3: Manual relative, 4: Running hours relative, 5: Fuel optimisation + running hours | X
110600110 | System power management > Priority > Selection | Transmit | INT32 | Off |  |  |  |  | 0: Off, 2: Running hours | X
110600020 | System power management > Priority > Running hours | Activate priority update | FLOAT | 175 | h | 1 | 20000 | 0 |  | X
110600030 | System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
11500050 | Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11500022 | Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11500023 | Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11500060 | Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11500000 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11500030 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11500010 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11500040 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600050 | Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11600022 | Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11600023 | Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11600060 | Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11600000 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11600030 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600010 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11600040 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700050 | Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11700022 | Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11700023 | Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11700060 | Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11700000 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11700030 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700010 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11700040 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
170000050 | Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
170000060 | Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
170000042 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
170000043 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
190000320 | Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
191000022 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
191000023 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000050 | Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
60000060 | Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
110000300 | Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
60000702 | Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
60000703 | Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60000100 | Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
60000300 | Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000320 | Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000330 | Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000340 | Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000350 | Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000360 | Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
147000042 | System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
147000043 | System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000153 | System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000163 | System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000173 | System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000090 | System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
110000263 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | No regulation |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
110000432 | System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000433 | System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000442 | System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000443 | System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000452 | System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000453 | System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000462 | System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000463 | System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000472 | System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000473 | System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000482 | System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000483 | System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000492 | System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000493 | System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000502 | System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000503 | System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
147000050 | System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
147000060 | System > Plant > Update | Application to broadcast | FLOAT | 1 |  | 1 | 4 | 0 | 1
803000 | System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800001: LC | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86140032 | Grid code > Capability curve > Protections > Import protection | Delay | FLOAT | 1 | s | 0.1 | 300 | 2
86140033 | Grid code > Capability curve > Protections > Import protection | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86140034 | Grid code > Capability curve > Protections > Import protection | Inhibit |  | Engine not running, Generator breaker open, Mains not in parallel
86140042 | Grid code > Capability curve > Protections > Export protection | Delay | FLOAT | 1 | s | 0.1 | 300 | 2
86140043 | Grid code > Capability curve > Protections > Export protection | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86140044 | Grid code > Capability curve > Protections > Export protection | Inhibit |  | Engine not running, Generator breaker open, Mains not in parallel
86140000 | Grid code > Capability curve > Configuration | Capability margin | FLOAT | 95 | % | 0 | 100 | 1
86140020 | Grid code > Capability curve > Configuration | y-axis nominal select | INT32 | Power (P) |  |  |  |  | 0: Apparent power (S), 1: Power (P)
86140050 | Grid code > Capability curve > Engine limit | Enable | INT32 | 1 |  | 0 | 1 | 0
86140060 | Grid code > Capability curve > Engine limit | Set point | INT32 | 100 | % | 0 | 100 | 0
86035020 | Grid code > Remote sensing > Power (P) | Enable | INT32 | 0 |  | 0 | 1 | 0
86035030 | Grid code > Remote sensing > Reactive power (Q) | Enable | INT32 | 0 |  | 0 | 1 | 0
86035040 | Grid code > Remote sensing > Voltage (V) | Enable | INT32 | 0 |  | 0 | 1 | 0
86060200 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Voltage deadband | FLOAT | 0 | % | 0 | 5 | 2
86060210 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Reference voltage at Q=0 | FLOAT | 1 |  | 0.5 | 1.5 | 2
86060220 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Maximum voltage at Q max | FLOAT | 1.04 |  | 0.5 | 1.5 | 2
86060230 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Maximum Q during over-voltage | FLOAT | 0.33 |  | 0 | 0.4 | 2
86060240 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Minimum Q during under-voltage | FLOAT | -0.33 |  | -0.4 | 0 | 2
86060250 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Reference voltage offset value | FLOAT | 0 |  | -0.2 | 0.2 | 3
86060260 | Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
86060400 | Grid code > Reactive power regulation > Variants > Variant C: Q(U) Q-shift | Q/Pnom offset | FLOAT | 0 |  | -0.4 | 0.4 | 2
86060410 | Grid code > Reactive power regulation > Variants > Variant C: Q(U) Q-shift | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
86060600 | Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi set point | FLOAT | 1 |  | 0.9 | 1 | 3
86060610 | Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
86060620 | Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi offset | FLOAT | 0 |  | -0.1 | 0.1 | 3
86060630 | Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
86060800 | Grid code > Reactive power regulation > Variants > Variant E: Q fixed | Q set point | FLOAT | 0 | % | -100 | 100 | 1
86060000 | Grid code > Reactive power regulation > Configuration | Type selection | INT32 | Default |  |  |  |  | 0: Default, 1: Variant A: Q(U) U-shift, 2: Variant B: Q(P) curve, 3: Variant C: Q(U) Q-shift, 4: Variant D: Cos phi fixed, 5: Variant E: Q fixed
86060010 | Grid code > Reactive power regulation > Configuration | Ramp switch timer | FLOAT | 240 | s | 0 | 600 | 0
86060030 | Grid code > Reactive power regulation > Configuration | Limit Q under-excited | INT32 | 0 |  | 0 | 1 | 0
86060040 | Grid code > Reactive power regulation > Configuration | Limit Q over-excited | INT32 | 0 |  | 0 | 1 | 0
86100100 | Grid code > Droop curve > Active power droop > Deadband > Percentage | Low limit | FLOAT | 0.4 | % | 0 | 99.99 | 2 |  | X
86100110 | Grid code > Droop curve > Active power droop > Deadband > Percentage | High limit | FLOAT | 0.4 | % | 0 | 99.99 | 2 |  | X
86100160 | Grid code > Droop curve > Active power droop > Deadband > Frequency | Low limit | FLOAT | 0.2 | Hz | 0 | 62 | 2
86100170 | Grid code > Droop curve > Active power droop > Deadband > Frequency | High limit | FLOAT | 0.2 | Hz | 0 | 62 | 2
86100200 | Grid code > Droop curve > Active power droop > Deadband > Voltage | Low limit | FLOAT | 1.6 | V | 0 | 25000 | 1 |  | X
86100210 | Grid code > Droop curve > Active power droop > Deadband > Voltage | High limit | FLOAT | 1.6 | V | 0 | 25000 | 1 |  | X
86100120 | Grid code > Droop curve > Active power droop > Hysteresis > Percentage | Low limit | FLOAT | 0.5 | % | 0 | 99.99 | 2 |  | X
86100130 | Grid code > Droop curve > Active power droop > Hysteresis > Percentage | High limit | FLOAT | 0.5 | % | 0 | 99.99 | 2 |  | X
86100180 | Grid code > Droop curve > Active power droop > Hysteresis > Frequency | Low limit | FLOAT | 0.25 | Hz | 0 | 62 | 2
86100190 | Grid code > Droop curve > Active power droop > Hysteresis > Frequency | High limit | FLOAT | 0.25 | Hz | 0 | 62 | 2
86100220 | Grid code > Droop curve > Active power droop > Hysteresis > Voltage | Low limit | FLOAT | 2 | V | 0 | 25000 | 1 |  | X
86100230 | Grid code > Droop curve > Active power droop > Hysteresis > Voltage | High limit | FLOAT | 2 | V | 0 | 25000 | 1 |  | X
86100000 | Grid code > Droop curve > Active power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
86100010 | Grid code > Droop curve > Active power droop > Configuration | Dependency | INT32 | Frequency |  |  |  |  | 0: Frequency, 2: Voltage
86100020 | Grid code > Droop curve > Active power droop > Configuration | Calculation method | INT32 | Active power installed |  |  |  |  | 0: Active power momentary, 1: Active power installed
86100030 | Grid code > Droop curve > Active power droop > Configuration | Slope calculation method | INT32 | Absolute |  |  |  |  | 0: Absolute, 1: Percentage
86100080 | Grid code > Droop curve > Active power droop > Active power | Minimum set point | FLOAT | 50 | kW | 0 | 20000 | 0
86100090 | Grid code > Droop curve > Active power droop > Active power | Maximum set point | FLOAT | 1000 | kW | 0 | 20000 | 0
86100040 | Grid code > Droop curve > Active power droop > Slopes | Low percentage | FLOAT | 5 | % | -100 | 100 | 1 |  | X
86100050 | Grid code > Droop curve > Active power droop > Slopes | High percentage | FLOAT | -5 | % | -100 | 100 | 1 |  | X
86100060 | Grid code > Droop curve > Active power droop > Slopes | Low absolute | FLOAT | 96 | kW | -20000 | 20000 | 0
86100070 | Grid code > Droop curve > Active power droop > Slopes | High absolute | FLOAT | -96 | kW | -20000 | 20000 | 0
86100140 | Grid code > Droop curve > Active power droop > Delays | Recovery | FLOAT | 600 | s | 0 | 3600 | 0
86100150 | Grid code > Droop curve > Active power droop > Delays | Ramp 3 activation | FLOAT | 5 | s | 0 | 10 | 1
86120030 | Grid code > Droop curve > Reactive power droop > Slopes > Cos phi | Low value | FLOAT | -0.005 |  | -1 | 1 | 3
86120040 | Grid code > Droop curve > Reactive power droop > Slopes > Cos phi | High value | FLOAT | 0.005 |  | -1 | 1 | 3
86120090 | Grid code > Droop curve > Reactive power droop > Slopes > Reactive power | Low value | FLOAT | 50 | kvar | -20000 | 20000 | 0
86120100 | Grid code > Droop curve > Reactive power droop > Slopes > Reactive power | High value | FLOAT | -50 | kvar | -20000 | 20000 | 0
86120130 | Grid code > Droop curve > Reactive power droop > Deadband > Percentage | Low limit | FLOAT | 2 | % | 0 | 99.99 | 2
86120140 | Grid code > Droop curve > Reactive power droop > Deadband > Percentage | High limit | FLOAT | 2 | % | 0 | 99.99 | 2
86120150 | Grid code > Droop curve > Reactive power droop > Hysteresis > Percentage | Low limit | FLOAT | 2.1 | % | 0 | 99.99 | 2
86120160 | Grid code > Droop curve > Reactive power droop > Hysteresis > Percentage | High limit | FLOAT | 2.1 | % | 0 | 99.99 | 2
86120000 | Grid code > Droop curve > Reactive power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
86120010 | Grid code > Droop curve > Reactive power droop > Configuration | Curve output | INT32 | Cos phi |  |  |  |  | 0: Cos phi, 1: Reactive power
86120020 | Grid code > Droop curve > Reactive power droop > Configuration | Dependency | INT32 | Voltage |  |  |  |  | 0: Voltage, 1: Active power
86120050 | Grid code > Droop curve > Reactive power droop > Cos phi | Minimum value | FLOAT | 0.8 |  | 0.7 | 1 | 2
86120060 | Grid code > Droop curve > Reactive power droop > Cos phi | Minimum direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
86120070 | Grid code > Droop curve > Reactive power droop > Cos phi | Maximum value | FLOAT | 1 |  | 0.7 | 1 | 2
86120080 | Grid code > Droop curve > Reactive power droop > Cos phi | Maximum direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
86120110 | Grid code > Droop curve > Reactive power droop > Reactive power | Minimum set point | FLOAT | 400 | kvar | -20000 | 20000 | 0
86120120 | Grid code > Droop curve > Reactive power droop > Reactive power | Maximum set point | FLOAT | 1000 | kvar | -20000 | 20000 | 0
86040090 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 0: One phase-phase, 1: Two phase-phase, 2: Three phase-phase, 3: Any phase-phase, 4: One phase-neutral, 5: Two phase-neutral, 6: Three phase-neutral, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 9: Symmetrical phase-phase, 10: Asymmetrical phase-phase, 11: Symmetrical asymmetrical any phase-phase, 12: Symmetrical phase-neutral, 13: Asymmetrical phase-neutral, 14: Symmetrical asymmetrical any phase-neutral
86040120 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Recovery threshold | FLOAT | 95 | % | 0 | 100 | 1
86040150 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
86040180 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
86040210 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
86040243 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040244 | Grid code > Fault ride through > Protections > Low voltage ride through 1 | Inhibit |  | Mains not in parallel
86040100 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 0: One phase-phase, 1: Two phase-phase, 2: Three phase-phase, 3: Any phase-phase, 4: One phase-neutral, 5: Two phase-neutral, 6: Three phase-neutral, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 9: Symmetrical phase-phase, 10: Asymmetrical phase-phase, 11: Symmetrical asymmetrical any phase-phase, 12: Symmetrical phase-neutral, 13: Asymmetrical phase-neutral, 14: Symmetrical asymmetrical any phase-neutral
86040130 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Recovery threshold | FLOAT | 95 | % | 0 | 100 | 1
86040160 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
86040190 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
86040220 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
86040253 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040254 | Grid code > Fault ride through > Protections > Low voltage ride through 2 | Inhibit |  | Mains not in parallel
86040110 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 3: Any phase-phase, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 11: Symmetrical asymmetrical any phase-phase, 14: Symmetrical asymmetrical any phase-neutral
86040140 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Recovery threshold | FLOAT | 105 | % | 100 | 130 | 1
86040170 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
86040200 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
86040230 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
86040263 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040264 | Grid code > Fault ride through > Protections > High voltage ride through 1 | Inhibit |  | Mains not in parallel
86040060 | Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
86040273 | Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040274 | Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Inhibit |  | Engine not running, Generator breaker open
86040070 | Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Set point | FLOAT | 90 | % | 0 | 100 | 1
86040283 | Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040284 | Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Inhibit |  | Engine not running, Generator breaker open
86040080 | Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Set point | FLOAT | 110 | % | 100 | 130 | 1
86040293 | Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86040294 | Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Inhibit |  | Engine not running, Generator breaker open
86040410 | Grid code > Fault ride through > Preset all parameters | Preset to | INT32 | [5 empty] | 0: , 1: VDE 2025
86040300 | Grid code > Fault ride through > Suspend regulation | GOV enable | INT32 | 1 |  | 0 | 1 | 0
86040310 | Grid code > Fault ride through > Suspend regulation | GOV timeout | FLOAT | 10 | s | 0 | 120 | 2
86040320 | Grid code > Fault ride through > Suspend regulation | AVR enable | INT32 | 1 |  | 0 | 1 | 0
86040330 | Grid code > Fault ride through > Suspend regulation | AVR timeout | FLOAT | 10 | s | 0 | 120 | 2
86160020 | Grid code > Power feed in management > Contractual limit > Percentage | Contractual limit | FLOAT | 0 | % | 0 | 110 | 1
86160040 | Grid code > Power feed in management > Contractual limit > Percentage | Contractual limit margin | FLOAT | 0 | % | 0 | 100 | 1
86160030 | Grid code > Power feed in management > Contractual limit > Absolute | Contractual limit | FLOAT | 0 | kW | 0 | 900000 | 1 |  | X
86160050 | Grid code > Power feed in management > Contractual limit > Absolute | Contractual limit margin | FLOAT | 0 | kW | 0 | 900000 | 1 |  | X
86165010 | Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Delay | FLOAT | 1.6 | s | 0 | 7200 | 2
86165020 | Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Set point | FLOAT | 90 | % | 0 | 110 | 1
86165030 | Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
86165003 | Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86165004 | Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Inhibit |  | Engine not running, Mains not in parallel
86165050 | Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Delay | FLOAT | 4 | s | 0 | 7200 | 2
86165060 | Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Set point | FLOAT | 15 | % | 0 | 110 | 1
86165070 | Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
86165043 | Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86165044 | Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Inhibit |  | Engine not running, Mains not in parallel
86165090 | Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Delay | FLOAT | 11 | s | 0 | 7200 | 2
86165100 | Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Set point | FLOAT | 5 | % | 0 | 110 | 1
86165110 | Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
86165083 | Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
86165084 | Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Inhibit |  | Engine not running, Mains not in parallel
86160000 | Grid code > Power feed in management > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
86160010 | Grid code > Power feed in management > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
86160060 | Grid code > Power feed in management > Ramp | Curve type | INT32 | Exponential |  |  |  |  | 0: Exponential, 1: Linear
86160070 | Grid code > Power feed in management > Ramp | Start delay | FLOAT | 0 | s | 0 | 300 | 1
86160080 | Grid code > Power feed in management > Ramp | End time | FLOAT | 40 | s | 0 | 3600 | 1 |  | X
86160090 | Grid code > Power feed in management > Ramp | Decay factor | FLOAT | 1.05 |  | 0.01 | 2 | 2
90100400 | Grid code > Feed forward | Reactive power gain | FLOAT | 10 |  | 0 | 50 | 2
90100410 | Grid code > Feed forward | Reactive power enable | INT32 | 0 |  | 0 | 1 | 0
90100420 | Grid code > Feed forward | Active power gain | FLOAT | 12.5 |  | 0 | 50 | 2
90100430 | Grid code > Feed forward | Active power enable | INT32 | 0 |  | 0 | 1 | 0
86000000 | Grid code > RRCR | Inputs enable | INT32 | 0 |  | 0 | 1 | 0
86000010 | Grid code > RRCR | Outputs enable | INT32 | 0 |  | 0 | 1 | 0
70000800 | Grid code > Frequency offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
70000790 | Grid code > Frequency offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
86080000 | Grid code > Mains sync inhibit | Voltage low limit | FLOAT | 85 | % | 80 | 100 | 0
86080010 | Grid code > Mains sync inhibit | Voltage high limit | FLOAT | 110 | % | 100 | 120 | 0
86080020 | Grid code > Mains sync inhibit | Frequency low limit | FLOAT | 95 | % | 90 | 100 | 1
86080030 | Grid code > Mains sync inhibit | Frequency high limit | FLOAT | 101 | % | 100 | 110 | 1
86080050 | Grid code > Mains sync inhibit | Recovery delay select | FLOAT | 1 |  | 1 | 1 | 0 |  | X
86080060 | Grid code > Mains sync inhibit | Recovery delay select time | FLOAT | 3 | s | 0 | 20 | 1
86080070 | Grid code > Mains sync inhibit | Recovery delay 1 | FLOAT | 1 |  | 1 | 1 | 0 |  | X
86080080 | Grid code > Mains sync inhibit | Recovery delay 1 time | FLOAT | 5 | s | 0 | 60 | 1
86080090 | Grid code > Mains sync inhibit | Recovery delay 2 | FLOAT | 1 |  | 1 | 1 | 0 |  | X
86080100 | Grid code > Mains sync inhibit | Recovery delay 2 time | FLOAT | 600 | s | 0 | 2000 | 1
86080043 | Grid code > Mains sync inhibit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop

## GENSET
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40030110 | Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40175110 | Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40180110 | Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40185110 | Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
100010002 | Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11200030 | Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
11200040 | Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
11200010 | Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
11200000 | Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
11200100 | Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
11200070 | Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
11200020 | Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
11200090 | Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
11200052 | Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
11200053 | Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000182 | Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
11000183 | Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000184 | Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
11000000 | Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1
11000050 | Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 600 | 1
11000030 | Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 600 | 1
11000040 | Engine > Start sequence > Run coil | During start attempts | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous
11000010 | Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
11000020 | Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 99 | 1
11200060 | Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
11000210 | Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 100 | 0
11000220 | Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 7 |  | 1 | 10 | 0
11000113 | Engine > Start sequence > Start failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000120 | Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 0
11000122 | Engine > Start sequence > Crank failure | Delay | FLOAT | 2 | s | 0 | 20 | 1
11000123 | Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000270 | Engine > Start sequence > Run detection not reached | Run detection not reached | FLOAT | 10 | s | 1 | 1200 | 0
11100000 | Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0
11120000 | Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
11100100 | Engine > Idle run start > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
11100110 | Engine > Idle run start > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
11000060 | Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 0 | 9900 | 0
11000080 | Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 99 | 1
11000102 | Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 10 | 120 | 1
11000103 | Engine > Stop sequence > Stop failure | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000192 | Engine > Stop sequence > Externally stopped | Delay | FLOAT | 10 | s | 1 | 1200 | 0
11000193 | Engine > Stop sequence > Externally stopped | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11110100 | Engine > Idle run stop > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
11110110 | Engine > Idle run stop > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
11000140 | Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
11000141 | Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000142 | Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000143 | Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000150 | Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
11000151 | Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000152 | Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000153 | Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000160 | Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
11000161 | Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000162 | Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000163 | Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000164 | Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
11000170 | Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
11000171 | Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000172 | Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000173 | Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11000174 | Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
11001000 | Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
11001001 | Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
11001002 | Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001003 | Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001004 | Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
11001010 | Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
11001011 | Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
11001012 | Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
11001013 | Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001014 | Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
11001020 | Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
11001021 | Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001022 | Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001023 | Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001030 | Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
11001031 | Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001032 | Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001033 | Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001040 | Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
11001041 | Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001042 | Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001043 | Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001050 | Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
11001051 | Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001052 | Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001053 | Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001060 | Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
11001061 | Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
11001062 | Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001063 | Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001070 | Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
11001071 | Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001072 | Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001073 | Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001080 | Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
11001081 | Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001082 | Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001083 | Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11001090 | Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
11001091 | Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
11001092 | Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
11001093 | Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40600500 | Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11300330 | Engine > Maintenance > Service timer > Service timer 1 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300333 | Engine > Maintenance > Service timer > Service timer 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300340 | Engine > Maintenance > Service timer > Service timer 2 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300343 | Engine > Maintenance > Service timer > Service timer 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300350 | Engine > Maintenance > Service timer > Service timer 3 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300353 | Engine > Maintenance > Service timer > Service timer 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
11300360 | Engine > Maintenance > Service timer > Service timer 4 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
11300363 | Engine > Maintenance > Service timer > Service timer 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
170000610 | Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
11000280 | Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
11000290 | Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
11000300 | Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
11000310 | Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
11800000 | Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
11800010 | Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
11800020 | Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
11800030 | Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
40310000 | Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40310010 | Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40310030 | Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
40500010 | Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
40410130 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
40410140 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0 |  | X
40410150 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2 |  | X
40410160 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2 |  | X
40410102 | Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
40410070 | Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
90100082 | Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100092 | Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100102 | Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100042 | Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40030000 | Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40030020 | Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40030010 | Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40030090 | Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40030070 | Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40030080 | Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40175000 | Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40175020 | Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40175010 | Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40175090 | Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40175070 | Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40175080 | Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40180000 | Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40180020 | Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40180010 | Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40180090 | Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40180070 | Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40180080 | Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40185000 | Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40185020 | Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40185010 | Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40185090 | Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40185070 | Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40185080 | Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
46010010 | Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46010110 | Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
46010101 | Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000010 | Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000004 | Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active
46000110 | Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000104 | Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active
46000210 | Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000201 | Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000203 | Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46000204 | Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active
46020010 | Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46020004 | Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage, ACM wire break
46030200 | Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46030204 | Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
46030000 | Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46030100 | Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040000 | Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
46040001 | Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040100 | Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040101 | Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040103 | Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040200 | Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040201 | Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040202 | Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040203 | Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46040300 | Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040301 | Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040302 | Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040303 | Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46050000 | Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
46050001 | Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46050003 | Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46050100 | Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
46050101 | Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
46050103 | Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46060000 | Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46060100 | Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
46060101 | Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46070000 | Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
46070001 | Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46070100 | Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
46070101 | Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45300070 | Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46080000 | Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46080100 | Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090000 | Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
46090001 | Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090100 | Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090101 | Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090103 | Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46090200 | Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090201 | Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090202 | Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090203 | Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100000 | Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
46100001 | Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100004 | Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46100100 | Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100101 | Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100103 | Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100104 | Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46100200 | Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100201 | Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100202 | Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100203 | Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46100204 | Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
46110000 | Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
46110001 | Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110100 | Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110101 | Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110103 | Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110200 | Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110201 | Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110203 | Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110300 | Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110301 | Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110302 | Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110303 | Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46110400 | Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110401 | Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110402 | Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110403 | Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46120000 | Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
46120001 | Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46120003 | Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46120100 | Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
46120101 | Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120103 | Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46130000 | Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46130100 | Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46140000 | Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
46140001 | Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140003 | Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46140100 | Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140101 | Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140103 | Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101070 | Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
45300950 | Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300960 | Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001110 | Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001111 | Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001112 | Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
45001113 | Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101080 | Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
45300970 | Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300980 | Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001120 | Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001121 | Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001122 | Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
45001123 | Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101030 | Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
45301020 | Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001130 | Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
45001131 | Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001132 | Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001133 | Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45101040 | Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
45301040 | Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001140 | Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
45001141 | Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001142 | Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001143 | Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40210010 | Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40510030 | Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
90100052 | Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100062 | Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100072 | Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
90100032 | Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
46160310 | Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160300 | Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160301 | Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160302 | Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160303 | Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46160304 | Busbar > Voltage protections > Under-voltage 4 | Inhibit |  | Generator breaker open, ACM wire break
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46170004 | Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
46180200 | Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180201 | Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180202 | Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180203 | Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46180204 | Busbar > Frequency protections > Over-frequency 3 | Inhibit |  | Generator breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
46190200 | Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190201 | Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190202 | Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190203 | Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190204 | Busbar > Frequency protections > Under-frequency 3 | Inhibit |  | Generator breaker open, ACM wire break
46190300 | Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190301 | Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190302 | Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190303 | Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
46190304 | Busbar > Frequency protections > Under-frequency 4 | Inhibit |  | Generator breaker open, ACM wire break
45101060 | Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Generator
45300050 | Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
45001020 | Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
45001023 | Busbar > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45001024 | Busbar > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
45101050 | Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Generator
45301100 | Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
45301110 | Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
45301120 | Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
45001012 | Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
45001013 | Busbar > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45001014 | Busbar > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
70000780 | Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU
70000560 | Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0
70001590 | Regulators > GOV > General configuration > Frequency recovery | Frequency recovery | INT32 | Off |  |  |  |  | 0: Off, 1: Volvo Penta EMS 2.4, 2: Frequency measurement
70001600 | Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery limit | FLOAT | 3 | Hz | 0 | 20 | 1
70001610 | Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery duration | FLOAT | 1 | s | 0 | 10 | 1
90100210 | Regulators > GOV > Regulation set points > Base load | Return mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto
90100310 | Regulators > GOV > Regulation set points > Base load | Base load | INT32 | 0 |  | 0 | 1 | 0
90100320 | Regulators > GOV > Regulation set points > Base load | Set point | FLOAT | 90 | % | 10 | 120 | 0
70200040 | Regulators > GOV > Regulation set points > Active power ramp configuration | Warm up set point | FLOAT | 10 | % | 0.1 | 100 | 1
70200060 | Regulators > GOV > Regulation set points > Active power ramp configuration | Island ramping | INT32 | 0 |  | 0 | 1 | 0
70200100 | Regulators > GOV > Regulation set points > Active power ramp configuration | Enter operation ramp enable | INT32 | 0 |  | 0 | 1 | 0
70200110 | Regulators > GOV > Regulation set points > Active power ramp configuration | Deload ramp enable | INT32 | 0 |  | 0 | 1 | 0
40030120 | Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175120 | Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180120 | Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185120 | Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000100 | Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000110 | Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000120 | Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000130 | Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000140 | Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000150 | Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000160 | Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000180 | Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000190 | Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000200 | Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000040 | Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000050 | Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000060 | Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000070 | Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 0.5 |  | 0 | 60 | 2
70000080 | Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 3 | s | 0 | 60 | 2
70000090 | Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
30000010 | Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000000 | Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2500 | ms | 250 | 32500 | 0
70000010 | Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 500 | ms | 10 | 6500 | 0
70001620 | Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
70000230 | Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000240 | Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000270 | Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000290 | Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000280 | Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000300 | Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000250 | Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000260 | Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000210 | Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000220 | Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
30000000 | Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000520 | Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000522 | Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
70000523 | Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
70000770 | Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Relay, 1: Analogue / Digital AVR
40030130 | Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175130 | Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180130 | Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185130 | Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000350 | Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000360 | Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000370 | Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000320 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000330 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000340 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
70000170 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
70000380 | Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
70000390 | Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
70000400 | Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
30000030 | Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000020 | Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 500 | ms | 50 | 15000 | 0
70000030 | Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 100 | ms | 10 | 3000 | 0
70001630 | Regulators > AVR > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
70000410 | Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000420 | Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
70000430 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000440 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1
70000470 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1
70000310 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
70000450 | Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
70000460 | Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
30000020 | Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
70000530 | Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000532 | Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
70000533 | Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100010 | Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000050 | Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1
3300070 | Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
90100170 | Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
90100200 | Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
20100082 | Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100092 | Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
20100093 | Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
3300090 | Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100052 | Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100042 | Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100062 | Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100072 | Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
20100123 | Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
20100133 | Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
33000000 | Breakers > Close before excitation > Configuration | Breaker close set point | FLOAT | 400 | RPM | 0 | 4000 | 0
33000010 | Breakers > Close before excitation > Configuration | Timer crank release to AVR on | FLOAT | 5 | s | 0 | 999 | 1
33000020 | Breakers > Close before excitation > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
33000060 | Breakers > Close before excitation > Configuration | Breakers to close | INT32 | Close GB |  |  |  |  | 0: Close GB, 1: Close GB and TB
33000070 | Breakers > Close before excitation > Configuration | Soft-start timer | FLOAT | 5 | s | 0 | 999 | 1
33000080 | Breakers > Close before excitation > Configuration | Minimum RPM for excitation | FLOAT | 1450 | RPM | 0 | 4000 | 0
33000090 | Breakers > Close before excitation > Configuration | Voltage discharge timer for GB close | FLOAT | 5 | s | 1 | 20 | 1
33000100 | Breakers > Close before excitation > Configuration | Maximum rerun voltage for GB close | FLOAT | 30 | % | 30 | 100 | 0
33000110 | Breakers > Close before excitation > Configuration | Excitation control during cooldown | INT32 | Excitation follow U busbar |  |  |  |  | 0: Excitation follow U busbar, 1: Excitation constant ON, 2: Excitation OFF
33000122 | Breakers > Close before excitation > CBE failure | Delay | FLOAT | 5 | s | 0 | 999 | 1
33000123 | Breakers > Close before excitation > CBE failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
33000052 | Breakers > Close before excitation > CBE rerun failure | Delay | FLOAT | 120 | s | 0 | 999 | 1
33000053 | Breakers > Close before excitation > CBE rerun failure | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
25000150 | Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
25000160 | Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
110000232 | Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
110000233 | Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110002250 | Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
110002260 | Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
110002270 | Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
25000060 | Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
110002210 | Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
110002220 | Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
110002290 | Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
110002300 | Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
110002310 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
110002320 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
40410170 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
40410180 | Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
40410190 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410200 | Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410210 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410220 | Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410230 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
40410250 | Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
40410260 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine, 2: Open MB at ready engine
40410270 | Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
40410280 | Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410290 | Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410300 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
40410310 | Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
90200040 | Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1
90600010 | Local power management > Genset test > Settings | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
90600020 | Local power management > Genset test > Settings | Base load | FLOAT | 80 | % | 1 | 100 | 0
90600030 | Local power management > Genset test > Settings | Mode | INT32 | No mode change |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change, 3: No regulation
90600040 | Local power management > Genset test > Settings | Test time | FLOAT | 300 | s | 0 | 59940 | 0
110002160 | Power management rules > Plant/genset mode > Modes | Genset mode | INT32 | Power management |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over, 6: Power management
150000170 | Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
110000600 | Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
110000610 | Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
110000620 | Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
110000270 | Power management rules > Mains power > Peak shaving | Start generator | FLOAT | 80 | % | 5 | 100 | 0
110000280 | Power management rules > Mains power > Peak shaving | Minimum load | FLOAT | 5 | % | 0 | 100 | 0
110000290 | Power management rules > Mains power > Peak shaving | Stop generator | FLOAT | 60 | % | 0 | 80 | 0
110000370 | Power management rules > Mains power > Peak shaving | Start delay | FLOAT | 10 | s | 0 | 990 | 1
110000380 | Power management rules > Mains power > Peak shaving | Stop delay | FLOAT | 30 | s | 0 | 990 | 1
110000310 | Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
110000320 | Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000340 | Power management rules > Mains power > Common power factor control | Controller settings Q | FLOAT | 0 | % | -100 | 100 | 0
110000350 | Power management rules > Mains power > Common power factor control | Controller settings cos phi or Q | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 3: Superior, 4: Fixed Q
110000510 | Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
110000520 | Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
110000530 | Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
110000540 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
110000550 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000560 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
110000570 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000580 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
110000590 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
150000020 | Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
150000040 | Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
150000032 | Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
150000033 | Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
32000040 | Power management rules > Ground relay > Enable | Ground relay | INT32 | 0 |  | 0 | 1 | 0
32000000 | Power management rules > Ground relay > Ground relay configuration | Relay type | INT32 | Continuous |  |  |  |  | 0: Continuous, 1: Pulse
32000010 | Power management rules > Ground relay > Ground relay configuration | Close configuration | INT32 | Hz/V OK |  |  |  |  | 0: Hz/V OK, 1: RPM MPU level, 2: RPM EIC level, 3: Start active
32000020 | Power management rules > Ground relay > Ground relay configuration | Open configuration | INT32 | After cooldown |  |  |  |  | 0: After cooldown, 1: After extended stop
32000050 | Power management rules > Ground relay > Ground relay configuration | RPM level | FLOAT | 1000 | RPM | 0 | 4000 | 0
32000032 | Power management rules > Ground relay > Ground relay general failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
32000033 | Power management rules > Ground relay > Ground relay general failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
32000062 | Power management rules > Ground relay > Ground relay open failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
32000063 | Power management rules > Ground relay > Ground relay open failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
32000072 | Power management rules > Ground relay > Ground relay close failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
32000073 | Power management rules > Ground relay > Ground relay close failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
32000082 | Power management rules > Ground relay > Ground relay position failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
32000083 | Power management rules > Ground relay > Ground relay position failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
150100330 | Power management rules > Number of gensets connected > Minimum set 1 | Set point | FLOAT | 1 |  | 0 | 32 | 0
150200330 | Power management rules > Number of gensets connected > Minimum set 2 | Set point | FLOAT | 1 |  | 0 | 32 | 0
153120040 | Power management rules > Number of gensets connected > Automatic start | Multi-start set 1 | INT32 | Auto calculation |  |  |  |  | 0: Auto calculation, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32
153120050 | Power management rules > Number of gensets connected > Automatic start | Multi-start set 2 | INT32 | 16 |  | 0 | 32 | 0 | 0: Auto calculation, 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, 22, 23, 24, 25, 26, 27, 28, 29, 30, 31, 32
153120060 | Power management rules > Number of gensets connected > Selection | Multi-start selection | INT32 | Multi-start set 1 |  |  |  |  | 0: Multi-start set 1, 1: Multi-start set 2
90200000 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
90200010 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0
110000360 | Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0
150100100 | Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA
150100110 | Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100000 | Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
150100010 | Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
150100020 | Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1
150100050 | Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
150100060 | Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
150100070 | Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1
150100120 | Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
150100130 | Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
150100140 | Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1
150100160 | Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
150100180 | Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
150100190 | Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1
150100210 | Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100300 | Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0
150000210 | Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1, 2, 3, 4, 5, 6, 7, 8
110600010 | System power management > Priority > Selection | Method | INT32 | Manual absolute |  |  |  |  | 0: Manual absolute, 1: Total running hours, 2: Fuel optimisation, 3: Manual relative, 4: Running hours relative, 5: Fuel optimisation + running hours
110600110 | System power management > Priority > Selection | Transmit | INT32 | Off |  |  |  |  | 0: Off, 2: Running hours
110600020 | System power management > Priority > Running hours | Activate priority update | FLOAT | 175 | h | 1 | 20000 | 0
110600030 | System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled
110002190 | System power management > Store common settings > Settings | Store common settings | INT32 | 0 |  | 0 | 1 | 0
11500050 | Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11500022 | Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11500023 | Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11500060 | Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11500000 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11500030 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11500010 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11500040 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600050 | Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11600022 | Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11600023 | Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11600060 | Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11600000 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11600030 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600010 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11600040 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700050 | Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11700022 | Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11700023 | Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
11700060 | Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11700000 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11700030 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700010 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11700040 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002380 | Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
170000050 | Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
170000060 | Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
170000042 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
170000043 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
190000320 | Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
191000022 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
191000023 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000050 | Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
60000060 | Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
110000300 | Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
60000702 | Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
60000703 | Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
60000100 | Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
60000300 | Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000320 | Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000330 | Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000340 | Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000350 | Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000360 | Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
147000042 | System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
147000043 | System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000153 | System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000163 | System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000173 | System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000090 | System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
110000263 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | No regulation |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
110000432 | System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000433 | System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000442 | System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000443 | System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000452 | System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000453 | System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000462 | System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000463 | System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000472 | System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000473 | System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000482 | System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000483 | System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000492 | System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000493 | System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
110000502 | System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000503 | System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
147000050 | System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
147000060 | System > Plant > Update | Application to broadcast | FLOAT | 1 |  | 1 | 4 | 0 | 1
803000 | System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800001: LC | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop

## MAINS
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
40310000 | Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40310010 | Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Mains > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40310030 | Mains > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Mains > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
40500010 | Mains > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
90800070 | Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
90800000 | Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
90800010 | Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
90800020 | Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
90800030 | Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
90800040 | Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
90800050 | Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
90800060 | Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
90800083 | Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
40410000 | Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1 |  | X
40410010 | Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
40410020 | Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0 |  | X
40410030 | Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2 |  | X
40410040 | Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2 |  | X
90800110 | Mains > AC setup > Voltage and frequency OK | Measurement configuration | INT32 | Phase-phase |  |  |  |  | 0: Phase-phase, 1: Phase-neutral, 2: Phase-phase or phase-neutral
40410070 | Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Mains > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
40030000 | Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40030020 | Mains > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40030010 | Mains > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40030090 | Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40030070 | Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40030080 | Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40175000 | Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40175020 | Mains > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40175010 | Mains > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40175090 | Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40175070 | Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40175080 | Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40180000 | Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40180020 | Mains > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40180010 | Mains > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40180090 | Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40180070 | Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40180080 | Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40185000 | Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40185020 | Mains > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40185010 | Mains > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40185090 | Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40185070 | Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40185080 | Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
100010002 | Mains > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Mains > Emergency stop > Emergency stop | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46010010 | Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46010110 | Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
46010101 | Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46000010 | Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46000110 | Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46000210 | Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000201 | Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000203 | Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46020010 | Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46020004 | Mains > Voltage protections > Voltage unbalance | Inhibit |  | No mains voltage
46030200 | Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46030204 | Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
46030000 | Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46030100 | Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46040000 | Mains > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
46040001 | Mains > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Mains > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Mains > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46040100 | Mains > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040101 | Mains > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Mains > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040103 | Mains > Current protections > Over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46040200 | Mains > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040201 | Mains > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040202 | Mains > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040203 | Mains > Current protections > Over-current 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46040300 | Mains > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040301 | Mains > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040302 | Mains > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040303 | Mains > Current protections > Over-current 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46050000 | Mains > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
46050001 | Mains > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Mains > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46050003 | Mains > Current protections > Fast over-current 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46050100 | Mains > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
46050101 | Mains > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Mains > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
46050103 | Mains > Current protections > Fast over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46060000 | Mains > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Mains > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Mains > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Mains > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46060100 | Mains > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
46060101 | Mains > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Mains > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Mains > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46070000 | Mains > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
46070001 | Mains > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Mains > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Mains > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46070100 | Mains > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
46070101 | Mains > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Mains > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Mains > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45300070 | Mains > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Mains > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Mains > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Mains > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Mains > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Mains > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Mains > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Mains > Current protections > Inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46080000 | Mains > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Mains > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Mains > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Mains > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46080100 | Mains > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Mains > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Mains > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Mains > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46090000 | Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
46090001 | Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46090100 | Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090101 | Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090103 | Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46090200 | Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090201 | Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090202 | Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090203 | Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46100000 | Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
46100001 | Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46100100 | Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100101 | Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100103 | Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46100200 | Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100201 | Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100202 | Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100203 | Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46110000 | Mains > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
46110001 | Mains > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Mains > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Mains > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46110100 | Mains > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110101 | Mains > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Mains > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110103 | Mains > Power protections > Overload 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46110200 | Mains > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110201 | Mains > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Mains > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110203 | Mains > Power protections > Overload 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46110300 | Mains > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110301 | Mains > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110302 | Mains > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110303 | Mains > Power protections > Overload 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46110400 | Mains > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110401 | Mains > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110402 | Mains > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110403 | Mains > Power protections > Overload 5 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46120000 | Mains > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
46120001 | Mains > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Mains > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46120003 | Mains > Power protections > Reverse power 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46120100 | Mains > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
46120101 | Mains > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Mains > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120103 | Mains > Power protections > Reverse power 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46130000 | Mains > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Mains > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Mains > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Mains > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46130100 | Mains > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Mains > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Mains > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Mains > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46140000 | Mains > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
46140001 | Mains > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Mains > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140003 | Mains > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46140100 | Mains > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140101 | Mains > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Mains > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46140103 | Mains > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45101070 | Mains > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
45300950 | Mains > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300960 | Mains > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001110 | Mains > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001111 | Mains > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001112 | Mains > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
45001113 | Mains > Additional protections > V< and Q< 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45101080 | Mains > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
45300970 | Mains > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300980 | Mains > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001120 | Mains > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001121 | Mains > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001122 | Mains > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
45001123 | Mains > Additional protections > V< and Q< 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45101030 | Mains > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
45301020 | Mains > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001130 | Mains > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
45001131 | Mains > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001132 | Mains > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001133 | Mains > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45101040 | Mains > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
45301040 | Mains > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001140 | Mains > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
45001141 | Mains > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001142 | Mains > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001143 | Mains > Additional protections > Average over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
40210010 | Mains > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Mains > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Mains > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Mains > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Mains > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Mains > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Mains > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Mains > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210410 | Mains > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210420 | Mains > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210510 | Mains > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210520 | Mains > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40510030 | Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
40010090 | Busbar > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40010100 | Busbar > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40010030 | Busbar > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40010070 | Busbar > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40010080 | Busbar > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
40160090 | Busbar > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40160100 | Busbar > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40160030 | Busbar > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40160070 | Busbar > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40160080 | Busbar > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
40165090 | Busbar > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40165100 | Busbar > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40165030 | Busbar > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40165070 | Busbar > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40165080 | Busbar > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
40170090 | Busbar > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40170100 | Busbar > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40170030 | Busbar > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40170070 | Busbar > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40170080 | Busbar > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46160310 | Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160300 | Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160301 | Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160302 | Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160303 | Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46180200 | Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180201 | Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180202 | Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180203 | Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46190200 | Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190201 | Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190202 | Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190203 | Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
46190300 | Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190301 | Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190302 | Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190303 | Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45101060 | Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Mains
45300050 | Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
45001020 | Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
45001023 | Busbar > Additional protections > Vector shift | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45001024 | Busbar > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
45101050 | Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Mains
45301100 | Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
45301110 | Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
45301120 | Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
45001012 | Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
45001013 | Busbar > Additional protections > ROCOF | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45001014 | Busbar > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
25000150 | Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
25000160 | Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
20200010 | Breakers > Tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20200020 | Breakers > Tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20200030 | Breakers > Tie breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
25000200 | Breakers > Tie breaker configuration > Configuration | Tie breaker normally open/closed | INT32 | Normally open |  |  |  |  | 0: Normally open, 1: Normally closed
3310080 | Breakers > Tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3310000 | Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
3310010 | Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
3310020 | Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3310030 | Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3310040 | Breakers > Tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3310050 | Breakers > Tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3310060 | Breakers > Tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20200082 | Breakers > Tie breaker configuration > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20200083 | Breakers > Tie breaker configuration > Synchronisation failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200092 | Breakers > Tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20200093 | Breakers > Tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
3310090 | Breakers > Tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3310092 | Breakers > Tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3310093 | Breakers > Tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200052 | Breakers > Tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200053 | Breakers > Tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200042 | Breakers > Tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200043 | Breakers > Tie breaker monitoring > Closing failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200062 | Breakers > Tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20200063 | Breakers > Tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200072 | Breakers > Tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20200073 | Breakers > Tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
20200123 | Breakers > Tie breaker monitoring > Tripped (external) | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20200133 | Breakers > Tie breaker monitoring > Short circuit | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100010 | Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Mains breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
3300080 | Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100092 | Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
3300090 | Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100052 | Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100042 | Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100062 | Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100072 | Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
20100123 | Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
20100133 | Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000232 | Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
110000233 | Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110002250 | Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section
110002260 | Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains
110002270 | Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0
110002280 | Local power management > Mains configuration > Controls | MB failure start | INT32 | 0 |  | 0 | 1 | 0
110002330 | Local power management > Mains configuration > Controls | Exclude run all | INT32 | 0 |  | 0 | 1 | 0
25000060 | Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
110002210 | Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
110002220 | Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
110002230 | Local power management > Mains configuration > Mains breaker configuration | Parallel | INT32 | 0 |  | 0 | 1 | 0
110002240 | Local power management > Mains configuration > Mains breaker configuration | No break transfer | INT32 | 0 |  | 0 | 1 | 0
90100300 | Local power management > Mains configuration > Tie breaker configuration | TB de-load before GB | INT32 | 0 |  | 0 | 1 | 0
110002290 | Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0
110002300 | Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0
110002310 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1
110002320 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0
40410170 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
40410180 | Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
40410190 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410200 | Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
40410210 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410220 | Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410230 | Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
40410250 | Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
40410260 | Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine
40410270 | Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
40410280 | Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
40410290 | Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
40410300 | Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
40410310 | Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
90200040 | Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1 |  | X
110002170 | Power management rules > Plant/genset mode > Modes | Plant mode | INT32 | Auto mains failure |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over
150000170 | Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
110000600 | Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
110000610 | Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
110000620 | Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
90600010 | Power management rules > Mains power > Mains test | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
90600020 | Power management rules > Mains power > Mains test | Base load | FLOAT | 500 | kW | 1 | 20000 | 0
90600030 | Power management rules > Mains power > Mains test | Mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change
90600040 | Power management rules > Mains power > Mains test | Test time | FLOAT | 300 | s | 0 | 59940 | 0
110000310 | Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
110000320 | Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000330 | Power management rules > Mains power > Common power factor control | Usage | INT32 | Off |  |  |  |  | 0: Off, 1: Fixed for DG(s), 2: Fixed for import/export
110000510 | Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
110000520 | Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
110000530 | Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
110000540 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
110000550 | Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000560 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
110000570 | Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
110000580 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
110000590 | Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
150000020 | Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
150000040 | Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
150000032 | Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
150000033 | Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000360 | Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0 |  | X
150100100 | Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA | X
150100110 | Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent | X
150100000 | Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
150100010 | Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
150100020 | Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
150100030 | Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
150100050 | Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
150100060 | Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
150100070 | Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
150100080 | Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
150100120 | Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
150100130 | Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
150100140 | Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
150100150 | Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
150100160 | Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100170 | Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
150100180 | Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
150100190 | Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
150100200 | Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
150100210 | Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150000210 | Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1, 2, 3, 4, 5, 6, 7, 8 | X
110600030 | System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
110002190 | System power management > Store common settings > Settings | Store common settings | INT32 | 0 |  | 0 | 1 | 0
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002380 | Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000050 | Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
60000060 | Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
110000300 | Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
60000702 | Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
60000703 | Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
60000100 | Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
60000300 | Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000320 | Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000330 | Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000340 | Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000350 | Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000360 | Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
147000042 | System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
147000043 | System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000153 | System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000163 | System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000173 | System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000090 | System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
110000263 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Manual |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
110000432 | System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000433 | System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000442 | System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000443 | System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000452 | System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000453 | System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000462 | System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000463 | System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000472 | System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000473 | System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000482 | System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000483 | System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000492 | System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000493 | System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
110000502 | System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000503 | System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
147000050 | System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
147000060 | System > Plant > Update | Application to broadcast | FLOAT | 1 |  | 1 | 4 | 0 | 1
803000 | System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800001: LC | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker

## BUS TIE breaker
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40310000 | Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40310010 | Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Busbar A > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40310030 | Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
40500010 | Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410110 | Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40410000 | Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40410010 | Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40410040 | Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40410070 | Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
90100082 | Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100092 | Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100102 | Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100042 | Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
40030000 | Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40030020 | Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40030010 | Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40030090 | Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40030070 | Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40030080 | Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40175000 | Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40175020 | Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40175010 | Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40175090 | Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40175070 | Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40175080 | Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40180000 | Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40180020 | Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40180010 | Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40180090 | Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40180070 | Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40180080 | Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
40185000 | Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
40185020 | Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40185010 | Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
40185090 | Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
40185070 | Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
40185080 | Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
100010002 | Busbar A > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Busbar A > Emergency stop > Emergency stop | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46010010 | Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46010110 | Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
46010101 | Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46000010 | Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46000110 | Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46000210 | Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000201 | Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000203 | Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46020010 | Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46020004 | Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46030204 | Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46030100 | Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46040000 | Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
46040001 | Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46040100 | Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040101 | Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040103 | Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46040200 | Busbar A > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040201 | Busbar A > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040202 | Busbar A > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040203 | Busbar A > Current protections > Over-current 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46040300 | Busbar A > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
46040301 | Busbar A > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040302 | Busbar A > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46040303 | Busbar A > Current protections > Over-current 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46050000 | Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
46050001 | Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46050003 | Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46050100 | Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
46050101 | Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
46050103 | Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46060000 | Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46060100 | Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
46060101 | Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46070000 | Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
46070001 | Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46070100 | Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
46070101 | Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46070200 | Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -5121.95 | 5121.95 | 1
46070201 | Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070202 | Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070203 | Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46070300 | Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -5121.95 | 5121.95 | 1
46070301 | Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070302 | Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070303 | Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45300070 | Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46080000 | Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46080100 | Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46090000 | Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
46090001 | Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46090100 | Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090101 | Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090103 | Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46090200 | Busbar A > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090201 | Busbar A > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090202 | Busbar A > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46090203 | Busbar A > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46100000 | Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
46100001 | Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46100100 | Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100101 | Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100103 | Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46100200 | Busbar A > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100201 | Busbar A > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100202 | Busbar A > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46100203 | Busbar A > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46110000 | Busbar A > Power protections > Power export 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
46110001 | Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46110100 | Busbar A > Power protections > Power export 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110101 | Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Busbar A > Power protections > Power export 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110103 | Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46110200 | Busbar A > Power protections > Power export 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110201 | Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Busbar A > Power protections > Power export 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110203 | Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46110300 | Busbar A > Power protections > Power export 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110301 | Busbar A > Power protections > Power export 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110302 | Busbar A > Power protections > Power export 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110303 | Busbar A > Power protections > Power export 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46110400 | Busbar A > Power protections > Power export 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
46110401 | Busbar A > Power protections > Power export 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110402 | Busbar A > Power protections > Power export 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46110403 | Busbar A > Power protections > Power export 5 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46120000 | Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46120001 | Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120003 | Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46120100 | Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46120101 | Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120103 | Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46130000 | Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46130100 | Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46140000 | Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
46140001 | Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46140100 | Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
46140101 | Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45101070 | Busbar A > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
45300950 | Busbar A > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300960 | Busbar A > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001110 | Busbar A > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001111 | Busbar A > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001112 | Busbar A > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
45001113 | Busbar A > Additional protections > V< and Q< 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45101080 | Busbar A > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
45300970 | Busbar A > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
45300980 | Busbar A > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
45001120 | Busbar A > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
45001121 | Busbar A > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001122 | Busbar A > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
45001123 | Busbar A > Additional protections > V< and Q< 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45101030 | Busbar A > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
45301020 | Busbar A > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001130 | Busbar A > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
45001131 | Busbar A > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001132 | Busbar A > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001133 | Busbar A > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45101040 | Busbar A > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
45301040 | Busbar A > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
45001140 | Busbar A > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
45001141 | Busbar A > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
45001142 | Busbar A > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
45001143 | Busbar A > Additional protections > Average over-voltage 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
40210010 | Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210410 | Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210420 | Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210510 | Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210520 | Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40300000 | Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
40300010 | Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40510030 | Busbar B > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
40400090 | Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
90100052 | Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100062 | Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100072 | Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90100032 | Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
40010000 | Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40010110 | Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40160000 | Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40160110 | Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40165000 | Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40165110 | Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40170000 | Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
40170110 | Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
46150010 | Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46150110 | Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46150210 | Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150203 | Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46160010 | Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46160004 | Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
46160110 | Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46160104 | Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
46160210 | Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160201 | Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160203 | Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46160204 | Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
46160310 | Busbar B > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160300 | Busbar B > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160301 | Busbar B > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160302 | Busbar B > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160303 | Busbar B > Voltage protections > Under-voltage 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46160304 | Busbar B > Voltage protections > Under-voltage 4 | Inhibit |  | ACM wire break
46170010 | Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46170004 | Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46200204 | Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46200100 | Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46180000 | Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46180100 | Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46180200 | Busbar B > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180201 | Busbar B > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180202 | Busbar B > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180203 | Busbar B > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46190000 | Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46190004 | Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
46190100 | Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46190104 | Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
46190200 | Busbar B > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190201 | Busbar B > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190202 | Busbar B > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190203 | Busbar B > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46190204 | Busbar B > Frequency protections > Under-frequency 3 | Inhibit |  | ACM wire break
46190300 | Busbar B > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190301 | Busbar B > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190302 | Busbar B > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190303 | Busbar B > Frequency protections > Under-frequency 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
46190304 | Busbar B > Frequency protections > Under-frequency 4 | Inhibit |  | ACM wire break
45101060 | Busbar B > Additional protections > Vector shift | AC setup | INT32 | Busbar B |  |  |  |  | 34: Busbar B, 35: Busbar A
45300050 | Busbar B > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
45001020 | Busbar B > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
45001023 | Busbar B > Additional protections > Vector shift | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45101050 | Busbar B > Additional protections > ROCOF | AC setup | INT32 | Busbar B |  |  |  |  | 32: Busbar B, 33: Busbar A
45301100 | Busbar B > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
45301110 | Busbar B > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
45301120 | Busbar B > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
45001012 | Busbar B > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
45001013 | Busbar B > Additional protections > ROCOF | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
20100010 | Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000070 | Breakers > Bus tie breaker configuration > Configuration | BTB supply | INT32 | DC voltage |  |  |  |  | 0: AC voltage, 1: DC voltage
25000200 | Breakers > Bus tie breaker configuration > Configuration | Tie breaker normally open/closed | INT32 | Normally open |  |  |  |  | 0: Normally open, 1: Normally closed
3300080 | Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100092 | Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
3300090 | Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100052 | Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100042 | Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100062 | Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100072 | Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
20100123 | Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
20100133 | Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000252 | Local power management > Alarms > Busbar blocked > Busbar A | Delay | FLOAT | 1 | s | 1 | 5 | 1
110000253 | Local power management > Alarms > Busbar blocked > Busbar A | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000242 | Local power management > Alarms > Busbar blocked > Busbar B | Delay | FLOAT | 1 | s | 1 | 5 | 1
110000243 | Local power management > Alarms > Busbar blocked > Busbar B | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110002250 | Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
110002260 | Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
110002270 | Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
110002290 | Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
110002300 | Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
110002310 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
110002320 | Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
90200040 | Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1 |  | X
150000020 | Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
150000032 | Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
150000033 | Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
90200000 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
90200010 | Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0 |  | X
110000360 | Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0 |  | X
150100100 | Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA | X
150100110 | Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent | X
150100000 | Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
150100010 | Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
150100020 | Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
150100030 | Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
150100050 | Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
150100060 | Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
150100070 | Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
150100080 | Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
150100120 | Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
150100130 | Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
150100140 | Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
150100150 | Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
150100160 | Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100170 | Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
150100180 | Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
150100190 | Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
150100200 | Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
150100210 | Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100310 | Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0 |  | X
150000210 | Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1, 2, 3, 4, 5, 6, 7, 8 | X
110600030 | System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002380 | Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000050 | Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
60000060 | Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
60000702 | Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
60000703 | Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
60000100 | Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
60000300 | Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000320 | Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000330 | Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000340 | Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000350 | Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000360 | Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
147000042 | System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
147000043 | System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000153 | System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000163 | System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000173 | System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000090 | System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
110000263 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Manual |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
110000432 | System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000433 | System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000442 | System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000443 | System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000452 | System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000453 | System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000462 | System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000463 | System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000472 | System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000473 | System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000482 | System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000483 | System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000492 | System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000493 | System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
110000502 | System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
110000503 | System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
147000050 | System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
147000060 | System > Plant > Update | Application to broadcast | FLOAT | 1 |  | 1 | 4 | 0 | 1
803000 | System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800001: LC | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker