## Descriptions
iE 150 Land Modbus descriptions
Software version
The information contained in these tables (Revision E) is applicable to software version 1.36.0 of the iE 150, for these controller types:
| Name | Controller
| BTB | Bus tie breaker
| Mains | Mains
| GEN | Genset
| GEN-H | Genset-hybrid (genset-solar)
| ENG | Engine drive
| ATS | ATS
See the iE 150 AGC 150 Modbus server User manual for more information.
Row | Hyperlink index
23 | Modbus function codes
34 | Discrete output coil
42 | Discrete input contact
51 | Output holding register
62 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
| Status flag | Read whether a status flag is activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| Weather area | Weather data.
| Write area 1 (PLC/external system to iE 150H) | Part of the DEIF Open protocol. A PLC or external system writes data here for the iE 150 Battery/Solar to use.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| Alarm list monitoring | Read the Address for each active alarm. Use the Parameters tab in the utility software to look up which alarm corresponds to each Address. The alarm list monitoring is in Modbus addresses 28000 to 28099. These addresses are not listed in the Input register (04) worksheet.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DAVR Alarm | Read one bit to see whether the digital AVR alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| DAVR measurement | Read the operating value of the associated digital AVR measurement.
| DC measurement | Read the operating value of the associated measurement.
| Digital input state | Read one bit to see whether the digital input is activated. The controller returns 0 (false) when the digital input is not activated. The controller returns 1 (true) when the digital input is activated.
| Digital output state | Read one bit to see whether the digital output is activated. The controller returns 0 (false) when the digital output is not activated. The controller returns 1 (true) when the digital output is activated.
| EIC alarm | Read one bit to see whether the alarm from engine communication is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| EIC measurement | Read the operating value of the associated engine communication measurement.
| EIC measurements validity | Read one bit to see whether the measurement from engine communication is valid. The controller returns 0 (false) when the measurement is not valid. The controller returns 1 (true) when the measurement is valid.
| EIC measurements value | Read the operating value of the associated engine communication measurement. Note: The offsets can be different for EIC measurement and EIC measurements value.
| EIC state | Read one bit to see whether the engine communication state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus. These addresses are not listed in the Input register (04) worksheet.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Plant config | Read the value of the plant configuration.
| Plant logic state | Read one bit to see whether the plant state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PMS lite | Read the operating value of the PMS lite measurement.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus. These addresses are not listed in the Input register (04) worksheet.
| PV monitoring area | The iE 150 Solar Modbus client can poll key data from the inverter(s) and place it in the designated Modbus server area for a monitoring system to read. PV monitoring can be used with unicast and broadcast topologies. The number of nodes determines the number of inverters the iE 150 Solar should poll data from. A maximum of 42 nodes can be monitored. The iE 150 Solar expects that the ModbusIDs of the inverters are consecutive in order starting from the selected ModbusID and forward. 70 registers are reserved for each inverter. The Modbus addresses are only for the first inverter. Registers for the following inverters are consecutive.
| Relay state | Read one bit to see the relay state. The controller returns 0 (false) when the relay is de-energised. The controller returns 1 (true) when the relay is energised.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | GEN | GEN-H | ENG | ATS
Command flag | 0 | 1 | 01; 05; 15 | Remote start genset-1 (gen/mains application) | [5 empty] | X
Command flag | 0 | 1 | 01; 05; 15 | Remote start |  |  | X | X | X
Command flag | 1 | 2 | 01; 05; 15 | Remote GB ON |  |  | X | X
Command flag | 1 | 2 | 01; 05; 15 | Remote TB ON |  | X
Command flag | 1 | 2 | 01; 05; 15 | Remote CB1 ON | [5 empty] | X
Command flag | 1 | 2 | 01; 05; 15 | Remote BTB ON | X
Command flag | 2 | 3 | 01; 05; 15 | Remote CB1 OFF | [5 empty] | X
Command flag | 2 | 3 | 01; 05; 15 | Remote GB OFF |  |  | X | X
Command flag | 2 | 3 | 01; 05; 15 | Remote TB OFF |  | X
Command flag | 2 | 3 | 01; 05; 15 | Remote BTB OFF | X
Command flag | 3 | 4 | 01; 05; 15 | Remote stop genset-1 (gen/mains application) | [5 empty] | X
Command flag | 3 | 4 | 01; 05; 15 | Remote stop |  |  | X | X | X
Command flag | 4 | 5 | 01; 05; 15 | Alarm inhibit 1 | X | X | X | X | X | X
Command flag | 5 | 6 | 01; 05; 15 | Alarm inhibit 2 | X | X | X | X | X | X
Command flag | 6 | 7 | 01; 05; 15 | Alarm inhibit 3 | X | X | X | X | X | X
Command flag | 7 | 8 | 01; 05; 15 | Reset GOV/AVR regulation output to offset |  |  | X | X
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X | X | X | X | X
Command flag | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X | X | X | X |  | X
Command flag | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X | X | X | X |  | X
Command flag | 12 | 13 | 01; 05; 15 | Nominal setting 3 | X | X | X | X |  | X
Command flag | 13 | 14 | 01; 05; 15 | Nominal setting 4 | X | X | X | X |  | X
Command flag | 14 | 15 | 01; 05; 15 | Start+sync. (MANUAL) / PLC control start+sync |  |  | X | X
Command flag | 15 | 16 | 01; 05; 15 | Deload/stop (MANUAL) / PLC control deload+stop |  |  | X | X
Command flag | 16 | 17 | 01; 05; 15 | Island |  | X | X | X
Command flag | 17 | 18 | 01; 05; 15 | Automatic mains failure (AMF) |  | X | X | X
Command flag | 18 | 19 | 01; 05; 15 | Peak shaving |  | X | X | X
Command flag | 19 | 20 | 01; 05; 15 | Fixed power |  | X | X | X
Command flag | 20 | 21 | 01; 05; 15 | Mains power export (MPE) |  | X | X | X
Command flag | 21 | 22 | 01; 05; 15 | Load takeover (LTO) |  | X | X | X
Command flag | 24 | 25 | 01; 05; 15 | Remote CB2 ON | [5 empty] | X
Command flag | 24 | 25 | 01; 05; 15 | MB ON |  | X | X | X
Command flag | 25 | 26 | 01; 05; 15 | Remote CB2 OFF | [5 empty] | X
Command flag | 25 | 26 | 01; 05; 15 | MB OFF |  | X | X | X
Command flag | 26 | 27 | 01; 05; 15 | AUTO start/stop |  | X | X | X | X
Command flag | 27 | 28 | 01; 05; 15 | No Regulation mode |  |  | X | X
Command flag | 28 | 29 | 01; 05; 15 | MANUAL mode |  | X | X | X | X | X
Command flag | 29 | 30 | 01; 05; 15 | AUTO mode |  | X | X | X | X | X
Command flag | 30 | 31 | 01; 05; 15 | TEST mode |  | X | X | X | X | X
Command flag | 31 | 32 | 01; 05; 15 | External frequency control |  |  | X | X
Command flag | 32 | 33 | 01; 05; 15 | External voltage control |  |  | X | X
Command flag | 33 | 34 | 01; 05; 15 | External power control |  | X | X | X
Command flag | 34 | 35 | 01; 05; 15 | External reactive power control |  |  | X | X
Command flag | 35 | 36 | 01; 05; 15 | External power factor control |  |  | X | X
Command flag | 36 | 37 | 01; 05; 15 | Capacitive PF |  |  | X | X
Command flag | 37 | 38 | 01; 05; 15 | Base load |  |  | X
Command flag | 38 | 39 | 01; 05; 15 | 1. priority |  |  | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X | X | X | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X | X | X | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X | X | X | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X | X | X | X
Command flag | 44 | 45 | 01; 05; 15 | Battery test |  |  | X | X | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X | X | X | X | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual event set 1 | X | X | X | X | X | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual event set 2 | X | X | X | X | X | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual event set 3 | X | X | X | X | X | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual event set 4 | X | X | X | X | X | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual event set 5 | X | X | X | X | X | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual event set 6 | X | X | X | X | X | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual event set 7 | X | X | X | X | X | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual event set 8 | X | X | X | X | X | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual event set 9 | X | X | X | X | X | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual event set 10 | X | X | X | X | X | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual event set 11 | X | X | X | X | X | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual event set 12 | X | X | X | X | X | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual event set 13 | X | X | X | X | X | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual event set 14 | X | X | X | X | X | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual event set 15 | X | X | X | X | X | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual event set 16 | X | X | X | X | X | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual event set 17 | X | X | X | X | X | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual event set 18 | X | X | X | X | X | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual event set 19 | X | X | X | X | X | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual event set 20 | X | X | X | X | X | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual event set 21 | X | X | X | X | X | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual event set 22 | X | X | X | X | X | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual event set 23 | X | X | X | X | X | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual event set 24 | X | X | X | X | X | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual event set 25 | X | X | X | X | X | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual event set 26 | X | X | X | X | X | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual event set 27 | X | X | X | X | X | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual event set 28 | X | X | X | X | X | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual event set 29 | X | X | X | X | X | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual event set 30 | X | X | X | X | X | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual event set 31 | X | X | X | X | X | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual event set 32 | X | X | X | X | X | X
Command flag | 112 | 113 | 01; 05; 15 | Store common settings |  | X | X
Command flag | 113 | 114 | 01; 05; 15 | Activate EIC logger |  |  | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X | X | X | X | X | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X | X | X | X | X
Command flag | 123 | 124 | 01; 05; 15 | Enable external frequency control |  |  | X | X
Command flag | 124 | 125 | 01; 05; 15 | Disable external frequency control |  |  | X | X
Command flag | 125 | 126 | 01; 05; 15 | Enable external voltage control |  |  | X | X
Command flag | 126 | 127 | 01; 05; 15 | Disable external voltage control |  |  | X | X
Command flag | 127 | 128 | 01; 05; 15 | Enable external power control |  | X | X | X
Command flag | 128 | 129 | 01; 05; 15 | Disable external power control |  | X | X | X
Command flag | 129 | 130 | 01; 05; 15 | Enable external VAr control |  |  | X | X
Command flag | 130 | 131 | 01; 05; 15 | Disable external VAr control |  |  | X | X
Command flag | 131 | 132 | 01; 05; 15 | Enable external CosPhi control |  |  | X | X
Command flag | 132 | 133 | 01; 05; 15 | Disable external CosPhi control |  |  | X | X
Command flag | 133 | 134 | 01; 05; 15 | Enable PM base load |  |  | X
Command flag | 134 | 135 | 01; 05; 15 | Disable PM base load |  |  | X
Command flag | 135 | 136 | 01; 05; 15 | Reset horn | X | X | X | X | X | X
Command flag | 137 | 138 | 01; 05; 15 | DVC 310/D510C: Reset Alarms |  |  | X | X
Command flag | 142 | 143 | 01; 05; 15 | Virtual event set 33 | X | X | X | X | X | X
Command flag | 143 | 144 | 01; 05; 15 | Virtual event set 34 | X | X | X | X | X | X
Command flag | 144 | 145 | 01; 05; 15 | Virtual event set 35 | X | X | X | X | X | X
Command flag | 145 | 146 | 01; 05; 15 | Virtual event set 36 | X | X | X | X | X | X
Command flag | 146 | 147 | 01; 05; 15 | Virtual event set 37 | X | X | X | X | X | X
Command flag | 147 | 148 | 01; 05; 15 | Virtual event set 38 | X | X | X | X | X | X
Command flag | 148 | 149 | 01; 05; 15 | Virtual event set 39 | X | X | X | X | X | X
Command flag | 149 | 150 | 01; 05; 15 | Virtual event set 40 | X | X | X | X | X | X
Command flag | 150 | 151 | 01; 05; 15 | Virtual event set 41 | X | X | X | X | X | X
Command flag | 151 | 152 | 01; 05; 15 | Virtual event set 42 | X | X | X | X | X | X
Command flag | 152 | 153 | 01; 05; 15 | Virtual event set 43 | X | X | X | X | X | X
Command flag | 153 | 154 | 01; 05; 15 | Virtual event set 44 | X | X | X | X | X | X
Command flag | 154 | 155 | 01; 05; 15 | Virtual event set 45 | X | X | X | X | X | X
Command flag | 155 | 156 | 01; 05; 15 | Virtual event set 46 | X | X | X | X | X | X
Command flag | 156 | 157 | 01; 05; 15 | Virtual event set 47 | X | X | X | X | X | X
Command flag | 157 | 158 | 01; 05; 15 | Virtual event set 48 | X | X | X | X | X | X
Command flag | 158 | 159 | 01; 05; 15 | Virtual event set 49 | X | X | X | X | X | X
Command flag | 159 | 160 | 01; 05; 15 | Virtual event set 50 | X | X | X | X | X | X
Command flag | 160 | 161 | 01; 05; 15 | Virtual event set 51 | X | X | X | X | X | X
Command flag | 161 | 162 | 01; 05; 15 | Virtual event set 52 | X | X | X | X | X | X
Command flag | 162 | 163 | 01; 05; 15 | Virtual event set 53 | X | X | X | X | X | X
Command flag | 163 | 164 | 01; 05; 15 | Virtual event set 54 | X | X | X | X | X | X
Command flag | 164 | 165 | 01; 05; 15 | Virtual event set 55 | X | X | X | X | X | X
Command flag | 165 | 166 | 01; 05; 15 | Virtual event set 56 | X | X | X | X | X | X
Command flag | 166 | 167 | 01; 05; 15 | Virtual event set 57 | X | X | X | X | X | X
Command flag | 167 | 168 | 01; 05; 15 | Virtual event set 58 | X | X | X | X | X | X
Command flag | 168 | 169 | 01; 05; 15 | Virtual event set 59 | X | X | X | X | X | X
Command flag | 169 | 170 | 01; 05; 15 | Virtual event set 60 | X | X | X | X | X | X
Command flag | 170 | 171 | 01; 05; 15 | Virtual event set 61 | X | X | X | X | X | X
Command flag | 171 | 172 | 01; 05; 15 | Virtual event set 62 | X | X | X | X | X | X
Command flag | 172 | 173 | 01; 05; 15 | Virtual event set 63 | X | X | X | X | X | X
Command flag | 173 | 174 | 01; 05; 15 | Virtual event set 64 | X | X | X | X | X | X
Command flag | 174 | 175 | 01; 05; 15 | Virtual event set 65 | X | X | X | X | X | X
Command flag | 175 | 176 | 01; 05; 15 | Virtual event set 66 | X | X | X | X | X | X
Command flag | 176 | 177 | 01; 05; 15 | Virtual event set 67 | X | X | X | X | X | X
Command flag | 177 | 178 | 01; 05; 15 | Virtual event set 68 | X | X | X | X | X | X
Command flag | 178 | 179 | 01; 05; 15 | Virtual event set 69 | X | X | X | X | X | X
Command flag | 179 | 180 | 01; 05; 15 | Virtual event set 70 | X | X | X | X | X | X
Command flag | 180 | 181 | 01; 05; 15 | ATS BTB ON | [5 empty] | X
Command flag | 180 | 181 | 01; 05; 15 | Virtual event set 71 | X | X | X | X | X | X
Command flag | 181 | 182 | 01; 05; 15 | ATS BTB OFF | [5 empty] | X
Command flag | 181 | 182 | 01; 05; 15 | Virtual event set 72 | X | X | X | X | X | X
Command flag | 182 | 183 | 01; 05; 15 | Virtual event set 73 | X | X | X | X | X | X
Command flag | 183 | 184 | 01; 05; 15 | Virtual event set 74 | X | X | X | X | X | X
Command flag | 184 | 185 | 01; 05; 15 | Virtual event set 75 | X | X | X | X | X | X
Command flag | 185 | 186 | 01; 05; 15 | Virtual event set 76 | X | X | X | X | X | X
Command flag | 186 | 187 | 01; 05; 15 | Virtual event set 77 | X | X | X | X | X | X
Command flag | 187 | 188 | 01; 05; 15 | Virtual event set 78 | X | X | X | X | X | X
Command flag | 188 | 189 | 01; 05; 15 | Virtual event set 79 | X | X | X | X | X | X
Command flag | 189 | 190 | 01; 05; 15 | Virtual event set 80 | X | X | X | X | X | X
Command flag | 190 | 191 | 01; 05; 15 | Virtual event set 81 | X | X | X | X | X | X
Command flag | 191 | 192 | 01; 05; 15 | Virtual event set 82 | X | X | X | X | X | X
Command flag | 192 | 193 | 01; 05; 15 | Virtual event set 83 | X | X | X | X | X | X
Command flag | 193 | 194 | 01; 05; 15 | Virtual event set 84 | X | X | X | X | X | X
Command flag | 194 | 195 | 01; 05; 15 | Virtual event set 85 | X | X | X | X | X | X
Command flag | 195 | 196 | 01; 05; 15 | Virtual event set 86 | X | X | X | X | X | X
Command flag | 196 | 197 | 01; 05; 15 | Virtual event set 87 | X | X | X | X | X | X
Command flag | 197 | 198 | 01; 05; 15 | Virtual event set 88 | X | X | X | X | X | X
Command flag | 198 | 199 | 01; 05; 15 | Virtual event set 89 | X | X | X | X | X | X
Command flag | 199 | 200 | 01; 05; 15 | Virtual event set 90 | X | X | X | X | X | X
Command flag | 200 | 201 | 01; 05; 15 | Virtual event set 91 | X | X | X | X | X | X
Command flag | 201 | 202 | 01; 05; 15 | Virtual event set 92 | X | X | X | X | X | X
Command flag | 202 | 203 | 01; 05; 15 | Virtual event set 93 | X | X | X | X | X | X
Command flag | 203 | 204 | 01; 05; 15 | Virtual event set 94 | X | X | X | X | X | X
Command flag | 204 | 205 | 01; 05; 15 | Virtual event set 95 | X | X | X | X | X | X
Command flag | 205 | 206 | 01; 05; 15 | Virtual event set 96 | X | X | X | X | X | X
Command flag | 206 | 207 | 01; 05; 15 | Set flipflop 01 | X | X | X | X | X | X
Command flag | 207 | 208 | 01; 05; 15 | Set flipflop 02 | X | X | X | X | X | X
Command flag | 208 | 209 | 01; 05; 15 | Set flipflop 03 | X | X | X | X | X | X
Command flag | 209 | 210 | 01; 05; 15 | Set flipflop 04 | X | X | X | X | X | X
Command flag | 210 | 211 | 01; 05; 15 | Set flipflop 05 | X | X | X | X | X | X
Command flag | 211 | 212 | 01; 05; 15 | Set flipflop 06 | X | X | X | X | X | X
Command flag | 212 | 213 | 01; 05; 15 | Set flipflop 07 | X | X | X | X | X | X
Command flag | 213 | 214 | 01; 05; 15 | Set flipflop 08 | X | X | X | X | X | X
Command flag | 214 | 215 | 01; 05; 15 | Set flipflop 09 | X | X | X | X | X | X
Command flag | 215 | 216 | 01; 05; 15 | Set flipflop 10 | X | X | X | X | X | X
Command flag | 216 | 217 | 01; 05; 15 | Set flipflop 11 | X | X | X | X | X | X
Command flag | 217 | 218 | 01; 05; 15 | Set flipflop 12 | X | X | X | X | X | X
Command flag | 218 | 219 | 01; 05; 15 | Set flipflop 13 | X | X | X | X | X | X
Command flag | 219 | 220 | 01; 05; 15 | Set flipflop 14 | X | X | X | X | X | X
Command flag | 220 | 221 | 01; 05; 15 | Set flipflop 15 | X | X | X | X | X | X
Command flag | 221 | 222 | 01; 05; 15 | Set flipflop 16 | X | X | X | X | X | X
Command flag | 222 | 223 | 01; 05; 15 | Reset flipflop 01 | X | X | X | X | X | X
Command flag | 223 | 224 | 01; 05; 15 | Reset flipflop 02 | X | X | X | X | X | X
Command flag | 224 | 225 | 01; 05; 15 | Reset flipflop 03 | X | X | X | X | X | X
Command flag | 225 | 226 | 01; 05; 15 | Reset flipflop 04 | X | X | X | X | X | X
Command flag | 226 | 227 | 01; 05; 15 | Reset flipflop 05 | X | X | X | X | X | X
Command flag | 227 | 228 | 01; 05; 15 | Reset flipflop 06 | X | X | X | X | X | X
Command flag | 228 | 229 | 01; 05; 15 | Reset flipflop 07 | X | X | X | X | X | X
Command flag | 229 | 230 | 01; 05; 15 | Reset flipflop 08 | X | X | X | X | X | X
Command flag | 230 | 231 | 01; 05; 15 | Reset flipflop 09 | X | X | X | X | X | X
Command flag | 231 | 232 | 01; 05; 15 | Reset flipflop 10 | X | X | X | X | X | X
Command flag | 232 | 233 | 01; 05; 15 | Reset flipflop 11 | X | X | X | X | X | X
Command flag | 233 | 234 | 01; 05; 15 | Reset flipflop 12 | X | X | X | X | X | X
Command flag | 234 | 235 | 01; 05; 15 | Reset flipflop 13 | X | X | X | X | X | X
Command flag | 235 | 236 | 01; 05; 15 | Reset flipflop 14 | X | X | X | X | X | X
Command flag | 236 | 237 | 01; 05; 15 | Reset flipflop 15 | X | X | X | X | X | X
Command flag | 237 | 238 | 01; 05; 15 | Reset flipflop 16 | X | X | X | X | X | X
Command flag | 238 | 239 | 01; 05; 15 | Toggle flipflop 01 | X | X | X | X | X | X
Command flag | 239 | 240 | 01; 05; 15 | Toggle flipflop 02 | X | X | X | X | X | X
Command flag | 240 | 241 | 01; 05; 15 | Toggle flipflop 03 | X | X | X | X | X | X
Command flag | 241 | 242 | 01; 05; 15 | Toggle flipflop 04 | X | X | X | X | X | X
Command flag | 242 | 243 | 01; 05; 15 | Toggle flipflop 05 | X | X | X | X | X | X
Command flag | 242 | 243 | 01; 05; 15 | Nominal setting 5 |  |  | X
Command flag | 243 | 244 | 01; 05; 15 | Toggle flipflop 06 | X | X | X | X | X | X
Command flag | 243 | 244 | 01; 05; 15 | Nominal setting 6 |  |  | X
Command flag | 244 | 245 | 01; 05; 15 | Toggle flipflop 07 | X | X | X | X | X | X
Command flag | 245 | 246 | 01; 05; 15 | Toggle flipflop 08 | X | X | X | X | X | X
Command flag | 246 | 247 | 01; 05; 15 | Toggle flipflop 09 | X | X | X | X | X | X
Command flag | 247 | 248 | 01; 05; 15 | Toggle flipflop 10 | X | X | X | X | X | X
Command flag | 248 | 249 | 01; 05; 15 | Toggle flipflop 11 | X | X | X | X | X | X
Command flag | 249 | 250 | 01; 05; 15 | Toggle flipflop 12 | X | X | X | X | X | X
Command flag | 250 | 251 | 01; 05; 15 | Toggle flipflop 13 | X | X | X | X | X | X
Command flag | 251 | 252 | 01; 05; 15 | Toggle flipflop 14 | X | X | X | X | X | X
Command flag | 252 | 253 | 01; 05; 15 | Toggle flipflop 15 | X | X | X | X | X | X
Command flag | 253 | 254 | 01; 05; 15 | Toggle flipflop 16 | X | X | X | X | X | X
Command flag | 274 | 275 | 01; 05; 15 | Easy connect add genset |  |  | X
Command flag | 275 | 276 | 01; 05; 15 | Easy connect remove genset |  |  | X
Command flag | 276 | 277 | 01; 05; 15 | Select yes on display for easy connect |  |  | X
Command flag | 277 | 278 | 01; 05; 15 | Select no on display for easy connect |  |  | X
Command flag | 284 | 285 | 01; 05; 15 | DVC 550/D550: Reset faults |  |  | X | X
Command flag | 285 | 286 | 01; 05; 15 | Remote PVB On |  |  |  | X
Command flag | 286 | 287 | 01; 05; 15 | Remote PVB Off |  |  |  | X
Command flag | 287 | 288 | 01; 05; 15 | PV semi start |  |  |  | X
Command flag | 288 | 289 | 01; 05; 15 | PV semi stop |  |  |  | X
Command flag | 289 | 290 | 01; 05; 15 | Controls PV auto start/stop |  |  |  | X
Command flag | 290 | 291 | 01; 05; 15 | Set if PV auto start/stop should be controlled from Modbus |  |  |  | X
Command flag | 291 | 292 | 01; 05; 15 | Set oneshot 01 | X | X | X | X | X | X
Command flag | 292 | 293 | 01; 05; 15 | Set oneshot 02 | X | X | X | X | X | X
Command flag | 293 | 294 | 01; 05; 15 | Set oneshot 03 | X | X | X | X | X | X
Command flag | 294 | 295 | 01; 05; 15 | Set oneshot 04 | X | X | X | X | X | X
Command flag | 295 | 296 | 01; 05; 15 | Set oneshot 05 | X | X | X | X | X | X
Command flag | 296 | 297 | 01; 05; 15 | Set oneshot 06 | X | X | X | X | X | X
Command flag | 297 | 298 | 01; 05; 15 | Set oneshot 07 | X | X | X | X | X | X
Command flag | 298 | 299 | 01; 05; 15 | Set oneshot 08 | X | X | X | X | X | X
Command flag | 299 | 300 | 01; 05; 15 | Set oneshot 09 | X | X | X | X | X | X
Command flag | 300 | 301 | 01; 05; 15 | Set oneshot 10 | X | X | X | X | X | X
Command flag | 301 | 302 | 01; 05; 15 | Set oneshot 11 | X | X | X | X | X | X
Command flag | 302 | 303 | 01; 05; 15 | Set oneshot 12 | X | X | X | X | X | X
Command flag | 303 | 304 | 01; 05; 15 | Set oneshot 13 | X | X | X | X | X | X
Command flag | 304 | 305 | 01; 05; 15 | Set oneshot 14 | X | X | X | X | X | X
Command flag | 305 | 306 | 01; 05; 15 | Set oneshot 15 | X | X | X | X | X | X
Command flag | 306 | 307 | 01; 05; 15 | Set oneshot 16 | X | X | X | X | X | X
Command flag | 307 | 308 | 01; 05; 15 | Virtual toggle set 1 | X | X | X | X | X | X
Command flag | 308 | 309 | 01; 05; 15 | Virtual toggle set 2 | X | X | X | X | X | X
Command flag | 309 | 310 | 01; 05; 15 | Virtual toggle set 3 | X | X | X | X | X | X
Command flag | 310 | 311 | 01; 05; 15 | Virtual toggle set 4 | X | X | X | X | X | X
Command flag | 311 | 312 | 01; 05; 15 | Virtual toggle set 5 | X | X | X | X | X | X
Command flag | 312 | 313 | 01; 05; 15 | Virtual toggle set 6 | X | X | X | X | X | X
Command flag | 313 | 314 | 01; 05; 15 | Virtual toggle set 7 | X | X | X | X | X | X
Command flag | 314 | 315 | 01; 05; 15 | Virtual toggle set 8 | X | X | X | X | X | X
Command flag | 315 | 316 | 01; 05; 15 | Virtual toggle set 9 | X | X | X | X | X | X
Command flag | 316 | 317 | 01; 05; 15 | Virtual toggle set 10 | X | X | X | X | X | X
Command flag | 317 | 318 | 01; 05; 15 | Virtual toggle set 11 | X | X | X | X | X | X
Command flag | 318 | 319 | 01; 05; 15 | Virtual toggle set 12 | X | X | X | X | X | X
Command flag | 319 | 320 | 01; 05; 15 | Virtual toggle set 13 | X | X | X | X | X | X
Command flag | 320 | 321 | 01; 05; 15 | Virtual toggle set 14 | X | X | X | X | X | X
Command flag | 321 | 322 | 01; 05; 15 | Virtual toggle set 15 | X | X | X | X | X | X
Command flag | 322 | 323 | 01; 05; 15 | Virtual toggle set 16 | X | X | X | X | X | X
Command flag | 323 | 324 | 01; 05; 15 | Virtual toggle set 17 | X | X | X | X | X | X
Command flag | 324 | 325 | 01; 05; 15 | Virtual toggle set 18 | X | X | X | X | X | X
Command flag | 325 | 326 | 01; 05; 15 | Virtual toggle set 19 | X | X | X | X | X | X
Command flag | 326 | 327 | 01; 05; 15 | Virtual toggle set 20 | X | X | X | X | X | X
Command flag | 327 | 328 | 01; 05; 15 | Virtual toggle set 21 | X | X | X | X | X | X
Command flag | 328 | 329 | 01; 05; 15 | Virtual toggle set 22 | X | X | X | X | X | X
Command flag | 329 | 330 | 01; 05; 15 | Virtual toggle set 23 | X | X | X | X | X | X
Command flag | 330 | 331 | 01; 05; 15 | Virtual toggle set 24 | X | X | X | X | X | X
Command flag | 331 | 332 | 01; 05; 15 | Virtual toggle set 25 | X | X | X | X | X | X
Command flag | 332 | 333 | 01; 05; 15 | Virtual toggle set 26 | X | X | X | X | X | X
Command flag | 333 | 334 | 01; 05; 15 | Virtual toggle set 27 | X | X | X | X | X | X
Command flag | 334 | 335 | 01; 05; 15 | Virtual toggle set 28 | X | X | X | X | X | X
Command flag | 335 | 336 | 01; 05; 15 | Virtual toggle set 29 | X | X | X | X | X | X
Command flag | 336 | 337 | 01; 05; 15 | Virtual toggle set 30 | X | X | X | X | X | X
Command flag | 337 | 338 | 01; 05; 15 | Virtual toggle set 31 | X | X | X | X | X | X
Command flag | 338 | 339 | 01; 05; 15 | Virtual toggle set 32 | X | X | X | X | X | X
Command flag | 340 | 341 | 01; 05; 15 | CAT C7.1 aftertreatment system - enable/disable |  |  | X | X | X
Command flag | 341 | 342 | 01; 05; 15 | CAT C7.1 aftertreatment dosing - standard/reduced |  |  | X | X | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | BTB | MAINS | GEN | GEN-H | ENG | ATS
Status flag | 0 | 100001 | 02 | GB position ON |  |  | X | X
Status flag | 0 | 100001 | 02 | TB position ON |  | X
Status flag | 0 | 100001 | 02 | BTB position ON | X
Status flag | 1 | 100002 | 02 | MB position ON |  | X | X | X
Status flag | 3 | 100004 | 02 | Running |  |  | X | X | X
Status flag | 4 | 100005 | 02 | Generator voltage/frequency OK |  |  | X | X
Status flag | 4 | 100005 | 02 | Busbar voltage/frequency OK |  | X
Status flag | 5 | 100006 | 02 | Mains failure (Single DG) |  |  | X | X
Status flag | 5 | 100006 | 02 | Mains failure |  | X
Status flag | 6 | 100007 | 02 | BLOCK mode |  | X | X | X | X
Status flag | 7 | 100008 | 02 | No Regulation mode |  |  | X | X | X
Status flag | 8 | 100009 | 02 | MANUAL mode | X | X | X | X | X | X
Status flag | 9 | 100010 | 02 | AUTO mode | X | X | X | X | X | X
Status flag | 10 | 100011 | 02 | TEST mode |  | X | X | X | X
Status flag | 11 | 100012 | 02 | GB position OFF |  |  | X | X
Status flag | 11 | 100012 | 02 | TB position OFF |  | X
Status flag | 11 | 100012 | 02 | BTB position OFF | X
Status flag | 12 | 100013 | 02 | MB position OFF |  | X | X | X
Status flag | 13 | 100014 | 02 | Island |  | X | X | X | X
Status flag | 14 | 100015 | 02 | Automatic mains failure (AMF) |  | X | X | X
Status flag | 15 | 100016 | 02 | Peak shaving |  | X | X
Status flag | 16 | 100017 | 02 | Fixed power |  | X | X | X
Status flag | 17 | 100018 | 02 | Mains power export (MPE) |  | X | X | X
Status flag | 18 | 100019 | 02 | Load takeover (LTO) |  | X | X | X
Status flag | 19 | 100020 | 02 | Power management |  |  | X
Status flag | 20 | 100021 | 02 | Any alarm on PMS ID1 | X | X | X
Status flag | 21 | 100022 | 02 | Any alarm on PMS ID2 | X | X | X
Status flag | 22 | 100023 | 02 | Any alarm on PMS ID3 | X | X | X
Status flag | 23 | 100024 | 02 | Any alarm on PMS ID4 | X | X | X
Status flag | 24 | 100025 | 02 | Any alarm on PMS ID5 | X | X | X
Status flag | 25 | 100026 | 02 | Any alarm on PMS ID6 | X | X | X
Status flag | 26 | 100027 | 02 | Any alarm on PMS ID7 | X | X | X
Status flag | 27 | 100028 | 02 | Any alarm on PMS ID8 | X | X | X
Status flag | 28 | 100029 | 02 | Any alarm mains (Mains Command Unit) | X | X | X
Status flag | 29 | 100030 | 02 | Battery test |  |  | X | X | X
Status flag | 31 | 100032 | 02 | Ready AUTO-start GEN1 | X | X | X
Status flag | 32 | 100033 | 02 | Ready AUTO-start GEN2 | X | X | X
Status flag | 33 | 100034 | 02 | Ready AUTO-start GEN3 | X | X | X
Status flag | 34 | 100035 | 02 | Ready AUTO-start GEN4 | X | X | X
Status flag | 35 | 100036 | 02 | Ready AUTO-start GEN5 | X | X | X
Status flag | 36 | 100037 | 02 | Ready AUTO-start GEN6 | X | X | X
Status flag | 37 | 100038 | 02 | Ready AUTO-start GEN7 | X | X | X
Status flag | 38 | 100039 | 02 | Ready AUTO-start GEN8 | X | X | X
Status flag | 53 | 100054 | 02 | Mains sync. inhibit |  | X | X | X
Status flag | 54 | 100055 | 02 | Any mains sync. inhibit | X | X | X
Status flag | 771 | 100772 | 02 | 3rd party loadshare status |  |  | X
Status flag | 772 | 100773 | 02 | 3rd party digital loadshare protocol |  |  | X
Status flag | 773 | 100774 | 02 | 3rd party loadshare active power setpoint |  |  | X
Status flag | 774 | 100775 | 02 | 3rd party loadshare reactive power setpoint |  |  | X
Status flag | 775 | 100776 | 02 | 3rd party loadshare number of units |  |  | X
Status flag | 776 | 100777 | 02 | 3rd party loadshare number of active units |  |  | X
Digital input | 22500 | 122501 | 02 | Digital input 39 | X | X | X | X | X | X
Digital input | 22501 | 122502 | 02 | Digital input 40 | X | X | X | X | X | X
Digital input | 22502 | 122503 | 02 | Digital input 41 | X | X | X | X | X | X
Digital input | 22503 | 122504 | 02 | Digital input 42 | X | X | X | X | X | X
Digital input | 22504 | 122505 | 02 | Digital input 43 | X | X | X | X | X | X
Digital input | 22505 | 122506 | 02 | Digital input 44 | X | X | X | X | X | X
Digital input | 22506 | 122507 | 02 | Digital input 45 | X | X | X | X | X | X
Digital input | 22507 | 122508 | 02 | Digital input 46 | X | X | X | X | X | X
Digital input | 22512 | 122513 | 02 | Dplus input 7 |  |  | X | X | X
Digital input | 22513 | 122514 | 02 | Emergency stop input 4 | X | X | X | X | X | X
Digital input | 22590 | 122591 | 02 | Binary in 23 | X | X | X | X | X | X
Digital input | 22591 | 122592 | 02 | Binary in 22 | X | X | X | X | X | X
Digital input | 22592 | 122593 | 02 | Binary in 21 | X | X | X | X | X | X
Digital input | 22593 | 122594 | 02 | Binary in 20 | X | X | X | X | X | X
Digital input | 22594 | 122595 | 02 | CIO 116 no. 1. Input 10 | X | X | X | X | X | X
Digital input | 22595 | 122596 | 02 | CIO 116 no. 1. Input 11 | X | X | X | X | X | X
Digital input | 22596 | 122597 | 02 | CIO 116 no. 1. Input 12 | X | X | X | X | X | X
Digital input | 22597 | 122598 | 02 | CIO 116 no. 1. Input 13 | X | X | X | X | X | X
Digital input | 22598 | 122599 | 02 | CIO 116 no. 1. Input 14 | X | X | X | X | X | X
Digital input | 22599 | 122600 | 02 | CIO 116 no. 1. Input 15 | X | X | X | X | X | X
Digital input | 22600 | 122601 | 02 | CIO 116 no. 1. Input 16 | X | X | X | X | X | X
Digital input | 22601 | 122602 | 02 | CIO 116 no. 1. Input 17 | X | X | X | X | X | X
Digital input | 22602 | 122603 | 02 | CIO 116 no. 1. Input 19 | X | X | X | X | X | X
Digital input | 22603 | 122604 | 02 | CIO 116 no. 1. Input 20 | X | X | X | X | X | X
Digital input | 22604 | 122605 | 02 | CIO 116 no. 1. Input 21 | X | X | X | X | X | X
Digital input | 22605 | 122606 | 02 | CIO 116 no. 1. Input 22 | X | X | X | X | X | X
Digital input | 22606 | 122607 | 02 | CIO 116 no. 1. Input 23 | X | X | X | X | X | X
Digital input | 22607 | 122608 | 02 | CIO 116 no. 1. Input 24 | X | X | X | X | X | X
Digital input | 22608 | 122609 | 02 | CIO 116 no. 1. Input 25 | X | X | X | X | X | X
Digital input | 22609 | 122610 | 02 | CIO 116 no. 1. Input 26 | X | X | X | X | X | X
Digital input | 22610 | 122611 | 02 | CIO 116 no. 2. Input 10 | X | X | X | X | X | X
Digital input | 22611 | 122612 | 02 | CIO 116 no. 2. Input 11 | X | X | X | X | X | X
Digital input | 22612 | 122613 | 02 | CIO 116 no. 2. Input 12 | X | X | X | X | X | X
Digital input | 22613 | 122614 | 02 | CIO 116 no. 2. Input 13 | X | X | X | X | X | X
Digital input | 22614 | 122615 | 02 | CIO 116 no. 2. Input 14 | X | X | X | X | X | X
Digital input | 22615 | 122616 | 02 | CIO 116 no. 2. Input 15 | X | X | X | X | X | X
Digital input | 22616 | 122617 | 02 | CIO 116 no. 2. Input 16 | X | X | X | X | X | X
Digital input | 22617 | 122618 | 02 | CIO 116 no. 2. Input 17 | X | X | X | X | X | X
Digital input | 22618 | 122619 | 02 | CIO 116 no. 2. Input 19 | X | X | X | X | X | X
Digital input | 22619 | 122620 | 02 | CIO 116 no. 2. Input 20 | X | X | X | X | X | X
Digital input | 22620 | 122621 | 02 | CIO 116 no. 2. Input 21 | X | X | X | X | X | X
Digital input | 22621 | 122622 | 02 | CIO 116 no. 2. Input 22 | X | X | X | X | X | X
Digital input | 22622 | 122623 | 02 | CIO 116 no. 2. Input 23 | X | X | X | X | X | X
Digital input | 22623 | 122624 | 02 | CIO 116 no. 2. Input 24 | X | X | X | X | X | X
Digital input | 22624 | 122625 | 02 | CIO 116 no. 2. Input 25 | X | X | X | X | X | X
Digital input | 22625 | 122626 | 02 | CIO 116 no. 2. Input 26 | X | X | X | X | X | X
Digital input | 22626 | 122627 | 02 | CIO 116 no. 3. Input 10 | X | X | X | X | X | X
Digital input | 22627 | 122628 | 02 | CIO 116 no. 3. Input 11 | X | X | X | X | X | X
Digital input | 22628 | 122629 | 02 | CIO 116 no. 3. Input 12 | X | X | X | X | X | X
Digital input | 22629 | 122630 | 02 | CIO 116 no. 3. Input 13 | X | X | X | X | X | X
Digital input | 22630 | 122631 | 02 | CIO 116 no. 3. Input 14 | X | X | X | X | X | X
Digital input | 22631 | 122632 | 02 | CIO 116 no. 3. Input 15 | X | X | X | X | X | X
Digital input | 22632 | 122633 | 02 | CIO 116 no. 3. Input 16 | X | X | X | X | X | X
Digital input | 22633 | 122634 | 02 | CIO 116 no. 3. Input 17 | X | X | X | X | X | X
Digital input | 22634 | 122635 | 02 | CIO 116 no. 3. Input 19 | X | X | X | X | X | X
Digital input | 22635 | 122636 | 02 | CIO 116 no. 3. Input 20 | X | X | X | X | X | X
Digital input | 22636 | 122637 | 02 | CIO 116 no. 3. Input 21 | X | X | X | X | X | X
Digital input | 22637 | 122638 | 02 | CIO 116 no. 3. Input 22 | X | X | X | X | X | X
Digital input | 22638 | 122639 | 02 | CIO 116 no. 3. Input 23 | X | X | X | X | X | X
Digital input | 22639 | 122640 | 02 | CIO 116 no. 3. Input 24 | X | X | X | X | X | X
Digital input | 22640 | 122641 | 02 | CIO 116 no. 3. Input 25 | X | X | X | X | X | X
Digital input | 22641 | 122642 | 02 | CIO 116 no. 3. Input 26 | X | X | X | X | X | X
Digital input | 22674 | 122675 | 02 | CIO 308 no. 1. Input 8 | X | X | X | X | X | X
Digital input | 22675 | 122676 | 02 | CIO 308 no. 1. Input 11 | X | X | X | X | X | X
Digital input | 22676 | 122677 | 02 | CIO 308 no. 1. Input 14 | X | X | X | X | X | X
Digital input | 22677 | 122678 | 02 | CIO 308 no. 1. Input 17 | X | X | X | X | X | X
Digital input | 22678 | 122679 | 02 | CIO 308 no. 1. Input 20 | X | X | X | X | X | X
Digital input | 22679 | 122680 | 02 | CIO 308 no. 1. Input 23 | X | X | X | X | X | X
Digital input | 22680 | 122681 | 02 | CIO 308 no. 1. Input 26 | X | X | X | X | X | X
Digital input | 22681 | 122682 | 02 | CIO 308 no. 1. Input 29 | X | X | X | X | X | X
Digital input | 22682 | 122683 | 02 | CIO 308 no. 2. Input 8 | X | X | X | X | X | X
Digital input | 22683 | 122684 | 02 | CIO 308 no. 2. Input 11 | X | X | X | X | X | X
Digital input | 22684 | 122685 | 02 | CIO 308 no. 2. Input 14 | X | X | X | X | X | X
Digital input | 22685 | 122686 | 02 | CIO 308 no. 2. Input 17 | X | X | X | X | X | X
Digital input | 22686 | 122687 | 02 | CIO 308 no. 2. Input 20 | X | X | X | X | X | X
Digital input | 22687 | 122688 | 02 | CIO 308 no. 2. Input 23 | X | X | X | X | X | X
Digital input | 22688 | 122689 | 02 | CIO 308 no. 2. Input 26 | X | X | X | X | X | X
Digital input | 22689 | 122690 | 02 | CIO 308 no. 2. Input 29 | X | X | X | X | X | X
Digital input | 22690 | 122691 | 02 | CIO 308 no. 3. Input 8 | X | X | X | X | X | X
Digital input | 22691 | 122692 | 02 | CIO 308 no. 3. Input 11 | X | X | X | X | X | X
Digital input | 22692 | 122693 | 02 | CIO 308 no. 3. Input 14 | X | X | X | X | X | X
Digital input | 22693 | 122694 | 02 | CIO 308 no. 3. Input 17 | X | X | X | X | X | X
Digital input | 22694 | 122695 | 02 | CIO 308 no. 3. Input 20 | X | X | X | X | X | X
Digital input | 22695 | 122696 | 02 | CIO 308 no. 3. Input 23 | X | X | X | X | X | X
Digital input | 22696 | 122697 | 02 | CIO 308 no. 3. Input 26 | X | X | X | X | X | X
Digital input | 22697 | 122698 | 02 | CIO 308 no. 3. Input 29 | X | X | X | X | X | X
Digital output | 23001 | 123002 | 02 | Relay 5 | X | X | X | X | X | X
Digital output | 23002 | 123003 | 02 | Relay 6 | X | X | X | X | X | X
Digital output | 23003 | 123004 | 02 | Relay 9 | X | X | X | X | X | X
Digital output | 23004 | 123005 | 02 | Relay 10 | X | X | X | X | X | X
Digital output | 23005 | 123006 | 02 | Relay 11 | X | X | X | X | X | X
Digital output | 23006 | 123007 | 02 | Relay 12 | X | X | X | X | X | X
Digital output | 23007 | 123008 | 02 | Relay 13 | X | X | X | X | X | X
Digital output | 23008 | 123009 | 02 | Relay 14 | X | X | X | X | X | X
Digital output | 23009 | 123010 | 02 | Relay 15 | X | X | X | X | X | X
Digital output | 23010 | 123011 | 02 | Relay 16 | X | X | X | X | X | X
Digital output | 23011 | 123012 | 02 | Relay 17 | X | X | X | X | X | X
Digital output | 23012 | 123013 | 02 | Relay 18 | X | X | X | X | X | X
Digital output | 23056 | 123057 | 02 | CIO 208 no. 1. Output 9 | X | X | X | X | X | X
Digital output | 23057 | 123058 | 02 | CIO 208 no. 1. Output 11 | X | X | X | X | X | X
Digital output | 23058 | 123059 | 02 | CIO 208 no. 1. Output 13 | X | X | X | X | X | X
Digital output | 23059 | 123060 | 02 | CIO 208 no. 1. Output 15 | X | X | X | X | X | X
Digital output | 23060 | 123061 | 02 | CIO 208 no. 1. Output 18 | X | X | X | X | X | X
Digital output | 23061 | 123062 | 02 | CIO 208 no. 1. Output 21 | X | X | X | X | X | X
Digital output | 23062 | 123063 | 02 | CIO 208 no. 1. Output 24 | X | X | X | X | X | X
Digital output | 23063 | 123064 | 02 | CIO 208 no. 1. Output 27 | X | X | X | X | X | X
Digital output | 23064 | 123065 | 02 | CIO 208 no. 2. Output 9 | X | X | X | X | X | X
Digital output | 23065 | 123066 | 02 | CIO 208 no. 2. Output 11 | X | X | X | X | X | X
Digital output | 23066 | 123067 | 02 | CIO 208 no. 2. Output 13 | X | X | X | X | X | X
Digital output | 23067 | 123068 | 02 | CIO 208 no. 2. Output 15 | X | X | X | X | X | X
Digital output | 23068 | 123069 | 02 | CIO 208 no. 2. Output 18 | X | X | X | X | X | X
Digital output | 23069 | 123070 | 02 | CIO 208 no. 2. Output 21 | X | X | X | X | X | X
Digital output | 23070 | 123071 | 02 | CIO 208 no. 2. Output 24 | X | X | X | X | X | X
Digital output | 23071 | 123072 | 02 | CIO 208 no. 2. Output 27 | X | X | X | X | X | X
Digital output | 23072 | 123073 | 02 | CIO 208 no. 3. Output 9 | X | X | X | X | X | X
Digital output | 23073 | 123074 | 02 | CIO 208 no. 3. Output 11 | X | X | X | X | X | X
Digital output | 23074 | 123075 | 02 | CIO 208 no. 3. Output 13 | X | X | X | X | X | X
Digital output | 23075 | 123076 | 02 | CIO 208 no. 3. Output 15 | X | X | X | X | X | X
Digital output | 23076 | 123077 | 02 | CIO 208 no. 3. Output 18 | X | X | X | X | X | X
Digital output | 23077 | 123078 | 02 | CIO 208 no. 3. Output 21 | X | X | X | X | X | X
Digital output | 23078 | 123079 | 02 | CIO 208 no. 3. Output 24 | X | X | X | X | X | X
Digital output | 23079 | 123080 | 02 | CIO 208 no. 3. Output 27 | X | X | X | X | X | X
Digital output | 23080 | 123081 | 02 | CIO 116 no. 1 conf. status out | X | X | X | X | X | X
Digital output | 23081 | 123082 | 02 | CIO 116 no. 2 conf. status out | X | X | X | X | X | X
Digital output | 23082 | 123083 | 02 | CIO 116 no. 3 conf. status out | X | X | X | X | X | X
Digital output | 23083 | 123084 | 02 | CIO 208 no. 1 conf. status out | X | X | X | X | X | X
Digital output | 23084 | 123085 | 02 | CIO 208 no. 2 conf. status out | X | X | X | X | X | X
Digital output | 23085 | 123086 | 02 | CIO 208 no. 3 conf. status out | X | X | X | X | X | X
Digital output | 23086 | 123087 | 02 | CIO 308 no. 1 conf. status out | X | X | X | X | X | X
Digital output | 23087 | 123088 | 02 | CIO 308 no. 2 conf. status out | X | X | X | X | X | X
Digital output | 23088 | 123089 | 02 | CIO 308 no. 3 conf. status out | X | X | X | X | X | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | GEN | GEN-H | ENG | ATS
Control command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Activated in menu 7501 | INT16s | AB | 0 |  |  | X | X | X
Control command | 1 |  | 400002 | 03; 06; 16 | cosPhi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7504 | INT16s | AB | 0 |  |  |  | X | X
Control command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Activated in menu 7505 | INT16s | AB | 0 |  |  |  | X | X
Control command | 3 |  | 400004 | 03; 06; 16 | Frequency regulator setpoint - +/-100% corresponding to +/10.0% of nominal frequency. Activated in menu 7502 | INT16s | AB | 0 |  |  |  | X | X
Control command | 4 |  | 400005 | 03; 06; 16 | Voltage regulator setpoint - +/-100% corresponding to +/10.0% of nominal voltage. Activated in menu 7503 | INT16s | AB | 0 |  |  |  | X | X
Control command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 5 | 1 | 400006 | 03; 06; 16 | Remote start genset-1 (gen/mains application) | BOOL | [8 empty] | X
Control command | 5 | 1 | 400006 | 03; 06; 16 | Remote start | BOOL | [5 empty] | X | X | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote CB1 ON | BOOL | [8 empty] | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote GB ON | BOOL | [5 empty] | X | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote TB ON | BOOL |  |  |  |  | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote BTB ON | BOOL |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote CB1 OFF | BOOL | [8 empty] | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote GB OFF | BOOL | [5 empty] | X | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote TB OFF | BOOL |  |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote BTB OFF | BOOL |  |  |  | X
Control command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop genset-1 (gen/mains application) | BOOL | [8 empty] | X
Control command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop | BOOL | [5 empty] | X | X | X
Control command | 5 | 5 | 400006 | 03; 06; 16 | Reset GOV/AVR regulation output to offset | BOOL | [5 empty] | X | X
Control command | 5 | 6 | 400006 | 03; 06; 16 | Start + sync. (MAN) | BOOL | [5 empty] | X | X
Control command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X | X | X | X
Control command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X | X | X | X
Control command | 5 | 13 | 400006 | 03; 06; 16 | Nominal setting 3 | BOOL |  |  |  | X | X | X | X
Control command | 5 | 14 | 400006 | 03; 06; 16 | Nominal setting 4 | BOOL |  |  |  | X | X | X | X
Control command | 5 | 15 | 400006 | 03; 06; 16 | Deload and stop (MAN) | BOOL | [5 empty] | X | X
Control command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 6 | 1 | 400007 | 03; 06; 16 | Island | BOOL |  |  |  |  | X | X | X
Control command | 6 | 2 | 400007 | 03; 06; 16 | Automatic mains failure (AMF) | BOOL |  |  |  |  | X | X | X
Control command | 6 | 3 | 400007 | 03; 06; 16 | Peak shaving | BOOL |  |  |  |  | X | X | X
Control command | 6 | 4 | 400007 | 03; 06; 16 | Fixed power | BOOL |  |  |  |  | X | X | X
Control command | 6 | 5 | 400007 | 03; 06; 16 | Mains power export (MPE) | BOOL |  |  |  |  | X | X | X
Control command | 6 | 6 | 400007 | 03; 06; 16 | Load takeover (LTO) | BOOL |  |  |  |  | X | X | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | Remote CB2 ON | BOOL | [8 empty] | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | MB ON (Single DG) | BOOL | [5 empty] | X | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | MB ON | BOOL |  |  |  |  | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | Remote CB2 OFF | BOOL | [8 empty] | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF (Single DG) | BOOL | [5 empty] | X | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | MB OFF | BOOL |  |  |  |  | X
Control command | 6 | 11 | 400007 | 03; 06; 16 | Auto start/stop | BOOL |  |  |  |  | X | X | X | X
Control command | 6 | 12 | 400007 | 03; 06; 16 | NO REGULATION mode | BOOL | [5 empty] | X | X | X
Control command | 6 | 13 | 400007 | 03; 06; 16 | AUTO mode | BOOL |  |  |  | X | X | X | X | X | X
Control command | 6 | 14 | 400007 | 03; 06; 16 | MANUAL mode | BOOL |  |  |  | X | X | X | X | X | X
Control command | 6 | 15 | 400007 | 03; 06; 16 | TEST mode | BOOL |  |  |  |  | X | X | X | X | X
Control command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 7 | 1 | 400008 | 03; 06; 16 | External frequency control | BOOL | [5 empty] | X | X
Control command | 7 | 2 | 400008 | 03; 06; 16 | External voltage control | BOOL | [5 empty] | X | X
Control command | 7 | 3 | 400008 | 03; 06; 16 | External power control | BOOL |  |  |  |  | X | X | X
Control command | 7 | 4 | 400008 | 03; 06; 16 | External reactive power control | BOOL | [5 empty] | X | X
Control command | 7 | 5 | 400008 | 03; 06; 16 | External power factor control | BOOL | [5 empty] | X | X
Control command | 7 | 6 | 400008 | 03; 06; 16 | Capacitive PF | BOOL | [5 empty] | X | X
Control command | 7 | 7 | 400008 | 03; 06; 16 | Base load | BOOL | [5 empty] | X
Control command | 7 | 8 | 400008 | 03; 06; 16 | 1. priority | BOOL | [5 empty] | X
Control command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X | X | X | X
Control command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X | X | X | X
Control command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X | X | X | X
Control command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X | X | X | X
Control command | 7 | 13 | 400008 | 03; 06; 16 | Battery test | BOOL | [5 empty] | X | X | X
Control command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 1 | 400009 | 03; 06; 16 | Virtual toggle event 1 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 2 | 400009 | 03; 06; 16 | Virtual toggle event 2 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 3 | 400009 | 03; 06; 16 | Virtual toggle event 3 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 4 | 400009 | 03; 06; 16 | Virtual toggle event 4 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 5 | 400009 | 03; 06; 16 | Virtual toggle event 5 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 6 | 400009 | 03; 06; 16 | Virtual toggle event 6 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 7 | 400009 | 03; 06; 16 | Virtual toggle event 7 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 8 | 400009 | 03; 06; 16 | Virtual toggle event 8 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 9 | 400009 | 03; 06; 16 | Virtual toggle event 9 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 10 | 400009 | 03; 06; 16 | Virtual toggle event 10 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 11 | 400009 | 03; 06; 16 | Virtual toggle event 11 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 12 | 400009 | 03; 06; 16 | Virtual toggle event 12 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 13 | 400009 | 03; 06; 16 | Virtual toggle event 13 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 14 | 400009 | 03; 06; 16 | Virtual toggle event 14 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 8 | 15 | 400009 | 03; 06; 16 | Virtual toggle event 15 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 1 | 400010 | 03; 06; 16 | Virtual toggle event 16 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 2 | 400010 | 03; 06; 16 | Virtual toggle event 17 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 3 | 400010 | 03; 06; 16 | Virtual toggle event 18 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 4 | 400010 | 03; 06; 16 | Virtual toggle event 19 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 5 | 400010 | 03; 06; 16 | Virtual toggle event 20 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 6 | 400010 | 03; 06; 16 | Virtual toggle event 21 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 7 | 400010 | 03; 06; 16 | Virtual toggle event 22 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 8 | 400010 | 03; 06; 16 | Virtual toggle event 23 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 9 | 400010 | 03; 06; 16 | Virtual toggle event 24 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 10 | 400010 | 03; 06; 16 | Virtual toggle event 25 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 11 | 400010 | 03; 06; 16 | Virtual toggle event 26 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 12 | 400010 | 03; 06; 16 | Virtual toggle event 27 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 13 | 400010 | 03; 06; 16 | Virtual toggle event 28 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 14 | 400010 | 03; 06; 16 | Virtual toggle event 29 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 9 | 15 | 400010 | 03; 06; 16 | Virtual toggle event 30 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X | X | X | X | X | X
Control command | 10 | 8 | 400011 | 03; 06; 16 | Nominal setting 5 | BOOL | [5 empty] | X
Control command | 10 | 9 | 400011 | 03; 06; 16 | Nominal setting 6 | BOOL | [5 empty] | X
Control command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X | X | X | X | X
Control command | 13 | 1 | 400014 | 03; 06; 16 | Enable external frequency control | BOOL | [5 empty] | X | X
Control command | 13 | 2 | 400014 | 03; 06; 16 | Disable external frequency control | BOOL | [5 empty] | X | X
Control command | 13 | 3 | 400014 | 03; 06; 16 | Enable external voltage control | BOOL | [5 empty] | X | X
Control command | 13 | 4 | 400014 | 03; 06; 16 | Disable external voltage control | BOOL | [5 empty] | X | X
Control command | 13 | 5 | 400014 | 03; 06; 16 | Enable external power control | BOOL |  |  |  |  | X | X | X
Control command | 13 | 6 | 400014 | 03; 06; 16 | Disable external power control | BOOL |  |  |  |  | X | X | X
Control command | 13 | 7 | 400014 | 03; 06; 16 | Enable external VAr control | BOOL | [5 empty] | X | X
Control command | 13 | 8 | 400014 | 03; 06; 16 | Disable external VAr control | BOOL | [5 empty] | X | X
Control command | 13 | 9 | 400014 | 03; 06; 16 | Enable external CosPhi control | BOOL | [5 empty] | X | X
Control command | 13 | 10 | 400014 | 03; 06; 16 | Disable external CosPhi control | BOOL | [5 empty] | X | X
Control command | 13 | 11 | 400014 | 03; 06; 16 | Enable PM base load | BOOL | [5 empty] | X
Control command | 13 | 12 | 400014 | 03; 06; 16 | Disable PM base load | BOOL | [5 empty] | X
Control command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X | X | X | X | X | X
Write area 1 (PLC/external system to iE 150H) | 46100 |  | 446101 | 03; 06; 16 | Available PV power. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_P_available will be used by logics. | INT32s | ABCD | 0 | kW* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46102 |  | 446103 | 03; 06; 16 | Active PV power. | INT32s | ABCD | 0 | kW* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46110 |  | 446111 | 03; 06; 16 | Available PV apparent power. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_S_available will be used by logics. | INT32s | ABCD | 0 | kVA* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46112 |  | 446113 | 03; 06; 16 | External PV spinning reserve request | INT32s | ABCD | 0 | kW |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46114 |  | 446115 | 03; 06; 16 | Current operation mode of the PV plant: 200: Ready for operation | INT32s | ABCD | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46116 |  | 446117 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on DEIF side. | INT32s | ABCD | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46120 |  | 446121 | 03; 06; 16 | To raise warning and shutdown alarms on DEIF side 100: Warning. 200: Shutdown. 300: Warning & Shutdown. | INT32s | ABCD | 0 | kW |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46122 |  | 446123 | 03; 06; 16 | Reactive PV power | INT32s | ABCD | 0 | kvar* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46124 |  | 446125 | 03; 06; 16 | Apparent PV power | INT32s | ABCD | 0 | kVA* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46128 |  | 446129 | 03; 06; 16 | Available PV reactive power in Q1. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_Q_available_Q1 will be used by logics. | INT32s | ABCD | 0 | kVAr* |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46130 |  | 446131 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46131 |  | 446132 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46132 |  | 446133 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46133 |  | 446134 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 1 | Deg C |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46134 |  | 446135 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 1 | Deg C |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46135 |  | 446136 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 1 | Deg C |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46136 |  | 446137 | 03; 06; 16 | Global horizontal irradiation [W/m2] | INT16s | AB | 0 | W/m2 |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46137 |  | 446138 | 03; 06; 16 | Ambient temperature [C] | INT16s | AB | 1 | Deg C |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46138 |  | 446139 | 03; 06; 16 | Relative humidity [%] | INT16s | AB | 0 | % |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46139 |  | 446140 | 03; 06; 16 | Barometric pressure [hPa] | INT16s | AB | 0 | hPa |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46140 |  | 446141 | 03; 06; 16 | Wind speed [m/s] | INT16s | AB | 0 | m/s |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46141 |  | 446142 | 03; 06; 16 | Wind direction [deg] | INT16s | AB | 0 | deg |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46142 |  | 446143 | 03; 06; 16 | Rain fall [mm] | INT16s | AB | 0 | mm |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46143 |  | 446144 | 03; 06; 16 | Snow depth [mm] | INT16s | AB | 0 | mm |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46144 |  | 446145 | 03; 06; 16 | Available PV reactive power in Q2. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_Q_available_Q2 will be used by logics. | INT32s | ABCD | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46146 |  | 446147 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q3. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_Q_available_Q3 will be used by logics. | INT32s | ABCD | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46148 |  | 446149 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q4. <0: Nominal power setting in the iE 150H will be used by logics. >=0: PV_Q_available_Q4 will be used by logics. | INT32s | ABCD | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46182 |  | 446183 | 03; 06; 16 | Active mains power. | INT16s | AB | 0 | kW |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46183 |  | 446184 | 03; 06; 16 | Reactive mains power. | INT16s | AB | 0 | kvar |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46184 |  | 446185 | 03; 06; 16 | GB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46185 |  | 446186 | 03; 06; 16 | MB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  |  | X
Write area 1 (PLC/external system to iE 150H) | 46186 |  | 446187 | 03; 06; 16 | MB open feedback bitwise from genset 01..16 | INT16s | AB | 0 |  |  |  |  | X
Weather area | 46432 |  | 446433 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 |  |  |  | X
Weather area | 46433 |  | 446434 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 |  |  |  | X
Weather area | 46434 |  | 446435 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 |  |  |  | X
Weather area | 46435 |  | 446436 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 |  |  |  | X
Weather area | 46436 |  | 446437 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 0 | Deg C |  |  |  | X
Weather area | 46437 |  | 446438 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 0 | Deg C |  |  |  | X
Weather area | 46438 |  | 446439 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 0 | Deg C |  |  |  | X
Weather area | 46439 |  | 446440 | 03; 06; 16 | Back of module temperature sensor - global | INT16s | AB | 0 | Deg C |  |  |  | X
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X | X | X | X | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X | X | X | X | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | BTB | MAINS | GEN | GEN-H | ENG | ATS
PMS lite | 40000 | 0 | 340001 | 04 |  | ID present GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 1 | 340001 | 04 |  | ID present GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 2 | 340001 | 04 |  | ID present GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 3 | 340001 | 04 |  | ID present GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 4 | 340001 | 04 |  | ID present GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 5 | 340001 | 04 |  | ID present GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 6 | 340001 | 04 |  | ID present GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 7 | 340001 | 04 |  | ID present GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 8 | 340001 | 04 |  | ID present GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 9 | 340001 | 04 |  | ID present GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 10 | 340001 | 04 |  | ID present GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 11 | 340001 | 04 |  | ID present GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 12 | 340001 | 04 |  | ID present GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 13 | 340001 | 04 |  | ID present GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 14 | 340001 | 04 |  | ID present GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40000 | 15 | 340001 | 04 |  | ID present GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 0 | 340002 | 04 |  | ID present GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 1 | 340002 | 04 |  | ID present GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 2 | 340002 | 04 |  | ID present GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 3 | 340002 | 04 |  | ID present GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 4 | 340002 | 04 |  | ID present GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 5 | 340002 | 04 |  | ID present GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 6 | 340002 | 04 |  | ID present GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 7 | 340002 | 04 |  | ID present GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 8 | 340002 | 04 |  | ID present GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 9 | 340002 | 04 |  | ID present GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 10 | 340002 | 04 |  | ID present GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 11 | 340002 | 04 |  | ID present GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 12 | 340002 | 04 |  | ID present GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 13 | 340002 | 04 |  | ID present GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 14 | 340002 | 04 |  | ID present GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40001 | 15 | 340002 | 04 |  | ID present GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 0 | 340003 | 04 |  | ID present GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 1 | 340003 | 04 |  | ID present GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 2 | 340003 | 04 |  | ID present GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 3 | 340003 | 04 |  | ID present GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 4 | 340003 | 04 |  | ID present GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 5 | 340003 | 04 |  | ID present GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 6 | 340003 | 04 |  | ID present GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 7 | 340003 | 04 |  | ID present GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 8 | 340003 | 04 |  | ID present GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 9 | 340003 | 04 |  | ID present GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 10 | 340003 | 04 |  | ID present GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 11 | 340003 | 04 |  | ID present GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 12 | 340003 | 04 |  | ID present GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 13 | 340003 | 04 |  | ID present GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 14 | 340003 | 04 |  | ID present GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40002 | 15 | 340003 | 04 |  | ID present GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 0 | 340004 | 04 |  | ID present GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 1 | 340004 | 04 |  | ID present GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 2 | 340004 | 04 |  | ID present GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 3 | 340004 | 04 |  | ID present GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 4 | 340004 | 04 |  | ID present GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 5 | 340004 | 04 |  | ID present GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 6 | 340004 | 04 |  | ID present GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 7 | 340004 | 04 |  | ID present GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 8 | 340004 | 04 |  | ID present GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 9 | 340004 | 04 |  | ID present GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 10 | 340004 | 04 |  | ID present GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 11 | 340004 | 04 |  | ID present GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 12 | 340004 | 04 |  | ID present GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 13 | 340004 | 04 |  | ID present GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 14 | 340004 | 04 |  | ID present GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40003 | 15 | 340004 | 04 |  | ID present GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 0 | 340005 | 04 |  | ID present GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 1 | 340005 | 04 |  | ID present GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 2 | 340005 | 04 |  | ID present GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 3 | 340005 | 04 |  | ID present GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 4 | 340005 | 04 |  | ID present GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 5 | 340005 | 04 |  | ID present GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 6 | 340005 | 04 |  | ID present GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 7 | 340005 | 04 |  | ID present GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 8 | 340005 | 04 |  | ID present GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 9 | 340005 | 04 |  | ID present GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 10 | 340005 | 04 |  | ID present GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 11 | 340005 | 04 |  | ID present GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 12 | 340005 | 04 |  | ID present GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 13 | 340005 | 04 |  | ID present GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 14 | 340005 | 04 |  | ID present GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40004 | 15 | 340005 | 04 |  | ID present GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 0 | 340006 | 04 |  | ID present GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 1 | 340006 | 04 |  | ID present GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 2 | 340006 | 04 |  | ID present GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 3 | 340006 | 04 |  | ID present GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 4 | 340006 | 04 |  | ID present GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 5 | 340006 | 04 |  | ID present GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 6 | 340006 | 04 |  | ID present GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 7 | 340006 | 04 |  | ID present GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 8 | 340006 | 04 |  | ID present GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 9 | 340006 | 04 |  | ID present GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 10 | 340006 | 04 |  | ID present GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 11 | 340006 | 04 |  | ID present GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 12 | 340006 | 04 |  | ID present GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 13 | 340006 | 04 |  | ID present GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 14 | 340006 | 04 |  | ID present GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40005 | 15 | 340006 | 04 |  | ID present GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 0 | 340007 | 04 |  | ID present GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 1 | 340007 | 04 |  | ID present GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 2 | 340007 | 04 |  | ID present GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 3 | 340007 | 04 |  | ID present GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 4 | 340007 | 04 |  | ID present GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 5 | 340007 | 04 |  | ID present GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 6 | 340007 | 04 |  | ID present GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 7 | 340007 | 04 |  | ID present GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 8 | 340007 | 04 |  | ID present GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 9 | 340007 | 04 |  | ID present GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 10 | 340007 | 04 |  | ID present GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 11 | 340007 | 04 |  | ID present GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 12 | 340007 | 04 |  | ID present GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 13 | 340007 | 04 |  | ID present GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 14 | 340007 | 04 |  | ID present GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40006 | 15 | 340007 | 04 |  | ID present GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 0 | 340008 | 04 |  | ID present GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 1 | 340008 | 04 |  | ID present GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 2 | 340008 | 04 |  | ID present GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 3 | 340008 | 04 |  | ID present GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 4 | 340008 | 04 |  | ID present GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 5 | 340008 | 04 |  | ID present GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 6 | 340008 | 04 |  | ID present GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 7 | 340008 | 04 |  | ID present GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 8 | 340008 | 04 |  | ID present GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 9 | 340008 | 04 |  | ID present GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 10 | 340008 | 04 |  | ID present GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 11 | 340008 | 04 |  | ID present GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 12 | 340008 | 04 |  | ID present GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 13 | 340008 | 04 |  | ID present GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 14 | 340008 | 04 |  | ID present GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40007 | 15 | 340008 | 04 |  | ID present GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 0 | 340009 | 04 |  | ID present GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 1 | 340009 | 04 |  | ID present GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 2 | 340009 | 04 |  | ID present GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 3 | 340009 | 04 |  | ID present GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 4 | 340009 | 04 |  | ID present GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 5 | 340009 | 04 |  | ID present GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 6 | 340009 | 04 |  | ID present GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 7 | 340009 | 04 |  | ID present GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 8 | 340009 | 04 |  | ID present GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 9 | 340009 | 04 |  | ID present GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 10 | 340009 | 04 |  | ID present GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 11 | 340009 | 04 |  | ID present GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 12 | 340009 | 04 |  | ID present GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 13 | 340009 | 04 |  | ID present GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 14 | 340009 | 04 |  | ID present GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40008 | 15 | 340009 | 04 |  | ID present GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 0 | 340010 | 04 |  | ID present GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 1 | 340010 | 04 |  | ID present GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 2 | 340010 | 04 |  | ID present GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 3 | 340010 | 04 |  | ID present GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 4 | 340010 | 04 |  | ID present GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 5 | 340010 | 04 |  | ID present GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 6 | 340010 | 04 |  | ID present GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 7 | 340010 | 04 |  | ID present GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 8 | 340010 | 04 |  | ID present GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 9 | 340010 | 04 |  | ID present GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 10 | 340010 | 04 |  | ID present GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 11 | 340010 | 04 |  | ID present GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 12 | 340010 | 04 |  | ID present GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 13 | 340010 | 04 |  | ID present GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 14 | 340010 | 04 |  | ID present GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40009 | 15 | 340010 | 04 |  | ID present GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 0 | 340011 | 04 |  | ID present GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 1 | 340011 | 04 |  | ID present GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 2 | 340011 | 04 |  | ID present GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 3 | 340011 | 04 |  | ID present GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 4 | 340011 | 04 |  | ID present GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 5 | 340011 | 04 |  | ID present GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 6 | 340011 | 04 |  | ID present GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 7 | 340011 | 04 |  | ID present GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 8 | 340011 | 04 |  | ID present GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 9 | 340011 | 04 |  | ID present GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 10 | 340011 | 04 |  | ID present GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 11 | 340011 | 04 |  | ID present GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 12 | 340011 | 04 |  | ID present GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 13 | 340011 | 04 |  | ID present GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 14 | 340011 | 04 |  | ID present GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40010 | 15 | 340011 | 04 |  | ID present GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 0 | 340012 | 04 |  | ID present GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 1 | 340012 | 04 |  | ID present GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 2 | 340012 | 04 |  | ID present GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 3 | 340012 | 04 |  | ID present GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 4 | 340012 | 04 |  | ID present GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 5 | 340012 | 04 |  | ID present GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 6 | 340012 | 04 |  | ID present GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 7 | 340012 | 04 |  | ID present GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 8 | 340012 | 04 |  | ID present GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 9 | 340012 | 04 |  | ID present GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 10 | 340012 | 04 |  | ID present GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 11 | 340012 | 04 |  | ID present GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 12 | 340012 | 04 |  | ID present GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 13 | 340012 | 04 |  | ID present GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 14 | 340012 | 04 |  | ID present GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40011 | 15 | 340012 | 04 |  | ID present GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 0 | 340013 | 04 |  | ID present GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 1 | 340013 | 04 |  | ID present GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 2 | 340013 | 04 |  | ID present GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 3 | 340013 | 04 |  | ID present GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 4 | 340013 | 04 |  | ID present GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 5 | 340013 | 04 |  | ID present GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 6 | 340013 | 04 |  | ID present GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 7 | 340013 | 04 |  | ID present GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 8 | 340013 | 04 |  | ID present GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 9 | 340013 | 04 |  | ID present GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 10 | 340013 | 04 |  | ID present GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 11 | 340013 | 04 |  | ID present GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 12 | 340013 | 04 |  | ID present GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 13 | 340013 | 04 |  | ID present GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 14 | 340013 | 04 |  | ID present GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40012 | 15 | 340013 | 04 |  | ID present GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 0 | 340014 | 04 |  | ID present GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 1 | 340014 | 04 |  | ID present GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 2 | 340014 | 04 |  | ID present GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 3 | 340014 | 04 |  | ID present GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 4 | 340014 | 04 |  | ID present GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 5 | 340014 | 04 |  | ID present GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 6 | 340014 | 04 |  | ID present GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 7 | 340014 | 04 |  | ID present GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 8 | 340014 | 04 |  | ID present GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 9 | 340014 | 04 |  | ID present GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 10 | 340014 | 04 |  | ID present GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 11 | 340014 | 04 |  | ID present GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 12 | 340014 | 04 |  | ID present GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 13 | 340014 | 04 |  | ID present GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 14 | 340014 | 04 |  | ID present GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40013 | 15 | 340014 | 04 |  | ID present GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 0 | 340015 | 04 |  | ID present GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 1 | 340015 | 04 |  | ID present GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 2 | 340015 | 04 |  | ID present GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 3 | 340015 | 04 |  | ID present GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 4 | 340015 | 04 |  | ID present GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 5 | 340015 | 04 |  | ID present GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 6 | 340015 | 04 |  | ID present GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 7 | 340015 | 04 |  | ID present GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 8 | 340015 | 04 |  | ID present GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 9 | 340015 | 04 |  | ID present GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 10 | 340015 | 04 |  | ID present GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 11 | 340015 | 04 |  | ID present GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 12 | 340015 | 04 |  | ID present GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 13 | 340015 | 04 |  | ID present GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 14 | 340015 | 04 |  | ID present GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40014 | 15 | 340015 | 04 |  | ID present GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 0 | 340016 | 04 |  | ID present GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 1 | 340016 | 04 |  | ID present GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 2 | 340016 | 04 |  | ID present GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 3 | 340016 | 04 |  | ID present GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 4 | 340016 | 04 |  | ID present GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 5 | 340016 | 04 |  | ID present GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 6 | 340016 | 04 |  | ID present GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 7 | 340016 | 04 |  | ID present GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 8 | 340016 | 04 |  | ID present GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 9 | 340016 | 04 |  | ID present GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 10 | 340016 | 04 |  | ID present GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 11 | 340016 | 04 |  | ID present GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 12 | 340016 | 04 |  | ID present GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40015 | 13 | 340016 | 04 |  | ID present GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 0 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 1 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 2 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 3 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 4 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 5 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 6 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 7 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 8 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 9 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 10 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 11 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 12 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 13 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 14 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40016 | 15 | 340017 | 04 |  | ID active (GB closed and loadshare) GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 0 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 1 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 2 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 3 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 4 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 5 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 6 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 7 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 8 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 9 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 10 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 11 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 12 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 13 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 14 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40017 | 15 | 340018 | 04 |  | ID active (GB closed and loadshare) GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 0 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 1 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 2 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 3 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 4 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 5 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 6 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 7 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 8 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 9 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 10 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 11 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 12 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 13 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 14 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40018 | 15 | 340019 | 04 |  | ID active (GB closed and loadshare) GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 0 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 1 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 2 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 3 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 4 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 5 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 6 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 7 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 8 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 9 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 10 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 11 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 12 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 13 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 14 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40019 | 15 | 340020 | 04 |  | ID active (GB closed and loadshare) GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 0 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 1 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 2 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 3 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 4 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 5 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 6 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 7 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 8 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 9 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 10 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 11 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 12 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 13 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 14 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40020 | 15 | 340021 | 04 |  | ID active (GB closed and loadshare) GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 0 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 1 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 2 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 3 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 4 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 5 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 6 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 7 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 8 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 9 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 10 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 11 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 12 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 13 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 14 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40021 | 15 | 340022 | 04 |  | ID active (GB closed and loadshare) GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 0 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 1 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 2 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 3 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 4 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 5 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 6 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 7 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 8 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 9 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 10 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 11 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 12 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 13 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 14 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40022 | 15 | 340023 | 04 |  | ID active (GB closed and loadshare) GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 0 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 1 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 2 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 3 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 4 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 5 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 6 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 7 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 8 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 9 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 10 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 11 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 12 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 13 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 14 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40023 | 15 | 340024 | 04 |  | ID active (GB closed and loadshare) GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 0 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 1 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 2 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 3 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 4 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 5 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 6 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 7 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 8 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 9 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 10 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 11 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 12 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 13 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 14 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40024 | 15 | 340025 | 04 |  | ID active (GB closed and loadshare) GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 0 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 1 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 2 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 3 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 4 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 5 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 6 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 7 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 8 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 9 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 10 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 11 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 12 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 13 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 14 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40025 | 15 | 340026 | 04 |  | ID active (GB closed and loadshare) GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 0 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 1 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 2 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 3 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 4 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 5 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 6 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 7 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 8 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 9 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 10 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 11 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 12 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 13 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 14 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40026 | 15 | 340027 | 04 |  | ID active (GB closed and loadshare) GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 0 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 1 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 2 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 3 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 4 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 5 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 6 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 7 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 8 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 9 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 10 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 11 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 12 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 13 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 14 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40027 | 15 | 340028 | 04 |  | ID active (GB closed and loadshare) GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 0 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 1 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 2 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 3 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 4 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 5 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 6 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 7 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 8 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 9 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 10 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 11 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 12 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 13 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 14 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40028 | 15 | 340029 | 04 |  | ID active (GB closed and loadshare) GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 0 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 1 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 2 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 3 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 4 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 5 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 6 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 7 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 8 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 9 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 10 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 11 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 12 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 13 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 14 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40029 | 15 | 340030 | 04 |  | ID active (GB closed and loadshare) GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 0 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 1 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 2 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 3 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 4 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 5 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 6 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 7 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 8 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 9 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 10 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 11 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 12 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 13 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 14 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40030 | 15 | 340031 | 04 |  | ID active (GB closed and loadshare) GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 0 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 1 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 2 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 3 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 4 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 5 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 6 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 7 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 8 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 9 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 10 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 11 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 12 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40031 | 13 | 340032 | 04 |  | ID active (GB closed and loadshare) GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 0 | 340033 | 04 |  | ID present or active GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 1 | 340033 | 04 |  | ID present or active GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 2 | 340033 | 04 |  | ID present or active GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 3 | 340033 | 04 |  | ID present or active GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 4 | 340033 | 04 |  | ID present or active GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 5 | 340033 | 04 |  | ID present or active GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 6 | 340033 | 04 |  | ID present or active GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 7 | 340033 | 04 |  | ID present or active GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 8 | 340033 | 04 |  | ID present or active GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 9 | 340033 | 04 |  | ID present or active GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 10 | 340033 | 04 |  | ID present or active GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 11 | 340033 | 04 |  | ID present or active GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 12 | 340033 | 04 |  | ID present or active GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 13 | 340033 | 04 |  | ID present or active GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 14 | 340033 | 04 |  | ID present or active GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40032 | 15 | 340033 | 04 |  | ID present or active GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 0 | 340034 | 04 |  | ID present or active GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 1 | 340034 | 04 |  | ID present or active GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 2 | 340034 | 04 |  | ID present or active GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 3 | 340034 | 04 |  | ID present or active GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 4 | 340034 | 04 |  | ID present or active GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 5 | 340034 | 04 |  | ID present or active GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 6 | 340034 | 04 |  | ID present or active GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 7 | 340034 | 04 |  | ID present or active GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 8 | 340034 | 04 |  | ID present or active GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 9 | 340034 | 04 |  | ID present or active GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 10 | 340034 | 04 |  | ID present or active GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 11 | 340034 | 04 |  | ID present or active GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 12 | 340034 | 04 |  | ID present or active GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 13 | 340034 | 04 |  | ID present or active GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 14 | 340034 | 04 |  | ID present or active GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40033 | 15 | 340034 | 04 |  | ID present or active GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 0 | 340035 | 04 |  | ID present or active GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 1 | 340035 | 04 |  | ID present or active GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 2 | 340035 | 04 |  | ID present or active GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 3 | 340035 | 04 |  | ID present or active GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 4 | 340035 | 04 |  | ID present or active GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 5 | 340035 | 04 |  | ID present or active GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 6 | 340035 | 04 |  | ID present or active GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 7 | 340035 | 04 |  | ID present or active GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 8 | 340035 | 04 |  | ID present or active GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 9 | 340035 | 04 |  | ID present or active GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 10 | 340035 | 04 |  | ID present or active GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 11 | 340035 | 04 |  | ID present or active GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 12 | 340035 | 04 |  | ID present or active GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 13 | 340035 | 04 |  | ID present or active GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 14 | 340035 | 04 |  | ID present or active GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40034 | 15 | 340035 | 04 |  | ID present or active GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 0 | 340036 | 04 |  | ID present or active GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 1 | 340036 | 04 |  | ID present or active GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 2 | 340036 | 04 |  | ID present or active GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 3 | 340036 | 04 |  | ID present or active GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 4 | 340036 | 04 |  | ID present or active GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 5 | 340036 | 04 |  | ID present or active GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 6 | 340036 | 04 |  | ID present or active GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 7 | 340036 | 04 |  | ID present or active GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 8 | 340036 | 04 |  | ID present or active GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 9 | 340036 | 04 |  | ID present or active GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 10 | 340036 | 04 |  | ID present or active GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 11 | 340036 | 04 |  | ID present or active GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 12 | 340036 | 04 |  | ID present or active GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 13 | 340036 | 04 |  | ID present or active GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 14 | 340036 | 04 |  | ID present or active GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40035 | 15 | 340036 | 04 |  | ID present or active GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 0 | 340037 | 04 |  | ID present or active GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 1 | 340037 | 04 |  | ID present or active GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 2 | 340037 | 04 |  | ID present or active GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 3 | 340037 | 04 |  | ID present or active GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 4 | 340037 | 04 |  | ID present or active GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 5 | 340037 | 04 |  | ID present or active GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 6 | 340037 | 04 |  | ID present or active GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 7 | 340037 | 04 |  | ID present or active GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 8 | 340037 | 04 |  | ID present or active GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 9 | 340037 | 04 |  | ID present or active GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 10 | 340037 | 04 |  | ID present or active GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 11 | 340037 | 04 |  | ID present or active GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 12 | 340037 | 04 |  | ID present or active GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 13 | 340037 | 04 |  | ID present or active GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 14 | 340037 | 04 |  | ID present or active GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40036 | 15 | 340037 | 04 |  | ID present or active GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 0 | 340038 | 04 |  | ID present or active GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 1 | 340038 | 04 |  | ID present or active GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 2 | 340038 | 04 |  | ID present or active GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 3 | 340038 | 04 |  | ID present or active GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 4 | 340038 | 04 |  | ID present or active GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 5 | 340038 | 04 |  | ID present or active GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 6 | 340038 | 04 |  | ID present or active GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 7 | 340038 | 04 |  | ID present or active GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 8 | 340038 | 04 |  | ID present or active GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 9 | 340038 | 04 |  | ID present or active GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 10 | 340038 | 04 |  | ID present or active GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 11 | 340038 | 04 |  | ID present or active GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 12 | 340038 | 04 |  | ID present or active GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 13 | 340038 | 04 |  | ID present or active GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 14 | 340038 | 04 |  | ID present or active GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40037 | 15 | 340038 | 04 |  | ID present or active GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 0 | 340039 | 04 |  | ID present or active GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 1 | 340039 | 04 |  | ID present or active GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 2 | 340039 | 04 |  | ID present or active GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 3 | 340039 | 04 |  | ID present or active GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 4 | 340039 | 04 |  | ID present or active GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 5 | 340039 | 04 |  | ID present or active GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 6 | 340039 | 04 |  | ID present or active GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 7 | 340039 | 04 |  | ID present or active GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 8 | 340039 | 04 |  | ID present or active GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 9 | 340039 | 04 |  | ID present or active GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 10 | 340039 | 04 |  | ID present or active GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 11 | 340039 | 04 |  | ID present or active GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 12 | 340039 | 04 |  | ID present or active GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 13 | 340039 | 04 |  | ID present or active GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 14 | 340039 | 04 |  | ID present or active GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40038 | 15 | 340039 | 04 |  | ID present or active GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 0 | 340040 | 04 |  | ID present or active GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 1 | 340040 | 04 |  | ID present or active GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 2 | 340040 | 04 |  | ID present or active GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 3 | 340040 | 04 |  | ID present or active GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 4 | 340040 | 04 |  | ID present or active GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 5 | 340040 | 04 |  | ID present or active GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 6 | 340040 | 04 |  | ID present or active GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 7 | 340040 | 04 |  | ID present or active GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 8 | 340040 | 04 |  | ID present or active GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 9 | 340040 | 04 |  | ID present or active GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 10 | 340040 | 04 |  | ID present or active GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 11 | 340040 | 04 |  | ID present or active GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 12 | 340040 | 04 |  | ID present or active GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 13 | 340040 | 04 |  | ID present or active GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 14 | 340040 | 04 |  | ID present or active GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40039 | 15 | 340040 | 04 |  | ID present or active GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 0 | 340041 | 04 |  | ID present or active GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 1 | 340041 | 04 |  | ID present or active GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 2 | 340041 | 04 |  | ID present or active GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 3 | 340041 | 04 |  | ID present or active GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 4 | 340041 | 04 |  | ID present or active GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 5 | 340041 | 04 |  | ID present or active GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 6 | 340041 | 04 |  | ID present or active GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 7 | 340041 | 04 |  | ID present or active GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 8 | 340041 | 04 |  | ID present or active GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 9 | 340041 | 04 |  | ID present or active GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 10 | 340041 | 04 |  | ID present or active GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 11 | 340041 | 04 |  | ID present or active GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 12 | 340041 | 04 |  | ID present or active GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 13 | 340041 | 04 |  | ID present or active GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 14 | 340041 | 04 |  | ID present or active GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40040 | 15 | 340041 | 04 |  | ID present or active GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 0 | 340042 | 04 |  | ID present or active GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 1 | 340042 | 04 |  | ID present or active GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 2 | 340042 | 04 |  | ID present or active GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 3 | 340042 | 04 |  | ID present or active GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 4 | 340042 | 04 |  | ID present or active GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 5 | 340042 | 04 |  | ID present or active GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 6 | 340042 | 04 |  | ID present or active GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 7 | 340042 | 04 |  | ID present or active GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 8 | 340042 | 04 |  | ID present or active GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 9 | 340042 | 04 |  | ID present or active GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 10 | 340042 | 04 |  | ID present or active GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 11 | 340042 | 04 |  | ID present or active GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 12 | 340042 | 04 |  | ID present or active GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 13 | 340042 | 04 |  | ID present or active GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 14 | 340042 | 04 |  | ID present or active GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40041 | 15 | 340042 | 04 |  | ID present or active GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 0 | 340043 | 04 |  | ID present or active GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 1 | 340043 | 04 |  | ID present or active GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 2 | 340043 | 04 |  | ID present or active GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 3 | 340043 | 04 |  | ID present or active GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 4 | 340043 | 04 |  | ID present or active GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 5 | 340043 | 04 |  | ID present or active GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 6 | 340043 | 04 |  | ID present or active GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 7 | 340043 | 04 |  | ID present or active GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 8 | 340043 | 04 |  | ID present or active GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 9 | 340043 | 04 |  | ID present or active GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 10 | 340043 | 04 |  | ID present or active GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 11 | 340043 | 04 |  | ID present or active GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 12 | 340043 | 04 |  | ID present or active GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 13 | 340043 | 04 |  | ID present or active GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 14 | 340043 | 04 |  | ID present or active GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40042 | 15 | 340043 | 04 |  | ID present or active GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 0 | 340044 | 04 |  | ID present or active GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 1 | 340044 | 04 |  | ID present or active GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 2 | 340044 | 04 |  | ID present or active GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 3 | 340044 | 04 |  | ID present or active GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 4 | 340044 | 04 |  | ID present or active GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 5 | 340044 | 04 |  | ID present or active GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 6 | 340044 | 04 |  | ID present or active GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 7 | 340044 | 04 |  | ID present or active GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 8 | 340044 | 04 |  | ID present or active GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 9 | 340044 | 04 |  | ID present or active GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 10 | 340044 | 04 |  | ID present or active GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 11 | 340044 | 04 |  | ID present or active GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 12 | 340044 | 04 |  | ID present or active GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 13 | 340044 | 04 |  | ID present or active GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 14 | 340044 | 04 |  | ID present or active GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40043 | 15 | 340044 | 04 |  | ID present or active GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 0 | 340045 | 04 |  | ID present or active GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 1 | 340045 | 04 |  | ID present or active GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 2 | 340045 | 04 |  | ID present or active GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 3 | 340045 | 04 |  | ID present or active GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 4 | 340045 | 04 |  | ID present or active GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 5 | 340045 | 04 |  | ID present or active GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 6 | 340045 | 04 |  | ID present or active GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 7 | 340045 | 04 |  | ID present or active GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 8 | 340045 | 04 |  | ID present or active GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 9 | 340045 | 04 |  | ID present or active GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 10 | 340045 | 04 |  | ID present or active GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 11 | 340045 | 04 |  | ID present or active GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 12 | 340045 | 04 |  | ID present or active GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 13 | 340045 | 04 |  | ID present or active GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 14 | 340045 | 04 |  | ID present or active GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40044 | 15 | 340045 | 04 |  | ID present or active GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 0 | 340046 | 04 |  | ID present or active GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 1 | 340046 | 04 |  | ID present or active GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 2 | 340046 | 04 |  | ID present or active GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 3 | 340046 | 04 |  | ID present or active GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 4 | 340046 | 04 |  | ID present or active GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 5 | 340046 | 04 |  | ID present or active GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 6 | 340046 | 04 |  | ID present or active GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 7 | 340046 | 04 |  | ID present or active GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 8 | 340046 | 04 |  | ID present or active GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 9 | 340046 | 04 |  | ID present or active GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 10 | 340046 | 04 |  | ID present or active GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 11 | 340046 | 04 |  | ID present or active GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 12 | 340046 | 04 |  | ID present or active GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 13 | 340046 | 04 |  | ID present or active GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 14 | 340046 | 04 |  | ID present or active GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40045 | 15 | 340046 | 04 |  | ID present or active GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 0 | 340047 | 04 |  | ID present or active GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 1 | 340047 | 04 |  | ID present or active GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 2 | 340047 | 04 |  | ID present or active GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 3 | 340047 | 04 |  | ID present or active GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 4 | 340047 | 04 |  | ID present or active GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 5 | 340047 | 04 |  | ID present or active GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 6 | 340047 | 04 |  | ID present or active GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 7 | 340047 | 04 |  | ID present or active GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 8 | 340047 | 04 |  | ID present or active GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 9 | 340047 | 04 |  | ID present or active GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 10 | 340047 | 04 |  | ID present or active GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 11 | 340047 | 04 |  | ID present or active GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 12 | 340047 | 04 |  | ID present or active GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 13 | 340047 | 04 |  | ID present or active GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 14 | 340047 | 04 |  | ID present or active GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40046 | 15 | 340047 | 04 |  | ID present or active GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 0 | 340048 | 04 |  | ID present or active GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 1 | 340048 | 04 |  | ID present or active GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 2 | 340048 | 04 |  | ID present or active GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 3 | 340048 | 04 |  | ID present or active GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 4 | 340048 | 04 |  | ID present or active GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 5 | 340048 | 04 |  | ID present or active GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 6 | 340048 | 04 |  | ID present or active GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 7 | 340048 | 04 |  | ID present or active GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 8 | 340048 | 04 |  | ID present or active GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 9 | 340048 | 04 |  | ID present or active GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 10 | 340048 | 04 |  | ID present or active GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 11 | 340048 | 04 |  | ID present or active GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 12 | 340048 | 04 |  | ID present or active GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40047 | 13 | 340048 | 04 |  | ID present or active GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 0 | 340049 | 04 |  | Ready to auto start GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 1 | 340049 | 04 |  | Ready to auto start GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 2 | 340049 | 04 |  | Ready to auto start GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 3 | 340049 | 04 |  | Ready to auto start GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 4 | 340049 | 04 |  | Ready to auto start GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 5 | 340049 | 04 |  | Ready to auto start GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 6 | 340049 | 04 |  | Ready to auto start GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 7 | 340049 | 04 |  | Ready to auto start GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 8 | 340049 | 04 |  | Ready to auto start GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 9 | 340049 | 04 |  | Ready to auto start GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 10 | 340049 | 04 |  | Ready to auto start GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 11 | 340049 | 04 |  | Ready to auto start GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 12 | 340049 | 04 |  | Ready to auto start GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 13 | 340049 | 04 |  | Ready to auto start GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 14 | 340049 | 04 |  | Ready to auto start GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40048 | 15 | 340049 | 04 |  | Ready to auto start GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 0 | 340050 | 04 |  | Ready to auto start GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 1 | 340050 | 04 |  | Ready to auto start GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 2 | 340050 | 04 |  | Ready to auto start GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 3 | 340050 | 04 |  | Ready to auto start GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 4 | 340050 | 04 |  | Ready to auto start GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 5 | 340050 | 04 |  | Ready to auto start GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 6 | 340050 | 04 |  | Ready to auto start GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 7 | 340050 | 04 |  | Ready to auto start GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 8 | 340050 | 04 |  | Ready to auto start GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 9 | 340050 | 04 |  | Ready to auto start GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 10 | 340050 | 04 |  | Ready to auto start GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 11 | 340050 | 04 |  | Ready to auto start GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 12 | 340050 | 04 |  | Ready to auto start GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 13 | 340050 | 04 |  | Ready to auto start GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 14 | 340050 | 04 |  | Ready to auto start GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40049 | 15 | 340050 | 04 |  | Ready to auto start GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 0 | 340051 | 04 |  | Ready to auto start GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 1 | 340051 | 04 |  | Ready to auto start GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 2 | 340051 | 04 |  | Ready to auto start GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 3 | 340051 | 04 |  | Ready to auto start GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 4 | 340051 | 04 |  | Ready to auto start GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 5 | 340051 | 04 |  | Ready to auto start GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 6 | 340051 | 04 |  | Ready to auto start GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 7 | 340051 | 04 |  | Ready to auto start GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 8 | 340051 | 04 |  | Ready to auto start GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 9 | 340051 | 04 |  | Ready to auto start GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 10 | 340051 | 04 |  | Ready to auto start GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 11 | 340051 | 04 |  | Ready to auto start GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 12 | 340051 | 04 |  | Ready to auto start GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 13 | 340051 | 04 |  | Ready to auto start GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 14 | 340051 | 04 |  | Ready to auto start GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40050 | 15 | 340051 | 04 |  | Ready to auto start GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 0 | 340052 | 04 |  | Ready to auto start GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 1 | 340052 | 04 |  | Ready to auto start GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 2 | 340052 | 04 |  | Ready to auto start GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 3 | 340052 | 04 |  | Ready to auto start GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 4 | 340052 | 04 |  | Ready to auto start GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 5 | 340052 | 04 |  | Ready to auto start GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 6 | 340052 | 04 |  | Ready to auto start GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 7 | 340052 | 04 |  | Ready to auto start GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 8 | 340052 | 04 |  | Ready to auto start GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 9 | 340052 | 04 |  | Ready to auto start GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 10 | 340052 | 04 |  | Ready to auto start GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 11 | 340052 | 04 |  | Ready to auto start GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 12 | 340052 | 04 |  | Ready to auto start GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 13 | 340052 | 04 |  | Ready to auto start GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 14 | 340052 | 04 |  | Ready to auto start GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40051 | 15 | 340052 | 04 |  | Ready to auto start GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 0 | 340053 | 04 |  | Ready to auto start GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 1 | 340053 | 04 |  | Ready to auto start GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 2 | 340053 | 04 |  | Ready to auto start GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 3 | 340053 | 04 |  | Ready to auto start GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 4 | 340053 | 04 |  | Ready to auto start GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 5 | 340053 | 04 |  | Ready to auto start GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 6 | 340053 | 04 |  | Ready to auto start GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 7 | 340053 | 04 |  | Ready to auto start GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 8 | 340053 | 04 |  | Ready to auto start GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 9 | 340053 | 04 |  | Ready to auto start GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 10 | 340053 | 04 |  | Ready to auto start GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 11 | 340053 | 04 |  | Ready to auto start GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 12 | 340053 | 04 |  | Ready to auto start GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 13 | 340053 | 04 |  | Ready to auto start GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 14 | 340053 | 04 |  | Ready to auto start GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40052 | 15 | 340053 | 04 |  | Ready to auto start GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 0 | 340054 | 04 |  | Ready to auto start GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 1 | 340054 | 04 |  | Ready to auto start GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 2 | 340054 | 04 |  | Ready to auto start GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 3 | 340054 | 04 |  | Ready to auto start GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 4 | 340054 | 04 |  | Ready to auto start GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 5 | 340054 | 04 |  | Ready to auto start GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 6 | 340054 | 04 |  | Ready to auto start GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 7 | 340054 | 04 |  | Ready to auto start GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 8 | 340054 | 04 |  | Ready to auto start GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 9 | 340054 | 04 |  | Ready to auto start GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 10 | 340054 | 04 |  | Ready to auto start GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 11 | 340054 | 04 |  | Ready to auto start GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 12 | 340054 | 04 |  | Ready to auto start GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 13 | 340054 | 04 |  | Ready to auto start GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 14 | 340054 | 04 |  | Ready to auto start GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40053 | 15 | 340054 | 04 |  | Ready to auto start GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 0 | 340055 | 04 |  | Ready to auto start GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 1 | 340055 | 04 |  | Ready to auto start GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 2 | 340055 | 04 |  | Ready to auto start GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 3 | 340055 | 04 |  | Ready to auto start GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 4 | 340055 | 04 |  | Ready to auto start GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 5 | 340055 | 04 |  | Ready to auto start GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 6 | 340055 | 04 |  | Ready to auto start GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 7 | 340055 | 04 |  | Ready to auto start GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 8 | 340055 | 04 |  | Ready to auto start GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 9 | 340055 | 04 |  | Ready to auto start GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 10 | 340055 | 04 |  | Ready to auto start GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 11 | 340055 | 04 |  | Ready to auto start GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 12 | 340055 | 04 |  | Ready to auto start GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 13 | 340055 | 04 |  | Ready to auto start GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 14 | 340055 | 04 |  | Ready to auto start GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40054 | 15 | 340055 | 04 |  | Ready to auto start GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 0 | 340056 | 04 |  | Ready to auto start GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 1 | 340056 | 04 |  | Ready to auto start GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 2 | 340056 | 04 |  | Ready to auto start GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 3 | 340056 | 04 |  | Ready to auto start GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 4 | 340056 | 04 |  | Ready to auto start GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 5 | 340056 | 04 |  | Ready to auto start GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 6 | 340056 | 04 |  | Ready to auto start GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 7 | 340056 | 04 |  | Ready to auto start GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 8 | 340056 | 04 |  | Ready to auto start GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 9 | 340056 | 04 |  | Ready to auto start GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 10 | 340056 | 04 |  | Ready to auto start GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 11 | 340056 | 04 |  | Ready to auto start GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 12 | 340056 | 04 |  | Ready to auto start GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 13 | 340056 | 04 |  | Ready to auto start GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 14 | 340056 | 04 |  | Ready to auto start GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40055 | 15 | 340056 | 04 |  | Ready to auto start GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 0 | 340057 | 04 |  | Ready to auto start GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 1 | 340057 | 04 |  | Ready to auto start GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 2 | 340057 | 04 |  | Ready to auto start GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 3 | 340057 | 04 |  | Ready to auto start GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 4 | 340057 | 04 |  | Ready to auto start GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 5 | 340057 | 04 |  | Ready to auto start GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 6 | 340057 | 04 |  | Ready to auto start GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 7 | 340057 | 04 |  | Ready to auto start GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 8 | 340057 | 04 |  | Ready to auto start GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 9 | 340057 | 04 |  | Ready to auto start GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 10 | 340057 | 04 |  | Ready to auto start GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 11 | 340057 | 04 |  | Ready to auto start GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 12 | 340057 | 04 |  | Ready to auto start GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 13 | 340057 | 04 |  | Ready to auto start GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 14 | 340057 | 04 |  | Ready to auto start GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40056 | 15 | 340057 | 04 |  | Ready to auto start GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 0 | 340058 | 04 |  | Ready to auto start GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 1 | 340058 | 04 |  | Ready to auto start GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 2 | 340058 | 04 |  | Ready to auto start GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 3 | 340058 | 04 |  | Ready to auto start GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 4 | 340058 | 04 |  | Ready to auto start GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 5 | 340058 | 04 |  | Ready to auto start GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 6 | 340058 | 04 |  | Ready to auto start GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 7 | 340058 | 04 |  | Ready to auto start GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 8 | 340058 | 04 |  | Ready to auto start GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 9 | 340058 | 04 |  | Ready to auto start GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 10 | 340058 | 04 |  | Ready to auto start GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 11 | 340058 | 04 |  | Ready to auto start GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 12 | 340058 | 04 |  | Ready to auto start GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 13 | 340058 | 04 |  | Ready to auto start GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 14 | 340058 | 04 |  | Ready to auto start GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40057 | 15 | 340058 | 04 |  | Ready to auto start GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 0 | 340059 | 04 |  | Ready to auto start GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 1 | 340059 | 04 |  | Ready to auto start GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 2 | 340059 | 04 |  | Ready to auto start GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 3 | 340059 | 04 |  | Ready to auto start GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 4 | 340059 | 04 |  | Ready to auto start GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 5 | 340059 | 04 |  | Ready to auto start GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 6 | 340059 | 04 |  | Ready to auto start GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 7 | 340059 | 04 |  | Ready to auto start GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 8 | 340059 | 04 |  | Ready to auto start GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 9 | 340059 | 04 |  | Ready to auto start GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 10 | 340059 | 04 |  | Ready to auto start GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 11 | 340059 | 04 |  | Ready to auto start GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 12 | 340059 | 04 |  | Ready to auto start GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 13 | 340059 | 04 |  | Ready to auto start GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 14 | 340059 | 04 |  | Ready to auto start GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40058 | 15 | 340059 | 04 |  | Ready to auto start GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 0 | 340060 | 04 |  | Ready to auto start GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 1 | 340060 | 04 |  | Ready to auto start GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 2 | 340060 | 04 |  | Ready to auto start GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 3 | 340060 | 04 |  | Ready to auto start GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 4 | 340060 | 04 |  | Ready to auto start GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 5 | 340060 | 04 |  | Ready to auto start GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 6 | 340060 | 04 |  | Ready to auto start GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 7 | 340060 | 04 |  | Ready to auto start GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 8 | 340060 | 04 |  | Ready to auto start GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 9 | 340060 | 04 |  | Ready to auto start GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 10 | 340060 | 04 |  | Ready to auto start GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 11 | 340060 | 04 |  | Ready to auto start GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 12 | 340060 | 04 |  | Ready to auto start GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 13 | 340060 | 04 |  | Ready to auto start GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 14 | 340060 | 04 |  | Ready to auto start GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40059 | 15 | 340060 | 04 |  | Ready to auto start GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 0 | 340061 | 04 |  | Ready to auto start GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 1 | 340061 | 04 |  | Ready to auto start GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 2 | 340061 | 04 |  | Ready to auto start GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 3 | 340061 | 04 |  | Ready to auto start GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 4 | 340061 | 04 |  | Ready to auto start GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 5 | 340061 | 04 |  | Ready to auto start GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 6 | 340061 | 04 |  | Ready to auto start GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 7 | 340061 | 04 |  | Ready to auto start GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 8 | 340061 | 04 |  | Ready to auto start GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 9 | 340061 | 04 |  | Ready to auto start GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 10 | 340061 | 04 |  | Ready to auto start GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 11 | 340061 | 04 |  | Ready to auto start GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 12 | 340061 | 04 |  | Ready to auto start GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 13 | 340061 | 04 |  | Ready to auto start GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 14 | 340061 | 04 |  | Ready to auto start GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40060 | 15 | 340061 | 04 |  | Ready to auto start GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 0 | 340062 | 04 |  | Ready to auto start GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 1 | 340062 | 04 |  | Ready to auto start GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 2 | 340062 | 04 |  | Ready to auto start GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 3 | 340062 | 04 |  | Ready to auto start GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 4 | 340062 | 04 |  | Ready to auto start GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 5 | 340062 | 04 |  | Ready to auto start GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 6 | 340062 | 04 |  | Ready to auto start GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 7 | 340062 | 04 |  | Ready to auto start GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 8 | 340062 | 04 |  | Ready to auto start GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 9 | 340062 | 04 |  | Ready to auto start GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 10 | 340062 | 04 |  | Ready to auto start GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 11 | 340062 | 04 |  | Ready to auto start GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 12 | 340062 | 04 |  | Ready to auto start GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 13 | 340062 | 04 |  | Ready to auto start GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 14 | 340062 | 04 |  | Ready to auto start GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40061 | 15 | 340062 | 04 |  | Ready to auto start GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 0 | 340063 | 04 |  | Ready to auto start GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 1 | 340063 | 04 |  | Ready to auto start GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 2 | 340063 | 04 |  | Ready to auto start GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 3 | 340063 | 04 |  | Ready to auto start GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 4 | 340063 | 04 |  | Ready to auto start GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 5 | 340063 | 04 |  | Ready to auto start GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 6 | 340063 | 04 |  | Ready to auto start GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 7 | 340063 | 04 |  | Ready to auto start GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 8 | 340063 | 04 |  | Ready to auto start GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 9 | 340063 | 04 |  | Ready to auto start GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 10 | 340063 | 04 |  | Ready to auto start GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 11 | 340063 | 04 |  | Ready to auto start GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 12 | 340063 | 04 |  | Ready to auto start GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 13 | 340063 | 04 |  | Ready to auto start GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 14 | 340063 | 04 |  | Ready to auto start GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40062 | 15 | 340063 | 04 |  | Ready to auto start GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 0 | 340064 | 04 |  | Ready to auto start GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 1 | 340064 | 04 |  | Ready to auto start GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 2 | 340064 | 04 |  | Ready to auto start GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 3 | 340064 | 04 |  | Ready to auto start GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 4 | 340064 | 04 |  | Ready to auto start GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 5 | 340064 | 04 |  | Ready to auto start GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 6 | 340064 | 04 |  | Ready to auto start GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 7 | 340064 | 04 |  | Ready to auto start GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 8 | 340064 | 04 |  | Ready to auto start GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 9 | 340064 | 04 |  | Ready to auto start GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 10 | 340064 | 04 |  | Ready to auto start GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 11 | 340064 | 04 |  | Ready to auto start GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 12 | 340064 | 04 |  | Ready to auto start GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40063 | 13 | 340064 | 04 |  | Ready to auto start GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 0 | 340081 | 04 |  | GEN in auto GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 1 | 340081 | 04 |  | GEN in auto GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 2 | 340081 | 04 |  | GEN in auto GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 3 | 340081 | 04 |  | GEN in auto GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 4 | 340081 | 04 |  | GEN in auto GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 5 | 340081 | 04 |  | GEN in auto GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 6 | 340081 | 04 |  | GEN in auto GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 7 | 340081 | 04 |  | GEN in auto GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 8 | 340081 | 04 |  | GEN in auto GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 9 | 340081 | 04 |  | GEN in auto GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 10 | 340081 | 04 |  | GEN in auto GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 11 | 340081 | 04 |  | GEN in auto GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 12 | 340081 | 04 |  | GEN in auto GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 13 | 340081 | 04 |  | GEN in auto GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 14 | 340081 | 04 |  | GEN in auto GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40080 | 15 | 340081 | 04 |  | GEN in auto GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 0 | 340082 | 04 |  | GEN in auto GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 1 | 340082 | 04 |  | GEN in auto GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 2 | 340082 | 04 |  | GEN in auto GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 3 | 340082 | 04 |  | GEN in auto GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 4 | 340082 | 04 |  | GEN in auto GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 5 | 340082 | 04 |  | GEN in auto GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 6 | 340082 | 04 |  | GEN in auto GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 7 | 340082 | 04 |  | GEN in auto GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 8 | 340082 | 04 |  | GEN in auto GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 9 | 340082 | 04 |  | GEN in auto GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 10 | 340082 | 04 |  | GEN in auto GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 11 | 340082 | 04 |  | GEN in auto GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 12 | 340082 | 04 |  | GEN in auto GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 13 | 340082 | 04 |  | GEN in auto GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 14 | 340082 | 04 |  | GEN in auto GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40081 | 15 | 340082 | 04 |  | GEN in auto GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 0 | 340083 | 04 |  | GEN in auto GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 1 | 340083 | 04 |  | GEN in auto GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 2 | 340083 | 04 |  | GEN in auto GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 3 | 340083 | 04 |  | GEN in auto GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 4 | 340083 | 04 |  | GEN in auto GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 5 | 340083 | 04 |  | GEN in auto GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 6 | 340083 | 04 |  | GEN in auto GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 7 | 340083 | 04 |  | GEN in auto GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 8 | 340083 | 04 |  | GEN in auto GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 9 | 340083 | 04 |  | GEN in auto GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 10 | 340083 | 04 |  | GEN in auto GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 11 | 340083 | 04 |  | GEN in auto GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 12 | 340083 | 04 |  | GEN in auto GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 13 | 340083 | 04 |  | GEN in auto GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 14 | 340083 | 04 |  | GEN in auto GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40082 | 15 | 340083 | 04 |  | GEN in auto GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 0 | 340084 | 04 |  | GEN in auto GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 1 | 340084 | 04 |  | GEN in auto GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 2 | 340084 | 04 |  | GEN in auto GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 3 | 340084 | 04 |  | GEN in auto GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 4 | 340084 | 04 |  | GEN in auto GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 5 | 340084 | 04 |  | GEN in auto GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 6 | 340084 | 04 |  | GEN in auto GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 7 | 340084 | 04 |  | GEN in auto GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 8 | 340084 | 04 |  | GEN in auto GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 9 | 340084 | 04 |  | GEN in auto GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 10 | 340084 | 04 |  | GEN in auto GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 11 | 340084 | 04 |  | GEN in auto GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 12 | 340084 | 04 |  | GEN in auto GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 13 | 340084 | 04 |  | GEN in auto GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 14 | 340084 | 04 |  | GEN in auto GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40083 | 15 | 340084 | 04 |  | GEN in auto GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 0 | 340085 | 04 |  | GEN in auto GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 1 | 340085 | 04 |  | GEN in auto GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 2 | 340085 | 04 |  | GEN in auto GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 3 | 340085 | 04 |  | GEN in auto GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 4 | 340085 | 04 |  | GEN in auto GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 5 | 340085 | 04 |  | GEN in auto GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 6 | 340085 | 04 |  | GEN in auto GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 7 | 340085 | 04 |  | GEN in auto GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 8 | 340085 | 04 |  | GEN in auto GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 9 | 340085 | 04 |  | GEN in auto GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 10 | 340085 | 04 |  | GEN in auto GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 11 | 340085 | 04 |  | GEN in auto GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 12 | 340085 | 04 |  | GEN in auto GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 13 | 340085 | 04 |  | GEN in auto GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 14 | 340085 | 04 |  | GEN in auto GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40084 | 15 | 340085 | 04 |  | GEN in auto GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 0 | 340086 | 04 |  | GEN in auto GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 1 | 340086 | 04 |  | GEN in auto GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 2 | 340086 | 04 |  | GEN in auto GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 3 | 340086 | 04 |  | GEN in auto GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 4 | 340086 | 04 |  | GEN in auto GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 5 | 340086 | 04 |  | GEN in auto GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 6 | 340086 | 04 |  | GEN in auto GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 7 | 340086 | 04 |  | GEN in auto GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 8 | 340086 | 04 |  | GEN in auto GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 9 | 340086 | 04 |  | GEN in auto GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 10 | 340086 | 04 |  | GEN in auto GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 11 | 340086 | 04 |  | GEN in auto GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 12 | 340086 | 04 |  | GEN in auto GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 13 | 340086 | 04 |  | GEN in auto GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 14 | 340086 | 04 |  | GEN in auto GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40085 | 15 | 340086 | 04 |  | GEN in auto GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 0 | 340087 | 04 |  | GEN in auto GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 1 | 340087 | 04 |  | GEN in auto GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 2 | 340087 | 04 |  | GEN in auto GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 3 | 340087 | 04 |  | GEN in auto GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 4 | 340087 | 04 |  | GEN in auto GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 5 | 340087 | 04 |  | GEN in auto GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 6 | 340087 | 04 |  | GEN in auto GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 7 | 340087 | 04 |  | GEN in auto GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 8 | 340087 | 04 |  | GEN in auto GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 9 | 340087 | 04 |  | GEN in auto GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 10 | 340087 | 04 |  | GEN in auto GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 11 | 340087 | 04 |  | GEN in auto GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 12 | 340087 | 04 |  | GEN in auto GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 13 | 340087 | 04 |  | GEN in auto GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 14 | 340087 | 04 |  | GEN in auto GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40086 | 15 | 340087 | 04 |  | GEN in auto GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 0 | 340088 | 04 |  | GEN in auto GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 1 | 340088 | 04 |  | GEN in auto GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 2 | 340088 | 04 |  | GEN in auto GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 3 | 340088 | 04 |  | GEN in auto GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 4 | 340088 | 04 |  | GEN in auto GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 5 | 340088 | 04 |  | GEN in auto GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 6 | 340088 | 04 |  | GEN in auto GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 7 | 340088 | 04 |  | GEN in auto GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 8 | 340088 | 04 |  | GEN in auto GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 9 | 340088 | 04 |  | GEN in auto GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 10 | 340088 | 04 |  | GEN in auto GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 11 | 340088 | 04 |  | GEN in auto GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 12 | 340088 | 04 |  | GEN in auto GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 13 | 340088 | 04 |  | GEN in auto GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 14 | 340088 | 04 |  | GEN in auto GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40087 | 15 | 340088 | 04 |  | GEN in auto GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 0 | 340089 | 04 |  | GEN in auto GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 1 | 340089 | 04 |  | GEN in auto GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 2 | 340089 | 04 |  | GEN in auto GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 3 | 340089 | 04 |  | GEN in auto GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 4 | 340089 | 04 |  | GEN in auto GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 5 | 340089 | 04 |  | GEN in auto GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 6 | 340089 | 04 |  | GEN in auto GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 7 | 340089 | 04 |  | GEN in auto GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 8 | 340089 | 04 |  | GEN in auto GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 9 | 340089 | 04 |  | GEN in auto GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 10 | 340089 | 04 |  | GEN in auto GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 11 | 340089 | 04 |  | GEN in auto GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 12 | 340089 | 04 |  | GEN in auto GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 13 | 340089 | 04 |  | GEN in auto GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 14 | 340089 | 04 |  | GEN in auto GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40088 | 15 | 340089 | 04 |  | GEN in auto GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 0 | 340090 | 04 |  | GEN in auto GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 1 | 340090 | 04 |  | GEN in auto GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 2 | 340090 | 04 |  | GEN in auto GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 3 | 340090 | 04 |  | GEN in auto GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 4 | 340090 | 04 |  | GEN in auto GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 5 | 340090 | 04 |  | GEN in auto GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 6 | 340090 | 04 |  | GEN in auto GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 7 | 340090 | 04 |  | GEN in auto GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 8 | 340090 | 04 |  | GEN in auto GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 9 | 340090 | 04 |  | GEN in auto GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 10 | 340090 | 04 |  | GEN in auto GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 11 | 340090 | 04 |  | GEN in auto GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 12 | 340090 | 04 |  | GEN in auto GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 13 | 340090 | 04 |  | GEN in auto GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 14 | 340090 | 04 |  | GEN in auto GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40089 | 15 | 340090 | 04 |  | GEN in auto GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 0 | 340091 | 04 |  | GEN in auto GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 1 | 340091 | 04 |  | GEN in auto GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 2 | 340091 | 04 |  | GEN in auto GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 3 | 340091 | 04 |  | GEN in auto GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 4 | 340091 | 04 |  | GEN in auto GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 5 | 340091 | 04 |  | GEN in auto GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 6 | 340091 | 04 |  | GEN in auto GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 7 | 340091 | 04 |  | GEN in auto GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 8 | 340091 | 04 |  | GEN in auto GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 9 | 340091 | 04 |  | GEN in auto GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 10 | 340091 | 04 |  | GEN in auto GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 11 | 340091 | 04 |  | GEN in auto GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 12 | 340091 | 04 |  | GEN in auto GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 13 | 340091 | 04 |  | GEN in auto GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 14 | 340091 | 04 |  | GEN in auto GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40090 | 15 | 340091 | 04 |  | GEN in auto GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 0 | 340092 | 04 |  | GEN in auto GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 1 | 340092 | 04 |  | GEN in auto GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 2 | 340092 | 04 |  | GEN in auto GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 3 | 340092 | 04 |  | GEN in auto GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 4 | 340092 | 04 |  | GEN in auto GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 5 | 340092 | 04 |  | GEN in auto GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 6 | 340092 | 04 |  | GEN in auto GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 7 | 340092 | 04 |  | GEN in auto GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 8 | 340092 | 04 |  | GEN in auto GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 9 | 340092 | 04 |  | GEN in auto GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 10 | 340092 | 04 |  | GEN in auto GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 11 | 340092 | 04 |  | GEN in auto GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 12 | 340092 | 04 |  | GEN in auto GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 13 | 340092 | 04 |  | GEN in auto GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 14 | 340092 | 04 |  | GEN in auto GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40091 | 15 | 340092 | 04 |  | GEN in auto GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 0 | 340093 | 04 |  | GEN in auto GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 1 | 340093 | 04 |  | GEN in auto GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 2 | 340093 | 04 |  | GEN in auto GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 3 | 340093 | 04 |  | GEN in auto GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 4 | 340093 | 04 |  | GEN in auto GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 5 | 340093 | 04 |  | GEN in auto GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 6 | 340093 | 04 |  | GEN in auto GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 7 | 340093 | 04 |  | GEN in auto GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 8 | 340093 | 04 |  | GEN in auto GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 9 | 340093 | 04 |  | GEN in auto GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 10 | 340093 | 04 |  | GEN in auto GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 11 | 340093 | 04 |  | GEN in auto GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 12 | 340093 | 04 |  | GEN in auto GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 13 | 340093 | 04 |  | GEN in auto GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 14 | 340093 | 04 |  | GEN in auto GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40092 | 15 | 340093 | 04 |  | GEN in auto GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 0 | 340094 | 04 |  | GEN in auto GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 1 | 340094 | 04 |  | GEN in auto GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 2 | 340094 | 04 |  | GEN in auto GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 3 | 340094 | 04 |  | GEN in auto GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 4 | 340094 | 04 |  | GEN in auto GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 5 | 340094 | 04 |  | GEN in auto GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 6 | 340094 | 04 |  | GEN in auto GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 7 | 340094 | 04 |  | GEN in auto GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 8 | 340094 | 04 |  | GEN in auto GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 9 | 340094 | 04 |  | GEN in auto GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 10 | 340094 | 04 |  | GEN in auto GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 11 | 340094 | 04 |  | GEN in auto GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 12 | 340094 | 04 |  | GEN in auto GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 13 | 340094 | 04 |  | GEN in auto GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 14 | 340094 | 04 |  | GEN in auto GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40093 | 15 | 340094 | 04 |  | GEN in auto GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 0 | 340095 | 04 |  | GEN in auto GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 1 | 340095 | 04 |  | GEN in auto GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 2 | 340095 | 04 |  | GEN in auto GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 3 | 340095 | 04 |  | GEN in auto GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 4 | 340095 | 04 |  | GEN in auto GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 5 | 340095 | 04 |  | GEN in auto GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 6 | 340095 | 04 |  | GEN in auto GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 7 | 340095 | 04 |  | GEN in auto GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 8 | 340095 | 04 |  | GEN in auto GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 9 | 340095 | 04 |  | GEN in auto GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 10 | 340095 | 04 |  | GEN in auto GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 11 | 340095 | 04 |  | GEN in auto GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 12 | 340095 | 04 |  | GEN in auto GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 13 | 340095 | 04 |  | GEN in auto GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 14 | 340095 | 04 |  | GEN in auto GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40094 | 15 | 340095 | 04 |  | GEN in auto GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 0 | 340096 | 04 |  | GEN in auto GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 1 | 340096 | 04 |  | GEN in auto GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 2 | 340096 | 04 |  | GEN in auto GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 3 | 340096 | 04 |  | GEN in auto GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 4 | 340096 | 04 |  | GEN in auto GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 5 | 340096 | 04 |  | GEN in auto GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 6 | 340096 | 04 |  | GEN in auto GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 7 | 340096 | 04 |  | GEN in auto GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 8 | 340096 | 04 |  | GEN in auto GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 9 | 340096 | 04 |  | GEN in auto GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 10 | 340096 | 04 |  | GEN in auto GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 11 | 340096 | 04 |  | GEN in auto GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 12 | 340096 | 04 |  | GEN in auto GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40095 | 13 | 340096 | 04 |  | GEN in auto GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 0 | 340097 | 04 |  | Auto start/stop signal GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 1 | 340097 | 04 |  | Auto start/stop signal GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 2 | 340097 | 04 |  | Auto start/stop signal GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 3 | 340097 | 04 |  | Auto start/stop signal GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 4 | 340097 | 04 |  | Auto start/stop signal GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 5 | 340097 | 04 |  | Auto start/stop signal GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 6 | 340097 | 04 |  | Auto start/stop signal GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 7 | 340097 | 04 |  | Auto start/stop signal GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 8 | 340097 | 04 |  | Auto start/stop signal GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 9 | 340097 | 04 |  | Auto start/stop signal GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 10 | 340097 | 04 |  | Auto start/stop signal GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 11 | 340097 | 04 |  | Auto start/stop signal GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 12 | 340097 | 04 |  | Auto start/stop signal GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 13 | 340097 | 04 |  | Auto start/stop signal GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 14 | 340097 | 04 |  | Auto start/stop signal GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40096 | 15 | 340097 | 04 |  | Auto start/stop signal GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 0 | 340098 | 04 |  | Auto start/stop signal GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 1 | 340098 | 04 |  | Auto start/stop signal GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 2 | 340098 | 04 |  | Auto start/stop signal GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 3 | 340098 | 04 |  | Auto start/stop signal GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 4 | 340098 | 04 |  | Auto start/stop signal GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 5 | 340098 | 04 |  | Auto start/stop signal GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 6 | 340098 | 04 |  | Auto start/stop signal GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 7 | 340098 | 04 |  | Auto start/stop signal GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 8 | 340098 | 04 |  | Auto start/stop signal GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 9 | 340098 | 04 |  | Auto start/stop signal GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 10 | 340098 | 04 |  | Auto start/stop signal GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 11 | 340098 | 04 |  | Auto start/stop signal GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 12 | 340098 | 04 |  | Auto start/stop signal GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 13 | 340098 | 04 |  | Auto start/stop signal GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 14 | 340098 | 04 |  | Auto start/stop signal GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40097 | 15 | 340098 | 04 |  | Auto start/stop signal GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 0 | 340099 | 04 |  | Auto start/stop signal GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 1 | 340099 | 04 |  | Auto start/stop signal GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 2 | 340099 | 04 |  | Auto start/stop signal GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 3 | 340099 | 04 |  | Auto start/stop signal GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 4 | 340099 | 04 |  | Auto start/stop signal GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 5 | 340099 | 04 |  | Auto start/stop signal GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 6 | 340099 | 04 |  | Auto start/stop signal GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 7 | 340099 | 04 |  | Auto start/stop signal GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 8 | 340099 | 04 |  | Auto start/stop signal GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 9 | 340099 | 04 |  | Auto start/stop signal GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 10 | 340099 | 04 |  | Auto start/stop signal GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 11 | 340099 | 04 |  | Auto start/stop signal GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 12 | 340099 | 04 |  | Auto start/stop signal GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 13 | 340099 | 04 |  | Auto start/stop signal GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 14 | 340099 | 04 |  | Auto start/stop signal GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40098 | 15 | 340099 | 04 |  | Auto start/stop signal GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 0 | 340100 | 04 |  | Auto start/stop signal GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 1 | 340100 | 04 |  | Auto start/stop signal GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 2 | 340100 | 04 |  | Auto start/stop signal GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 3 | 340100 | 04 |  | Auto start/stop signal GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 4 | 340100 | 04 |  | Auto start/stop signal GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 5 | 340100 | 04 |  | Auto start/stop signal GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 6 | 340100 | 04 |  | Auto start/stop signal GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 7 | 340100 | 04 |  | Auto start/stop signal GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 8 | 340100 | 04 |  | Auto start/stop signal GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 9 | 340100 | 04 |  | Auto start/stop signal GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 10 | 340100 | 04 |  | Auto start/stop signal GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 11 | 340100 | 04 |  | Auto start/stop signal GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 12 | 340100 | 04 |  | Auto start/stop signal GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 13 | 340100 | 04 |  | Auto start/stop signal GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 14 | 340100 | 04 |  | Auto start/stop signal GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40099 | 15 | 340100 | 04 |  | Auto start/stop signal GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 0 | 340101 | 04 |  | Auto start/stop signal GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 1 | 340101 | 04 |  | Auto start/stop signal GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 2 | 340101 | 04 |  | Auto start/stop signal GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 3 | 340101 | 04 |  | Auto start/stop signal GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 4 | 340101 | 04 |  | Auto start/stop signal GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 5 | 340101 | 04 |  | Auto start/stop signal GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 6 | 340101 | 04 |  | Auto start/stop signal GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 7 | 340101 | 04 |  | Auto start/stop signal GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 8 | 340101 | 04 |  | Auto start/stop signal GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 9 | 340101 | 04 |  | Auto start/stop signal GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 10 | 340101 | 04 |  | Auto start/stop signal GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 11 | 340101 | 04 |  | Auto start/stop signal GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 12 | 340101 | 04 |  | Auto start/stop signal GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 13 | 340101 | 04 |  | Auto start/stop signal GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 14 | 340101 | 04 |  | Auto start/stop signal GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40100 | 15 | 340101 | 04 |  | Auto start/stop signal GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 0 | 340102 | 04 |  | Auto start/stop signal GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 1 | 340102 | 04 |  | Auto start/stop signal GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 2 | 340102 | 04 |  | Auto start/stop signal GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 3 | 340102 | 04 |  | Auto start/stop signal GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 4 | 340102 | 04 |  | Auto start/stop signal GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 5 | 340102 | 04 |  | Auto start/stop signal GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 6 | 340102 | 04 |  | Auto start/stop signal GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 7 | 340102 | 04 |  | Auto start/stop signal GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 8 | 340102 | 04 |  | Auto start/stop signal GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 9 | 340102 | 04 |  | Auto start/stop signal GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 10 | 340102 | 04 |  | Auto start/stop signal GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 11 | 340102 | 04 |  | Auto start/stop signal GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 12 | 340102 | 04 |  | Auto start/stop signal GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 13 | 340102 | 04 |  | Auto start/stop signal GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 14 | 340102 | 04 |  | Auto start/stop signal GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40101 | 15 | 340102 | 04 |  | Auto start/stop signal GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 0 | 340103 | 04 |  | Auto start/stop signal GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 1 | 340103 | 04 |  | Auto start/stop signal GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 2 | 340103 | 04 |  | Auto start/stop signal GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 3 | 340103 | 04 |  | Auto start/stop signal GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 4 | 340103 | 04 |  | Auto start/stop signal GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 5 | 340103 | 04 |  | Auto start/stop signal GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 6 | 340103 | 04 |  | Auto start/stop signal GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 7 | 340103 | 04 |  | Auto start/stop signal GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 8 | 340103 | 04 |  | Auto start/stop signal GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 9 | 340103 | 04 |  | Auto start/stop signal GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 10 | 340103 | 04 |  | Auto start/stop signal GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 11 | 340103 | 04 |  | Auto start/stop signal GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 12 | 340103 | 04 |  | Auto start/stop signal GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 13 | 340103 | 04 |  | Auto start/stop signal GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 14 | 340103 | 04 |  | Auto start/stop signal GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40102 | 15 | 340103 | 04 |  | Auto start/stop signal GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 0 | 340104 | 04 |  | Auto start/stop signal GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 1 | 340104 | 04 |  | Auto start/stop signal GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 2 | 340104 | 04 |  | Auto start/stop signal GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 3 | 340104 | 04 |  | Auto start/stop signal GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 4 | 340104 | 04 |  | Auto start/stop signal GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 5 | 340104 | 04 |  | Auto start/stop signal GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 6 | 340104 | 04 |  | Auto start/stop signal GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 7 | 340104 | 04 |  | Auto start/stop signal GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 8 | 340104 | 04 |  | Auto start/stop signal GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 9 | 340104 | 04 |  | Auto start/stop signal GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 10 | 340104 | 04 |  | Auto start/stop signal GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 11 | 340104 | 04 |  | Auto start/stop signal GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 12 | 340104 | 04 |  | Auto start/stop signal GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 13 | 340104 | 04 |  | Auto start/stop signal GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 14 | 340104 | 04 |  | Auto start/stop signal GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40103 | 15 | 340104 | 04 |  | Auto start/stop signal GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 0 | 340105 | 04 |  | Auto start/stop signal GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 1 | 340105 | 04 |  | Auto start/stop signal GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 2 | 340105 | 04 |  | Auto start/stop signal GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 3 | 340105 | 04 |  | Auto start/stop signal GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 4 | 340105 | 04 |  | Auto start/stop signal GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 5 | 340105 | 04 |  | Auto start/stop signal GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 6 | 340105 | 04 |  | Auto start/stop signal GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 7 | 340105 | 04 |  | Auto start/stop signal GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 8 | 340105 | 04 |  | Auto start/stop signal GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 9 | 340105 | 04 |  | Auto start/stop signal GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 10 | 340105 | 04 |  | Auto start/stop signal GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 11 | 340105 | 04 |  | Auto start/stop signal GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 12 | 340105 | 04 |  | Auto start/stop signal GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 13 | 340105 | 04 |  | Auto start/stop signal GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 14 | 340105 | 04 |  | Auto start/stop signal GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40104 | 15 | 340105 | 04 |  | Auto start/stop signal GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 0 | 340106 | 04 |  | Auto start/stop signal GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 1 | 340106 | 04 |  | Auto start/stop signal GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 2 | 340106 | 04 |  | Auto start/stop signal GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 3 | 340106 | 04 |  | Auto start/stop signal GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 4 | 340106 | 04 |  | Auto start/stop signal GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 5 | 340106 | 04 |  | Auto start/stop signal GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 6 | 340106 | 04 |  | Auto start/stop signal GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 7 | 340106 | 04 |  | Auto start/stop signal GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 8 | 340106 | 04 |  | Auto start/stop signal GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 9 | 340106 | 04 |  | Auto start/stop signal GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 10 | 340106 | 04 |  | Auto start/stop signal GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 11 | 340106 | 04 |  | Auto start/stop signal GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 12 | 340106 | 04 |  | Auto start/stop signal GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 13 | 340106 | 04 |  | Auto start/stop signal GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 14 | 340106 | 04 |  | Auto start/stop signal GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40105 | 15 | 340106 | 04 |  | Auto start/stop signal GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 0 | 340107 | 04 |  | Auto start/stop signal GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 1 | 340107 | 04 |  | Auto start/stop signal GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 2 | 340107 | 04 |  | Auto start/stop signal GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 3 | 340107 | 04 |  | Auto start/stop signal GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 4 | 340107 | 04 |  | Auto start/stop signal GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 5 | 340107 | 04 |  | Auto start/stop signal GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 6 | 340107 | 04 |  | Auto start/stop signal GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 7 | 340107 | 04 |  | Auto start/stop signal GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 8 | 340107 | 04 |  | Auto start/stop signal GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 9 | 340107 | 04 |  | Auto start/stop signal GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 10 | 340107 | 04 |  | Auto start/stop signal GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 11 | 340107 | 04 |  | Auto start/stop signal GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 12 | 340107 | 04 |  | Auto start/stop signal GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 13 | 340107 | 04 |  | Auto start/stop signal GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 14 | 340107 | 04 |  | Auto start/stop signal GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40106 | 15 | 340107 | 04 |  | Auto start/stop signal GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 0 | 340108 | 04 |  | Auto start/stop signal GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 1 | 340108 | 04 |  | Auto start/stop signal GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 2 | 340108 | 04 |  | Auto start/stop signal GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 3 | 340108 | 04 |  | Auto start/stop signal GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 4 | 340108 | 04 |  | Auto start/stop signal GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 5 | 340108 | 04 |  | Auto start/stop signal GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 6 | 340108 | 04 |  | Auto start/stop signal GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 7 | 340108 | 04 |  | Auto start/stop signal GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 8 | 340108 | 04 |  | Auto start/stop signal GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 9 | 340108 | 04 |  | Auto start/stop signal GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 10 | 340108 | 04 |  | Auto start/stop signal GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 11 | 340108 | 04 |  | Auto start/stop signal GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 12 | 340108 | 04 |  | Auto start/stop signal GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 13 | 340108 | 04 |  | Auto start/stop signal GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 14 | 340108 | 04 |  | Auto start/stop signal GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40107 | 15 | 340108 | 04 |  | Auto start/stop signal GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 0 | 340109 | 04 |  | Auto start/stop signal GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 1 | 340109 | 04 |  | Auto start/stop signal GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 2 | 340109 | 04 |  | Auto start/stop signal GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 3 | 340109 | 04 |  | Auto start/stop signal GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 4 | 340109 | 04 |  | Auto start/stop signal GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 5 | 340109 | 04 |  | Auto start/stop signal GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 6 | 340109 | 04 |  | Auto start/stop signal GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 7 | 340109 | 04 |  | Auto start/stop signal GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 8 | 340109 | 04 |  | Auto start/stop signal GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 9 | 340109 | 04 |  | Auto start/stop signal GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 10 | 340109 | 04 |  | Auto start/stop signal GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 11 | 340109 | 04 |  | Auto start/stop signal GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 12 | 340109 | 04 |  | Auto start/stop signal GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 13 | 340109 | 04 |  | Auto start/stop signal GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 14 | 340109 | 04 |  | Auto start/stop signal GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40108 | 15 | 340109 | 04 |  | Auto start/stop signal GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 0 | 340110 | 04 |  | Auto start/stop signal GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 1 | 340110 | 04 |  | Auto start/stop signal GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 2 | 340110 | 04 |  | Auto start/stop signal GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 3 | 340110 | 04 |  | Auto start/stop signal GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 4 | 340110 | 04 |  | Auto start/stop signal GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 5 | 340110 | 04 |  | Auto start/stop signal GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 6 | 340110 | 04 |  | Auto start/stop signal GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 7 | 340110 | 04 |  | Auto start/stop signal GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 8 | 340110 | 04 |  | Auto start/stop signal GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 9 | 340110 | 04 |  | Auto start/stop signal GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 10 | 340110 | 04 |  | Auto start/stop signal GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 11 | 340110 | 04 |  | Auto start/stop signal GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 12 | 340110 | 04 |  | Auto start/stop signal GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 13 | 340110 | 04 |  | Auto start/stop signal GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 14 | 340110 | 04 |  | Auto start/stop signal GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40109 | 15 | 340110 | 04 |  | Auto start/stop signal GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 0 | 340111 | 04 |  | Auto start/stop signal GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 1 | 340111 | 04 |  | Auto start/stop signal GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 2 | 340111 | 04 |  | Auto start/stop signal GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 3 | 340111 | 04 |  | Auto start/stop signal GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 4 | 340111 | 04 |  | Auto start/stop signal GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 5 | 340111 | 04 |  | Auto start/stop signal GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 6 | 340111 | 04 |  | Auto start/stop signal GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 7 | 340111 | 04 |  | Auto start/stop signal GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 8 | 340111 | 04 |  | Auto start/stop signal GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 9 | 340111 | 04 |  | Auto start/stop signal GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 10 | 340111 | 04 |  | Auto start/stop signal GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 11 | 340111 | 04 |  | Auto start/stop signal GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 12 | 340111 | 04 |  | Auto start/stop signal GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 13 | 340111 | 04 |  | Auto start/stop signal GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 14 | 340111 | 04 |  | Auto start/stop signal GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40110 | 15 | 340111 | 04 |  | Auto start/stop signal GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 0 | 340112 | 04 |  | Auto start/stop signal GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 1 | 340112 | 04 |  | Auto start/stop signal GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 2 | 340112 | 04 |  | Auto start/stop signal GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 3 | 340112 | 04 |  | Auto start/stop signal GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 4 | 340112 | 04 |  | Auto start/stop signal GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 5 | 340112 | 04 |  | Auto start/stop signal GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 6 | 340112 | 04 |  | Auto start/stop signal GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 7 | 340112 | 04 |  | Auto start/stop signal GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 8 | 340112 | 04 |  | Auto start/stop signal GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 9 | 340112 | 04 |  | Auto start/stop signal GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 10 | 340112 | 04 |  | Auto start/stop signal GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 11 | 340112 | 04 |  | Auto start/stop signal GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 12 | 340112 | 04 |  | Auto start/stop signal GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40111 | 13 | 340112 | 04 |  | Auto start/stop signal GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 40620 |  | 340621 | 04 |  | BIT0-BIT7 PMS lite version GEN1, BIT8-BIT15 PMS lite version GEN2 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40621 |  | 340622 | 04 |  | BIT0-BIT7 PMS lite version GEN3, BIT8-BIT15 PMS lite version GEN4 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40622 |  | 340623 | 04 |  | BIT0-BIT7 PMS lite version GEN5, BIT8-BIT15 PMS lite version GEN6 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40623 |  | 340624 | 04 |  | BIT0-BIT7 PMS lite version GEN7, BIT8-BIT15 PMS lite version GEN8 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40624 |  | 340625 | 04 |  | BIT0-BIT7 PMS lite version GEN9, BIT8-BIT15 PMS lite version GEN10 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40625 |  | 340626 | 04 |  | BIT0-BIT7 PMS lite version GEN11, BIT8-BIT15 PMS lite version GEN12 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40626 |  | 340627 | 04 |  | BIT0-BIT7 PMS lite version GEN13, BIT8-BIT15 PMS lite version GEN14 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40627 |  | 340628 | 04 |  | BIT0-BIT7 PMS lite version GEN15, BIT8-BIT15 PMS lite version GEN16 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40628 |  | 340629 | 04 |  | BIT0-BIT7 PMS lite version GEN17, BIT8-BIT15 PMS lite version GEN18 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40629 |  | 340630 | 04 |  | BIT0-BIT7 PMS lite version GEN19, BIT8-BIT15 PMS lite version GEN20 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40630 |  | 340631 | 04 |  | BIT0-BIT7 PMS lite version GEN21, BIT8-BIT15 PMS lite version GEN22 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40631 |  | 340632 | 04 |  | BIT0-BIT7 PMS lite version GEN23, BIT8-BIT15 PMS lite version GEN24 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40632 |  | 340633 | 04 |  | BIT0-BIT7 PMS lite version GEN25, BIT8-BIT15 PMS lite version GEN26 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40633 |  | 340634 | 04 |  | BIT0-BIT7 PMS lite version GEN27, BIT8-BIT15 PMS lite version GEN28 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40634 |  | 340635 | 04 |  | BIT0-BIT7 PMS lite version GEN29, BIT8-BIT15 PMS lite version GEN30 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40635 |  | 340636 | 04 |  | BIT0-BIT7 PMS lite version GEN31, BIT8-BIT15 PMS lite version GEN32 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40636 |  | 340637 | 04 |  | BIT0-BIT7 PMS lite version GEN33, BIT8-BIT15 PMS lite version GEN34 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40637 |  | 340638 | 04 |  | BIT0-BIT7 PMS lite version GEN35, BIT8-BIT15 PMS lite version GEN36 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40638 |  | 340639 | 04 |  | BIT0-BIT7 PMS lite version GEN37, BIT8-BIT15 PMS lite version GEN38 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40639 |  | 340640 | 04 |  | BIT0-BIT7 PMS lite version GEN39, BIT8-BIT15 PMS lite version GEN40 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40640 |  | 340641 | 04 |  | BIT0-BIT7 PMS lite version GEN41, BIT8-BIT15 PMS lite version GEN42 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40641 |  | 340642 | 04 |  | BIT0-BIT7 PMS lite version GEN43, BIT8-BIT15 PMS lite version GEN44 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40642 |  | 340643 | 04 |  | BIT0-BIT7 PMS lite version GEN45, BIT8-BIT15 PMS lite version GEN46 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40643 |  | 340644 | 04 |  | BIT0-BIT7 PMS lite version GEN47, BIT8-BIT15 PMS lite version GEN48 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40644 |  | 340645 | 04 |  | BIT0-BIT7 PMS lite version GEN49, BIT8-BIT15 PMS lite version GEN50 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40645 |  | 340646 | 04 |  | BIT0-BIT7 PMS lite version GEN51, BIT8-BIT15 PMS lite version GEN52 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40646 |  | 340647 | 04 |  | BIT0-BIT7 PMS lite version GEN53, BIT8-BIT15 PMS lite version GEN54 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40647 |  | 340648 | 04 |  | BIT0-BIT7 PMS lite version GEN55, BIT8-BIT15 PMS lite version GEN56 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40648 |  | 340649 | 04 |  | BIT0-BIT7 PMS lite version GEN57, BIT8-BIT15 PMS lite version GEN58 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40649 |  | 340650 | 04 |  | BIT0-BIT7 PMS lite version GEN59, BIT8-BIT15 PMS lite version GEN60 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40650 |  | 340651 | 04 |  | BIT0-BIT7 PMS lite version GEN61, BIT8-BIT15 PMS lite version GEN62 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40651 |  | 340652 | 04 |  | BIT0-BIT7 PMS lite version GEN63, BIT8-BIT15 PMS lite version GEN64 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40652 |  | 340653 | 04 |  | BIT0-BIT7 PMS lite version GEN65, BIT8-BIT15 PMS lite version GEN66 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40653 |  | 340654 | 04 |  | BIT0-BIT7 PMS lite version GEN67, BIT8-BIT15 PMS lite version GEN68 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40654 |  | 340655 | 04 |  | BIT0-BIT7 PMS lite version GEN69, BIT8-BIT15 PMS lite version GEN70 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40655 |  | 340656 | 04 |  | BIT0-BIT7 PMS lite version GEN71, BIT8-BIT15 PMS lite version GEN72 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40656 |  | 340657 | 04 |  | BIT0-BIT7 PMS lite version GEN73, BIT8-BIT15 PMS lite version GEN74 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40657 |  | 340658 | 04 |  | BIT0-BIT7 PMS lite version GEN75, BIT8-BIT15 PMS lite version GEN76 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40658 |  | 340659 | 04 |  | BIT0-BIT7 PMS lite version GEN77, BIT8-BIT15 PMS lite version GEN78 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40659 |  | 340660 | 04 |  | BIT0-BIT7 PMS lite version GEN79, BIT8-BIT15 PMS lite version GEN80 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40660 |  | 340661 | 04 |  | BIT0-BIT7 PMS lite version GEN81, BIT8-BIT15 PMS lite version GEN82 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40661 |  | 340662 | 04 |  | BIT0-BIT7 PMS lite version GEN83, BIT8-BIT15 PMS lite version GEN84 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40662 |  | 340663 | 04 |  | BIT0-BIT7 PMS lite version GEN85, BIT8-BIT15 PMS lite version GEN86 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40663 |  | 340664 | 04 |  | BIT0-BIT7 PMS lite version GEN87, BIT8-BIT15 PMS lite version GEN88 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40664 |  | 340665 | 04 |  | BIT0-BIT7 PMS lite version GEN89, BIT8-BIT15 PMS lite version GEN90 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40665 |  | 340666 | 04 |  | BIT0-BIT7 PMS lite version GEN91, BIT8-BIT15 PMS lite version GEN92 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40666 |  | 340667 | 04 |  | BIT0-BIT7 PMS lite version GEN93, BIT8-BIT15 PMS lite version GEN94 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40667 |  | 340668 | 04 |  | BIT0-BIT7 PMS lite version GEN95, BIT8-BIT15 PMS lite version GEN96 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40668 |  | 340669 | 04 |  | BIT0-BIT7 PMS lite version GEN97, BIT8-BIT15 PMS lite version GEN98 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40669 |  | 340670 | 04 |  | BIT0-BIT7 PMS lite version GEN99, BIT8-BIT15 PMS lite version GEN100 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40670 |  | 340671 | 04 |  | BIT0-BIT7 PMS lite version GEN101, BIT8-BIT15 PMS lite version GEN102 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40671 |  | 340672 | 04 |  | BIT0-BIT7 PMS lite version GEN103, BIT8-BIT15 PMS lite version GEN104 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40672 |  | 340673 | 04 |  | BIT0-BIT7 PMS lite version GEN105, BIT8-BIT15 PMS lite version GEN106 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40673 |  | 340674 | 04 |  | BIT0-BIT7 PMS lite version GEN107, BIT8-BIT15 PMS lite version GEN108 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40674 |  | 340675 | 04 |  | BIT0-BIT7 PMS lite version GEN109, BIT8-BIT15 PMS lite version GEN110 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40675 |  | 340676 | 04 |  | BIT0-BIT7 PMS lite version GEN111, BIT8-BIT15 PMS lite version GEN112 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40676 |  | 340677 | 04 |  | BIT0-BIT7 PMS lite version GEN113, BIT8-BIT15 PMS lite version GEN114 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40677 |  | 340678 | 04 |  | BIT0-BIT7 PMS lite version GEN115, BIT8-BIT15 PMS lite version GEN116 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40678 |  | 340679 | 04 |  | BIT0-BIT7 PMS lite version GEN117, BIT8-BIT15 PMS lite version GEN118 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40679 |  | 340680 | 04 |  | BIT0-BIT7 PMS lite version GEN119, BIT8-BIT15 PMS lite version GEN120 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40680 |  | 340681 | 04 |  | BIT0-BIT7 PMS lite version GEN121, BIT8-BIT15 PMS lite version GEN122 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40681 |  | 340682 | 04 |  | BIT0-BIT7 PMS lite version GEN123, BIT8-BIT15 PMS lite version GEN124 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40682 |  | 340683 | 04 |  | BIT0-BIT7 PMS lite version GEN125, BIT8-BIT15 PMS lite version GEN126 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40683 |  | 340684 | 04 |  | BIT0-BIT7 PMS lite version GEN127, BIT8-BIT15 PMS lite version GEN128 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40684 |  | 340685 | 04 |  | BIT0-BIT7 PMS lite version GEN129, BIT8-BIT15 PMS lite version GEN130 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40685 |  | 340686 | 04 |  | BIT0-BIT7 PMS lite version GEN131, BIT8-BIT15 PMS lite version GEN132 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40686 |  | 340687 | 04 |  | BIT0-BIT7 PMS lite version GEN133, BIT8-BIT15 PMS lite version GEN134 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40687 |  | 340688 | 04 |  | BIT0-BIT7 PMS lite version GEN135, BIT8-BIT15 PMS lite version GEN136 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40688 |  | 340689 | 04 |  | BIT0-BIT7 PMS lite version GEN137, BIT8-BIT15 PMS lite version GEN138 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40689 |  | 340690 | 04 |  | BIT0-BIT7 PMS lite version GEN139, BIT8-BIT15 PMS lite version GEN140 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40690 |  | 340691 | 04 |  | BIT0-BIT7 PMS lite version GEN141, BIT8-BIT15 PMS lite version GEN142 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40691 |  | 340692 | 04 |  | BIT0-BIT7 PMS lite version GEN143, BIT8-BIT15 PMS lite version GEN144 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40692 |  | 340693 | 04 |  | BIT0-BIT7 PMS lite version GEN145, BIT8-BIT15 PMS lite version GEN146 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40693 |  | 340694 | 04 |  | BIT0-BIT7 PMS lite version GEN147, BIT8-BIT15 PMS lite version GEN148 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40694 |  | 340695 | 04 |  | BIT0-BIT7 PMS lite version GEN149, BIT8-BIT15 PMS lite version GEN150 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40695 |  | 340696 | 04 |  | BIT0-BIT7 PMS lite version GEN151, BIT8-BIT15 PMS lite version GEN152 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40696 |  | 340697 | 04 |  | BIT0-BIT7 PMS lite version GEN153, BIT8-BIT15 PMS lite version GEN154 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40697 |  | 340698 | 04 |  | BIT0-BIT7 PMS lite version GEN155, BIT8-BIT15 PMS lite version GEN156 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40698 |  | 340699 | 04 |  | BIT0-BIT7 PMS lite version GEN157, BIT8-BIT15 PMS lite version GEN158 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40699 |  | 340700 | 04 |  | BIT0-BIT7 PMS lite version GEN159, BIT8-BIT15 PMS lite version GEN160 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40700 |  | 340701 | 04 |  | BIT0-BIT7 PMS lite version GEN161, BIT8-BIT15 PMS lite version GEN162 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40701 |  | 340702 | 04 |  | BIT0-BIT7 PMS lite version GEN163, BIT8-BIT15 PMS lite version GEN164 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40702 |  | 340703 | 04 |  | BIT0-BIT7 PMS lite version GEN165, BIT8-BIT15 PMS lite version GEN166 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40703 |  | 340704 | 04 |  | BIT0-BIT7 PMS lite version GEN167, BIT8-BIT15 PMS lite version GEN168 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40704 |  | 340705 | 04 |  | BIT0-BIT7 PMS lite version GEN169, BIT8-BIT15 PMS lite version GEN170 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40705 |  | 340706 | 04 |  | BIT0-BIT7 PMS lite version GEN171, BIT8-BIT15 PMS lite version GEN172 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40706 |  | 340707 | 04 |  | BIT0-BIT7 PMS lite version GEN173, BIT8-BIT15 PMS lite version GEN174 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40707 |  | 340708 | 04 |  | BIT0-BIT7 PMS lite version GEN175, BIT8-BIT15 PMS lite version GEN176 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40708 |  | 340709 | 04 |  | BIT0-BIT7 PMS lite version GEN177, BIT8-BIT15 PMS lite version GEN178 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40709 |  | 340710 | 04 |  | BIT0-BIT7 PMS lite version GEN179, BIT8-BIT15 PMS lite version GEN180 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40710 |  | 340711 | 04 |  | BIT0-BIT7 PMS lite version GEN181, BIT8-BIT15 PMS lite version GEN182 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40711 |  | 340712 | 04 |  | BIT0-BIT7 PMS lite version GEN183, BIT8-BIT15 PMS lite version GEN184 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40712 |  | 340713 | 04 |  | BIT0-BIT7 PMS lite version GEN185, BIT8-BIT15 PMS lite version GEN186 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40713 |  | 340714 | 04 |  | BIT0-BIT7 PMS lite version GEN187, BIT8-BIT15 PMS lite version GEN188 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40714 |  | 340715 | 04 |  | BIT0-BIT7 PMS lite version GEN189, BIT8-BIT15 PMS lite version GEN190 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40715 |  | 340716 | 04 |  | BIT0-BIT7 PMS lite version GEN191, BIT8-BIT15 PMS lite version GEN192 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40716 |  | 340717 | 04 |  | BIT0-BIT7 PMS lite version GEN193, BIT8-BIT15 PMS lite version GEN194 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40717 |  | 340718 | 04 |  | BIT0-BIT7 PMS lite version GEN195, BIT8-BIT15 PMS lite version GEN196 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40718 |  | 340719 | 04 |  | BIT0-BIT7 PMS lite version GEN197, BIT8-BIT15 PMS lite version GEN198 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40719 |  | 340720 | 04 |  | BIT0-BIT7 PMS lite version GEN199, BIT8-BIT15 PMS lite version GEN200 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40720 |  | 340721 | 04 |  | BIT0-BIT7 PMS lite version GEN201, BIT8-BIT15 PMS lite version GEN202 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40721 |  | 340722 | 04 |  | BIT0-BIT7 PMS lite version GEN203, BIT8-BIT15 PMS lite version GEN204 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40722 |  | 340723 | 04 |  | BIT0-BIT7 PMS lite version GEN205, BIT8-BIT15 PMS lite version GEN206 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40723 |  | 340724 | 04 |  | BIT0-BIT7 PMS lite version GEN207, BIT8-BIT15 PMS lite version GEN208 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40724 |  | 340725 | 04 |  | BIT0-BIT7 PMS lite version GEN209, BIT8-BIT15 PMS lite version GEN210 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40725 |  | 340726 | 04 |  | BIT0-BIT7 PMS lite version GEN211, BIT8-BIT15 PMS lite version GEN212 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40726 |  | 340727 | 04 |  | BIT0-BIT7 PMS lite version GEN213, BIT8-BIT15 PMS lite version GEN214 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40727 |  | 340728 | 04 |  | BIT0-BIT7 PMS lite version GEN215, BIT8-BIT15 PMS lite version GEN216 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40728 |  | 340729 | 04 |  | BIT0-BIT7 PMS lite version GEN217, BIT8-BIT15 PMS lite version GEN218 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40729 |  | 340730 | 04 |  | BIT0-BIT7 PMS lite version GEN219, BIT8-BIT15 PMS lite version GEN220 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40730 |  | 340731 | 04 |  | BIT0-BIT7 PMS lite version GEN221, BIT8-BIT15 PMS lite version GEN222 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40731 |  | 340732 | 04 |  | BIT0-BIT7 PMS lite version GEN223, BIT8-BIT15 PMS lite version GEN224 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40732 |  | 340733 | 04 |  | BIT0-BIT7 PMS lite version GEN225, BIT8-BIT15 PMS lite version GEN226 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40733 |  | 340734 | 04 |  | BIT0-BIT7 PMS lite version GEN227, BIT8-BIT15 PMS lite version GEN228 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40734 |  | 340735 | 04 |  | BIT0-BIT7 PMS lite version GEN229, BIT8-BIT15 PMS lite version GEN230 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40735 |  | 340736 | 04 |  | BIT0-BIT7 PMS lite version GEN231, BIT8-BIT15 PMS lite version GEN232 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40736 |  | 340737 | 04 |  | BIT0-BIT7 PMS lite version GEN233, BIT8-BIT15 PMS lite version GEN234 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40737 |  | 340738 | 04 |  | BIT0-BIT7 PMS lite version GEN235, BIT8-BIT15 PMS lite version GEN236 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40738 |  | 340739 | 04 |  | BIT0-BIT7 PMS lite version GEN237, BIT8-BIT15 PMS lite version GEN238 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40739 |  | 340740 | 04 |  | BIT0-BIT7 PMS lite version GEN239, BIT8-BIT15 PMS lite version GEN240 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40740 |  | 340741 | 04 |  | BIT0-BIT7 PMS lite version GEN241, BIT8-BIT15 PMS lite version GEN242 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40741 |  | 340742 | 04 |  | BIT0-BIT7 PMS lite version GEN243, BIT8-BIT15 PMS lite version GEN244 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40742 |  | 340743 | 04 |  | BIT0-BIT7 PMS lite version GEN245, BIT8-BIT15 PMS lite version GEN246 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40743 |  | 340744 | 04 |  | BIT0-BIT7 PMS lite version GEN247, BIT8-BIT15 PMS lite version GEN248 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40744 |  | 340745 | 04 |  | BIT0-BIT7 PMS lite version GEN249, BIT8-BIT15 PMS lite version GEN250 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40745 |  | 340746 | 04 |  | BIT0-BIT7 PMS lite version GEN251, BIT8-BIT15 PMS lite version GEN252 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40746 |  | 340747 | 04 |  | BIT0-BIT7 PMS lite version GEN253, BIT8-BIT15 PMS lite version GEN254 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 40747 |  | 340748 | 04 |  | Nominal P GEN1 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40748 |  | 340749 | 04 |  | Nominal P GEN2 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40749 |  | 340750 | 04 |  | Nominal P GEN3 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40750 |  | 340751 | 04 |  | Nominal P GEN4 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40751 |  | 340752 | 04 |  | Nominal P GEN5 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40752 |  | 340753 | 04 |  | Nominal P GEN6 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40753 |  | 340754 | 04 |  | Nominal P GEN7 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40754 |  | 340755 | 04 |  | Nominal P GEN8 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40755 |  | 340756 | 04 |  | Nominal P GEN9 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40756 |  | 340757 | 04 |  | Nominal P GEN10 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40757 |  | 340758 | 04 |  | Nominal P GEN11 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40758 |  | 340759 | 04 |  | Nominal P GEN12 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40759 |  | 340760 | 04 |  | Nominal P GEN13 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40760 |  | 340761 | 04 |  | Nominal P GEN14 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40761 |  | 340762 | 04 |  | Nominal P GEN15 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40762 |  | 340763 | 04 |  | Nominal P GEN16 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40763 |  | 340764 | 04 |  | Nominal P GEN17 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40764 |  | 340765 | 04 |  | Nominal P GEN18 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40765 |  | 340766 | 04 |  | Nominal P GEN19 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40766 |  | 340767 | 04 |  | Nominal P GEN20 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40767 |  | 340768 | 04 |  | Nominal P GEN21 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40768 |  | 340769 | 04 |  | Nominal P GEN22 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40769 |  | 340770 | 04 |  | Nominal P GEN23 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40770 |  | 340771 | 04 |  | Nominal P GEN24 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40771 |  | 340772 | 04 |  | Nominal P GEN25 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40772 |  | 340773 | 04 |  | Nominal P GEN26 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40773 |  | 340774 | 04 |  | Nominal P GEN27 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40774 |  | 340775 | 04 |  | Nominal P GEN28 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40775 |  | 340776 | 04 |  | Nominal P GEN29 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40776 |  | 340777 | 04 |  | Nominal P GEN30 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40777 |  | 340778 | 04 |  | Nominal P GEN31 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40778 |  | 340779 | 04 |  | Nominal P GEN32 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40779 |  | 340780 | 04 |  | Nominal P GEN33 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40780 |  | 340781 | 04 |  | Nominal P GEN34 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40781 |  | 340782 | 04 |  | Nominal P GEN35 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40782 |  | 340783 | 04 |  | Nominal P GEN36 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40783 |  | 340784 | 04 |  | Nominal P GEN37 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40784 |  | 340785 | 04 |  | Nominal P GEN38 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40785 |  | 340786 | 04 |  | Nominal P GEN39 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40786 |  | 340787 | 04 |  | Nominal P GEN40 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40787 |  | 340788 | 04 |  | Nominal P GEN41 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40788 |  | 340789 | 04 |  | Nominal P GEN42 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40789 |  | 340790 | 04 |  | Nominal P GEN43 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40790 |  | 340791 | 04 |  | Nominal P GEN44 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40791 |  | 340792 | 04 |  | Nominal P GEN45 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40792 |  | 340793 | 04 |  | Nominal P GEN46 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40793 |  | 340794 | 04 |  | Nominal P GEN47 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40794 |  | 340795 | 04 |  | Nominal P GEN48 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40795 |  | 340796 | 04 |  | Nominal P GEN49 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40796 |  | 340797 | 04 |  | Nominal P GEN50 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40797 |  | 340798 | 04 |  | Nominal P GEN51 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40798 |  | 340799 | 04 |  | Nominal P GEN52 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40799 |  | 340800 | 04 |  | Nominal P GEN53 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40800 |  | 340801 | 04 |  | Nominal P GEN54 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40801 |  | 340802 | 04 |  | Nominal P GEN55 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40802 |  | 340803 | 04 |  | Nominal P GEN56 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40803 |  | 340804 | 04 |  | Nominal P GEN57 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40804 |  | 340805 | 04 |  | Nominal P GEN58 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40805 |  | 340806 | 04 |  | Nominal P GEN59 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40806 |  | 340807 | 04 |  | Nominal P GEN60 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40807 |  | 340808 | 04 |  | Nominal P GEN61 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40808 |  | 340809 | 04 |  | Nominal P GEN62 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40809 |  | 340810 | 04 |  | Nominal P GEN63 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40810 |  | 340811 | 04 |  | Nominal P GEN64 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40811 |  | 340812 | 04 |  | Nominal P GEN65 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40812 |  | 340813 | 04 |  | Nominal P GEN66 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40813 |  | 340814 | 04 |  | Nominal P GEN67 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40814 |  | 340815 | 04 |  | Nominal P GEN68 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40815 |  | 340816 | 04 |  | Nominal P GEN69 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40816 |  | 340817 | 04 |  | Nominal P GEN70 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40817 |  | 340818 | 04 |  | Nominal P GEN71 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40818 |  | 340819 | 04 |  | Nominal P GEN72 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40819 |  | 340820 | 04 |  | Nominal P GEN73 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40820 |  | 340821 | 04 |  | Nominal P GEN74 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40821 |  | 340822 | 04 |  | Nominal P GEN75 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40822 |  | 340823 | 04 |  | Nominal P GEN76 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40823 |  | 340824 | 04 |  | Nominal P GEN77 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40824 |  | 340825 | 04 |  | Nominal P GEN78 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40825 |  | 340826 | 04 |  | Nominal P GEN79 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40826 |  | 340827 | 04 |  | Nominal P GEN80 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40827 |  | 340828 | 04 |  | Nominal P GEN81 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40828 |  | 340829 | 04 |  | Nominal P GEN82 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40829 |  | 340830 | 04 |  | Nominal P GEN83 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40830 |  | 340831 | 04 |  | Nominal P GEN84 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40831 |  | 340832 | 04 |  | Nominal P GEN85 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40832 |  | 340833 | 04 |  | Nominal P GEN86 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40833 |  | 340834 | 04 |  | Nominal P GEN87 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40834 |  | 340835 | 04 |  | Nominal P GEN88 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40835 |  | 340836 | 04 |  | Nominal P GEN89 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40836 |  | 340837 | 04 |  | Nominal P GEN90 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40837 |  | 340838 | 04 |  | Nominal P GEN91 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40838 |  | 340839 | 04 |  | Nominal P GEN92 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40839 |  | 340840 | 04 |  | Nominal P GEN93 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40840 |  | 340841 | 04 |  | Nominal P GEN94 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40841 |  | 340842 | 04 |  | Nominal P GEN95 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40842 |  | 340843 | 04 |  | Nominal P GEN96 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40843 |  | 340844 | 04 |  | Nominal P GEN97 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40844 |  | 340845 | 04 |  | Nominal P GEN98 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40845 |  | 340846 | 04 |  | Nominal P GEN99 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40846 |  | 340847 | 04 |  | Nominal P GEN100 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40847 |  | 340848 | 04 |  | Nominal P GEN101 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40848 |  | 340849 | 04 |  | Nominal P GEN102 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40849 |  | 340850 | 04 |  | Nominal P GEN103 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40850 |  | 340851 | 04 |  | Nominal P GEN104 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40851 |  | 340852 | 04 |  | Nominal P GEN105 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40852 |  | 340853 | 04 |  | Nominal P GEN106 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40853 |  | 340854 | 04 |  | Nominal P GEN107 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40854 |  | 340855 | 04 |  | Nominal P GEN108 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40855 |  | 340856 | 04 |  | Nominal P GEN109 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40856 |  | 340857 | 04 |  | Nominal P GEN110 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40857 |  | 340858 | 04 |  | Nominal P GEN111 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40858 |  | 340859 | 04 |  | Nominal P GEN112 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40859 |  | 340860 | 04 |  | Nominal P GEN113 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40860 |  | 340861 | 04 |  | Nominal P GEN114 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40861 |  | 340862 | 04 |  | Nominal P GEN115 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40862 |  | 340863 | 04 |  | Nominal P GEN116 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40863 |  | 340864 | 04 |  | Nominal P GEN117 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40864 |  | 340865 | 04 |  | Nominal P GEN118 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40865 |  | 340866 | 04 |  | Nominal P GEN119 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40866 |  | 340867 | 04 |  | Nominal P GEN120 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40867 |  | 340868 | 04 |  | Nominal P GEN121 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40868 |  | 340869 | 04 |  | Nominal P GEN122 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40869 |  | 340870 | 04 |  | Nominal P GEN123 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40870 |  | 340871 | 04 |  | Nominal P GEN124 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40871 |  | 340872 | 04 |  | Nominal P GEN125 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40872 |  | 340873 | 04 |  | Nominal P GEN126 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40873 |  | 340874 | 04 |  | Nominal P GEN127 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40874 |  | 340875 | 04 |  | Nominal P GEN128 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40875 |  | 340876 | 04 |  | Nominal P GEN129 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40876 |  | 340877 | 04 |  | Nominal P GEN130 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40877 |  | 340878 | 04 |  | Nominal P GEN131 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40878 |  | 340879 | 04 |  | Nominal P GEN132 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40879 |  | 340880 | 04 |  | Nominal P GEN133 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40880 |  | 340881 | 04 |  | Nominal P GEN134 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40881 |  | 340882 | 04 |  | Nominal P GEN135 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40882 |  | 340883 | 04 |  | Nominal P GEN136 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40883 |  | 340884 | 04 |  | Nominal P GEN137 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40884 |  | 340885 | 04 |  | Nominal P GEN138 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40885 |  | 340886 | 04 |  | Nominal P GEN139 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40886 |  | 340887 | 04 |  | Nominal P GEN140 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40887 |  | 340888 | 04 |  | Nominal P GEN141 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40888 |  | 340889 | 04 |  | Nominal P GEN142 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40889 |  | 340890 | 04 |  | Nominal P GEN143 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40890 |  | 340891 | 04 |  | Nominal P GEN144 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40891 |  | 340892 | 04 |  | Nominal P GEN145 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40892 |  | 340893 | 04 |  | Nominal P GEN146 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40893 |  | 340894 | 04 |  | Nominal P GEN147 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40894 |  | 340895 | 04 |  | Nominal P GEN148 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40895 |  | 340896 | 04 |  | Nominal P GEN149 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40896 |  | 340897 | 04 |  | Nominal P GEN150 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40897 |  | 340898 | 04 |  | Nominal P GEN151 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40898 |  | 340899 | 04 |  | Nominal P GEN152 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40899 |  | 340900 | 04 |  | Nominal P GEN153 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40900 |  | 340901 | 04 |  | Nominal P GEN154 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40901 |  | 340902 | 04 |  | Nominal P GEN155 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40902 |  | 340903 | 04 |  | Nominal P GEN156 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40903 |  | 340904 | 04 |  | Nominal P GEN157 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40904 |  | 340905 | 04 |  | Nominal P GEN158 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40905 |  | 340906 | 04 |  | Nominal P GEN159 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40906 |  | 340907 | 04 |  | Nominal P GEN160 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40907 |  | 340908 | 04 |  | Nominal P GEN161 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40908 |  | 340909 | 04 |  | Nominal P GEN162 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40909 |  | 340910 | 04 |  | Nominal P GEN163 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40910 |  | 340911 | 04 |  | Nominal P GEN164 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40911 |  | 340912 | 04 |  | Nominal P GEN165 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40912 |  | 340913 | 04 |  | Nominal P GEN166 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40913 |  | 340914 | 04 |  | Nominal P GEN167 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40914 |  | 340915 | 04 |  | Nominal P GEN168 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40915 |  | 340916 | 04 |  | Nominal P GEN169 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40916 |  | 340917 | 04 |  | Nominal P GEN170 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40917 |  | 340918 | 04 |  | Nominal P GEN171 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40918 |  | 340919 | 04 |  | Nominal P GEN172 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40919 |  | 340920 | 04 |  | Nominal P GEN173 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40920 |  | 340921 | 04 |  | Nominal P GEN174 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40921 |  | 340922 | 04 |  | Nominal P GEN175 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40922 |  | 340923 | 04 |  | Nominal P GEN176 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40923 |  | 340924 | 04 |  | Nominal P GEN177 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40924 |  | 340925 | 04 |  | Nominal P GEN178 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40925 |  | 340926 | 04 |  | Nominal P GEN179 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40926 |  | 340927 | 04 |  | Nominal P GEN180 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40927 |  | 340928 | 04 |  | Nominal P GEN181 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40928 |  | 340929 | 04 |  | Nominal P GEN182 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40929 |  | 340930 | 04 |  | Nominal P GEN183 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40930 |  | 340931 | 04 |  | Nominal P GEN184 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40931 |  | 340932 | 04 |  | Nominal P GEN185 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40932 |  | 340933 | 04 |  | Nominal P GEN186 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40933 |  | 340934 | 04 |  | Nominal P GEN187 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40934 |  | 340935 | 04 |  | Nominal P GEN188 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40935 |  | 340936 | 04 |  | Nominal P GEN189 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40936 |  | 340937 | 04 |  | Nominal P GEN190 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40937 |  | 340938 | 04 |  | Nominal P GEN191 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40938 |  | 340939 | 04 |  | Nominal P GEN192 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40939 |  | 340940 | 04 |  | Nominal P GEN193 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40940 |  | 340941 | 04 |  | Nominal P GEN194 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40941 |  | 340942 | 04 |  | Nominal P GEN195 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40942 |  | 340943 | 04 |  | Nominal P GEN196 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40943 |  | 340944 | 04 |  | Nominal P GEN197 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40944 |  | 340945 | 04 |  | Nominal P GEN198 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40945 |  | 340946 | 04 |  | Nominal P GEN199 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40946 |  | 340947 | 04 |  | Nominal P GEN200 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40947 |  | 340948 | 04 |  | Nominal P GEN201 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40948 |  | 340949 | 04 |  | Nominal P GEN202 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40949 |  | 340950 | 04 |  | Nominal P GEN203 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40950 |  | 340951 | 04 |  | Nominal P GEN204 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40951 |  | 340952 | 04 |  | Nominal P GEN205 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40952 |  | 340953 | 04 |  | Nominal P GEN206 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40953 |  | 340954 | 04 |  | Nominal P GEN207 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40954 |  | 340955 | 04 |  | Nominal P GEN208 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40955 |  | 340956 | 04 |  | Nominal P GEN209 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40956 |  | 340957 | 04 |  | Nominal P GEN210 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40957 |  | 340958 | 04 |  | Nominal P GEN211 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40958 |  | 340959 | 04 |  | Nominal P GEN212 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40959 |  | 340960 | 04 |  | Nominal P GEN213 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40960 |  | 340961 | 04 |  | Nominal P GEN214 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40961 |  | 340962 | 04 |  | Nominal P GEN215 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40962 |  | 340963 | 04 |  | Nominal P GEN216 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40963 |  | 340964 | 04 |  | Nominal P GEN217 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40964 |  | 340965 | 04 |  | Nominal P GEN218 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40965 |  | 340966 | 04 |  | Nominal P GEN219 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40966 |  | 340967 | 04 |  | Nominal P GEN220 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40967 |  | 340968 | 04 |  | Nominal P GEN221 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40968 |  | 340969 | 04 |  | Nominal P GEN222 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40969 |  | 340970 | 04 |  | Nominal P GEN223 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40970 |  | 340971 | 04 |  | Nominal P GEN224 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40971 |  | 340972 | 04 |  | Nominal P GEN225 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40972 |  | 340973 | 04 |  | Nominal P GEN226 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40973 |  | 340974 | 04 |  | Nominal P GEN227 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40974 |  | 340975 | 04 |  | Nominal P GEN228 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40975 |  | 340976 | 04 |  | Nominal P GEN229 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40976 |  | 340977 | 04 |  | Nominal P GEN230 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40977 |  | 340978 | 04 |  | Nominal P GEN231 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40978 |  | 340979 | 04 |  | Nominal P GEN232 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40979 |  | 340980 | 04 |  | Nominal P GEN233 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40980 |  | 340981 | 04 |  | Nominal P GEN234 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40981 |  | 340982 | 04 |  | Nominal P GEN235 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40982 |  | 340983 | 04 |  | Nominal P GEN236 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40983 |  | 340984 | 04 |  | Nominal P GEN237 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40984 |  | 340985 | 04 |  | Nominal P GEN238 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40985 |  | 340986 | 04 |  | Nominal P GEN239 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40986 |  | 340987 | 04 |  | Nominal P GEN240 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40987 |  | 340988 | 04 |  | Nominal P GEN241 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40988 |  | 340989 | 04 |  | Nominal P GEN242 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40989 |  | 340990 | 04 |  | Nominal P GEN243 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40990 |  | 340991 | 04 |  | Nominal P GEN244 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40991 |  | 340992 | 04 |  | Nominal P GEN245 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40992 |  | 340993 | 04 |  | Nominal P GEN246 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40993 |  | 340994 | 04 |  | Nominal P GEN247 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40994 |  | 340995 | 04 |  | Nominal P GEN248 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40995 |  | 340996 | 04 |  | Nominal P GEN249 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40996 |  | 340997 | 04 |  | Nominal P GEN250 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40997 |  | 340998 | 04 |  | Nominal P GEN251 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40998 |  | 340999 | 04 |  | Nominal P GEN252 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 40999 |  | 341000 | 04 |  | Nominal P GEN253 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41000 |  | 341001 | 04 |  | Nominal P GEN254 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41001 |  | 341002 | 04 |  | Active P GEN1 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41002 |  | 341003 | 04 |  | Active P GEN2 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41003 |  | 341004 | 04 |  | Active P GEN3 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41004 |  | 341005 | 04 |  | Active P GEN4 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41005 |  | 341006 | 04 |  | Active P GEN5 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41006 |  | 341007 | 04 |  | Active P GEN6 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41007 |  | 341008 | 04 |  | Active P GEN7 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41008 |  | 341009 | 04 |  | Active P GEN8 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41009 |  | 341010 | 04 |  | Active P GEN9 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41010 |  | 341011 | 04 |  | Active P GEN10 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41011 |  | 341012 | 04 |  | Active P GEN11 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41012 |  | 341013 | 04 |  | Active P GEN12 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41013 |  | 341014 | 04 |  | Active P GEN13 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41014 |  | 341015 | 04 |  | Active P GEN14 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41015 |  | 341016 | 04 |  | Active P GEN15 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41016 |  | 341017 | 04 |  | Active P GEN16 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41017 |  | 341018 | 04 |  | Active P GEN17 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41018 |  | 341019 | 04 |  | Active P GEN18 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41019 |  | 341020 | 04 |  | Active P GEN19 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41020 |  | 341021 | 04 |  | Active P GEN20 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41021 |  | 341022 | 04 |  | Active P GEN21 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41022 |  | 341023 | 04 |  | Active P GEN22 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41023 |  | 341024 | 04 |  | Active P GEN23 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41024 |  | 341025 | 04 |  | Active P GEN24 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41025 |  | 341026 | 04 |  | Active P GEN25 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41026 |  | 341027 | 04 |  | Active P GEN26 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41027 |  | 341028 | 04 |  | Active P GEN27 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41028 |  | 341029 | 04 |  | Active P GEN28 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41029 |  | 341030 | 04 |  | Active P GEN29 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41030 |  | 341031 | 04 |  | Active P GEN30 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41031 |  | 341032 | 04 |  | Active P GEN31 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41032 |  | 341033 | 04 |  | Active P GEN32 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41033 |  | 341034 | 04 |  | Active P GEN33 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41034 |  | 341035 | 04 |  | Active P GEN34 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41035 |  | 341036 | 04 |  | Active P GEN35 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41036 |  | 341037 | 04 |  | Active P GEN36 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41037 |  | 341038 | 04 |  | Active P GEN37 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41038 |  | 341039 | 04 |  | Active P GEN38 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41039 |  | 341040 | 04 |  | Active P GEN39 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41040 |  | 341041 | 04 |  | Active P GEN40 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41041 |  | 341042 | 04 |  | Active P GEN41 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41042 |  | 341043 | 04 |  | Active P GEN42 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41043 |  | 341044 | 04 |  | Active P GEN43 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41044 |  | 341045 | 04 |  | Active P GEN44 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41045 |  | 341046 | 04 |  | Active P GEN45 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41046 |  | 341047 | 04 |  | Active P GEN46 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41047 |  | 341048 | 04 |  | Active P GEN47 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41048 |  | 341049 | 04 |  | Active P GEN48 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41049 |  | 341050 | 04 |  | Active P GEN49 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41050 |  | 341051 | 04 |  | Active P GEN50 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41051 |  | 341052 | 04 |  | Active P GEN51 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41052 |  | 341053 | 04 |  | Active P GEN52 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41053 |  | 341054 | 04 |  | Active P GEN53 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41054 |  | 341055 | 04 |  | Active P GEN54 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41055 |  | 341056 | 04 |  | Active P GEN55 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41056 |  | 341057 | 04 |  | Active P GEN56 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41057 |  | 341058 | 04 |  | Active P GEN57 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41058 |  | 341059 | 04 |  | Active P GEN58 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41059 |  | 341060 | 04 |  | Active P GEN59 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41060 |  | 341061 | 04 |  | Active P GEN60 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41061 |  | 341062 | 04 |  | Active P GEN61 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41062 |  | 341063 | 04 |  | Active P GEN62 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41063 |  | 341064 | 04 |  | Active P GEN63 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41064 |  | 341065 | 04 |  | Active P GEN64 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41065 |  | 341066 | 04 |  | Active P GEN65 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41066 |  | 341067 | 04 |  | Active P GEN66 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41067 |  | 341068 | 04 |  | Active P GEN67 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41068 |  | 341069 | 04 |  | Active P GEN68 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41069 |  | 341070 | 04 |  | Active P GEN69 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41070 |  | 341071 | 04 |  | Active P GEN70 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41071 |  | 341072 | 04 |  | Active P GEN71 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41072 |  | 341073 | 04 |  | Active P GEN72 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41073 |  | 341074 | 04 |  | Active P GEN73 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41074 |  | 341075 | 04 |  | Active P GEN74 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41075 |  | 341076 | 04 |  | Active P GEN75 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41076 |  | 341077 | 04 |  | Active P GEN76 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41077 |  | 341078 | 04 |  | Active P GEN77 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41078 |  | 341079 | 04 |  | Active P GEN78 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41079 |  | 341080 | 04 |  | Active P GEN79 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41080 |  | 341081 | 04 |  | Active P GEN80 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41081 |  | 341082 | 04 |  | Active P GEN81 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41082 |  | 341083 | 04 |  | Active P GEN82 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41083 |  | 341084 | 04 |  | Active P GEN83 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41084 |  | 341085 | 04 |  | Active P GEN84 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41085 |  | 341086 | 04 |  | Active P GEN85 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41086 |  | 341087 | 04 |  | Active P GEN86 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41087 |  | 341088 | 04 |  | Active P GEN87 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41088 |  | 341089 | 04 |  | Active P GEN88 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41089 |  | 341090 | 04 |  | Active P GEN89 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41090 |  | 341091 | 04 |  | Active P GEN90 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41091 |  | 341092 | 04 |  | Active P GEN91 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41092 |  | 341093 | 04 |  | Active P GEN92 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41093 |  | 341094 | 04 |  | Active P GEN93 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41094 |  | 341095 | 04 |  | Active P GEN94 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41095 |  | 341096 | 04 |  | Active P GEN95 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41096 |  | 341097 | 04 |  | Active P GEN96 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41097 |  | 341098 | 04 |  | Active P GEN97 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41098 |  | 341099 | 04 |  | Active P GEN98 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41099 |  | 341100 | 04 |  | Active P GEN99 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41100 |  | 341101 | 04 |  | Active P GEN100 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41101 |  | 341102 | 04 |  | Active P GEN101 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41102 |  | 341103 | 04 |  | Active P GEN102 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41103 |  | 341104 | 04 |  | Active P GEN103 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41104 |  | 341105 | 04 |  | Active P GEN104 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41105 |  | 341106 | 04 |  | Active P GEN105 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41106 |  | 341107 | 04 |  | Active P GEN106 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41107 |  | 341108 | 04 |  | Active P GEN107 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41108 |  | 341109 | 04 |  | Active P GEN108 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41109 |  | 341110 | 04 |  | Active P GEN109 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41110 |  | 341111 | 04 |  | Active P GEN110 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41111 |  | 341112 | 04 |  | Active P GEN111 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41112 |  | 341113 | 04 |  | Active P GEN112 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41113 |  | 341114 | 04 |  | Active P GEN113 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41114 |  | 341115 | 04 |  | Active P GEN114 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41115 |  | 341116 | 04 |  | Active P GEN115 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41116 |  | 341117 | 04 |  | Active P GEN116 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41117 |  | 341118 | 04 |  | Active P GEN117 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41118 |  | 341119 | 04 |  | Active P GEN118 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41119 |  | 341120 | 04 |  | Active P GEN119 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41120 |  | 341121 | 04 |  | Active P GEN120 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41121 |  | 341122 | 04 |  | Active P GEN121 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41122 |  | 341123 | 04 |  | Active P GEN122 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41123 |  | 341124 | 04 |  | Active P GEN123 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41124 |  | 341125 | 04 |  | Active P GEN124 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41125 |  | 341126 | 04 |  | Active P GEN125 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41126 |  | 341127 | 04 |  | Active P GEN126 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41127 |  | 341128 | 04 |  | Active P GEN127 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41128 |  | 341129 | 04 |  | Active P GEN128 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41129 |  | 341130 | 04 |  | Active P GEN129 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41130 |  | 341131 | 04 |  | Active P GEN130 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41131 |  | 341132 | 04 |  | Active P GEN131 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41132 |  | 341133 | 04 |  | Active P GEN132 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41133 |  | 341134 | 04 |  | Active P GEN133 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41134 |  | 341135 | 04 |  | Active P GEN134 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41135 |  | 341136 | 04 |  | Active P GEN135 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41136 |  | 341137 | 04 |  | Active P GEN136 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41137 |  | 341138 | 04 |  | Active P GEN137 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41138 |  | 341139 | 04 |  | Active P GEN138 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41139 |  | 341140 | 04 |  | Active P GEN139 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41140 |  | 341141 | 04 |  | Active P GEN140 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41141 |  | 341142 | 04 |  | Active P GEN141 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41142 |  | 341143 | 04 |  | Active P GEN142 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41143 |  | 341144 | 04 |  | Active P GEN143 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41144 |  | 341145 | 04 |  | Active P GEN144 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41145 |  | 341146 | 04 |  | Active P GEN145 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41146 |  | 341147 | 04 |  | Active P GEN146 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41147 |  | 341148 | 04 |  | Active P GEN147 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41148 |  | 341149 | 04 |  | Active P GEN148 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41149 |  | 341150 | 04 |  | Active P GEN149 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41150 |  | 341151 | 04 |  | Active P GEN150 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41151 |  | 341152 | 04 |  | Active P GEN151 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41152 |  | 341153 | 04 |  | Active P GEN152 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41153 |  | 341154 | 04 |  | Active P GEN153 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41154 |  | 341155 | 04 |  | Active P GEN154 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41155 |  | 341156 | 04 |  | Active P GEN155 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41156 |  | 341157 | 04 |  | Active P GEN156 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41157 |  | 341158 | 04 |  | Active P GEN157 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41158 |  | 341159 | 04 |  | Active P GEN158 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41159 |  | 341160 | 04 |  | Active P GEN159 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41160 |  | 341161 | 04 |  | Active P GEN160 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41161 |  | 341162 | 04 |  | Active P GEN161 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41162 |  | 341163 | 04 |  | Active P GEN162 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41163 |  | 341164 | 04 |  | Active P GEN163 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41164 |  | 341165 | 04 |  | Active P GEN164 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41165 |  | 341166 | 04 |  | Active P GEN165 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41166 |  | 341167 | 04 |  | Active P GEN166 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41167 |  | 341168 | 04 |  | Active P GEN167 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41168 |  | 341169 | 04 |  | Active P GEN168 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41169 |  | 341170 | 04 |  | Active P GEN169 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41170 |  | 341171 | 04 |  | Active P GEN170 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41171 |  | 341172 | 04 |  | Active P GEN171 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41172 |  | 341173 | 04 |  | Active P GEN172 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41173 |  | 341174 | 04 |  | Active P GEN173 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41174 |  | 341175 | 04 |  | Active P GEN174 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41175 |  | 341176 | 04 |  | Active P GEN175 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41176 |  | 341177 | 04 |  | Active P GEN176 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41177 |  | 341178 | 04 |  | Active P GEN177 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41178 |  | 341179 | 04 |  | Active P GEN178 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41179 |  | 341180 | 04 |  | Active P GEN179 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41180 |  | 341181 | 04 |  | Active P GEN180 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41181 |  | 341182 | 04 |  | Active P GEN181 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41182 |  | 341183 | 04 |  | Active P GEN182 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41183 |  | 341184 | 04 |  | Active P GEN183 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41184 |  | 341185 | 04 |  | Active P GEN184 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41185 |  | 341186 | 04 |  | Active P GEN185 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41186 |  | 341187 | 04 |  | Active P GEN186 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41187 |  | 341188 | 04 |  | Active P GEN187 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41188 |  | 341189 | 04 |  | Active P GEN188 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41189 |  | 341190 | 04 |  | Active P GEN189 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41190 |  | 341191 | 04 |  | Active P GEN190 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41191 |  | 341192 | 04 |  | Active P GEN191 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41192 |  | 341193 | 04 |  | Active P GEN192 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41193 |  | 341194 | 04 |  | Active P GEN193 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41194 |  | 341195 | 04 |  | Active P GEN194 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41195 |  | 341196 | 04 |  | Active P GEN195 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41196 |  | 341197 | 04 |  | Active P GEN196 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41197 |  | 341198 | 04 |  | Active P GEN197 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41198 |  | 341199 | 04 |  | Active P GEN198 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41199 |  | 341200 | 04 |  | Active P GEN199 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41200 |  | 341201 | 04 |  | Active P GEN200 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41201 |  | 341202 | 04 |  | Active P GEN201 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41202 |  | 341203 | 04 |  | Active P GEN202 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41203 |  | 341204 | 04 |  | Active P GEN203 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41204 |  | 341205 | 04 |  | Active P GEN204 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41205 |  | 341206 | 04 |  | Active P GEN205 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41206 |  | 341207 | 04 |  | Active P GEN206 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41207 |  | 341208 | 04 |  | Active P GEN207 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41208 |  | 341209 | 04 |  | Active P GEN208 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41209 |  | 341210 | 04 |  | Active P GEN209 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41210 |  | 341211 | 04 |  | Active P GEN210 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41211 |  | 341212 | 04 |  | Active P GEN211 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41212 |  | 341213 | 04 |  | Active P GEN212 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41213 |  | 341214 | 04 |  | Active P GEN213 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41214 |  | 341215 | 04 |  | Active P GEN214 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41215 |  | 341216 | 04 |  | Active P GEN215 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41216 |  | 341217 | 04 |  | Active P GEN216 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41217 |  | 341218 | 04 |  | Active P GEN217 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41218 |  | 341219 | 04 |  | Active P GEN218 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41219 |  | 341220 | 04 |  | Active P GEN219 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41220 |  | 341221 | 04 |  | Active P GEN220 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41221 |  | 341222 | 04 |  | Active P GEN221 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41222 |  | 341223 | 04 |  | Active P GEN222 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41223 |  | 341224 | 04 |  | Active P GEN223 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41224 |  | 341225 | 04 |  | Active P GEN224 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41225 |  | 341226 | 04 |  | Active P GEN225 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41226 |  | 341227 | 04 |  | Active P GEN226 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41227 |  | 341228 | 04 |  | Active P GEN227 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41228 |  | 341229 | 04 |  | Active P GEN228 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41229 |  | 341230 | 04 |  | Active P GEN229 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41230 |  | 341231 | 04 |  | Active P GEN230 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41231 |  | 341232 | 04 |  | Active P GEN231 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41232 |  | 341233 | 04 |  | Active P GEN232 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41233 |  | 341234 | 04 |  | Active P GEN233 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41234 |  | 341235 | 04 |  | Active P GEN234 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41235 |  | 341236 | 04 |  | Active P GEN235 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41236 |  | 341237 | 04 |  | Active P GEN236 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41237 |  | 341238 | 04 |  | Active P GEN237 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41238 |  | 341239 | 04 |  | Active P GEN238 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41239 |  | 341240 | 04 |  | Active P GEN239 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41240 |  | 341241 | 04 |  | Active P GEN240 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41241 |  | 341242 | 04 |  | Active P GEN241 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41242 |  | 341243 | 04 |  | Active P GEN242 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41243 |  | 341244 | 04 |  | Active P GEN243 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41244 |  | 341245 | 04 |  | Active P GEN244 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41245 |  | 341246 | 04 |  | Active P GEN245 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41246 |  | 341247 | 04 |  | Active P GEN246 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41247 |  | 341248 | 04 |  | Active P GEN247 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41248 |  | 341249 | 04 |  | Active P GEN248 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41249 |  | 341250 | 04 |  | Active P GEN249 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41250 |  | 341251 | 04 |  | Active P GEN250 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41251 |  | 341252 | 04 |  | Active P GEN251 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41252 |  | 341253 | 04 |  | Active P GEN252 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41253 |  | 341254 | 04 |  | Active P GEN253 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41254 |  | 341255 | 04 |  | Active P GEN254 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41255 |  | 341256 | 04 |  | Active Q GEN1 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41256 |  | 341257 | 04 |  | Active Q GEN2 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41257 |  | 341258 | 04 |  | Active Q GEN3 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41258 |  | 341259 | 04 |  | Active Q GEN4 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41259 |  | 341260 | 04 |  | Active Q GEN5 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41260 |  | 341261 | 04 |  | Active Q GEN6 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41261 |  | 341262 | 04 |  | Active Q GEN7 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41262 |  | 341263 | 04 |  | Active Q GEN8 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41263 |  | 341264 | 04 |  | Active Q GEN9 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41264 |  | 341265 | 04 |  | Active Q GEN10 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41265 |  | 341266 | 04 |  | Active Q GEN11 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41266 |  | 341267 | 04 |  | Active Q GEN12 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41267 |  | 341268 | 04 |  | Active Q GEN13 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41268 |  | 341269 | 04 |  | Active Q GEN14 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41269 |  | 341270 | 04 |  | Active Q GEN15 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41270 |  | 341271 | 04 |  | Active Q GEN16 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41271 |  | 341272 | 04 |  | Active Q GEN17 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41272 |  | 341273 | 04 |  | Active Q GEN18 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41273 |  | 341274 | 04 |  | Active Q GEN19 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41274 |  | 341275 | 04 |  | Active Q GEN20 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41275 |  | 341276 | 04 |  | Active Q GEN21 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41276 |  | 341277 | 04 |  | Active Q GEN22 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41277 |  | 341278 | 04 |  | Active Q GEN23 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41278 |  | 341279 | 04 |  | Active Q GEN24 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41279 |  | 341280 | 04 |  | Active Q GEN25 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41280 |  | 341281 | 04 |  | Active Q GEN26 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41281 |  | 341282 | 04 |  | Active Q GEN27 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41282 |  | 341283 | 04 |  | Active Q GEN28 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41283 |  | 341284 | 04 |  | Active Q GEN29 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41284 |  | 341285 | 04 |  | Active Q GEN30 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41285 |  | 341286 | 04 |  | Active Q GEN31 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41286 |  | 341287 | 04 |  | Active Q GEN32 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41287 |  | 341288 | 04 |  | Active Q GEN33 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41288 |  | 341289 | 04 |  | Active Q GEN34 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41289 |  | 341290 | 04 |  | Active Q GEN35 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41290 |  | 341291 | 04 |  | Active Q GEN36 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41291 |  | 341292 | 04 |  | Active Q GEN37 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41292 |  | 341293 | 04 |  | Active Q GEN38 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41293 |  | 341294 | 04 |  | Active Q GEN39 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41294 |  | 341295 | 04 |  | Active Q GEN40 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41295 |  | 341296 | 04 |  | Active Q GEN41 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41296 |  | 341297 | 04 |  | Active Q GEN42 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41297 |  | 341298 | 04 |  | Active Q GEN43 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41298 |  | 341299 | 04 |  | Active Q GEN44 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41299 |  | 341300 | 04 |  | Active Q GEN45 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41300 |  | 341301 | 04 |  | Active Q GEN46 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41301 |  | 341302 | 04 |  | Active Q GEN47 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41302 |  | 341303 | 04 |  | Active Q GEN48 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41303 |  | 341304 | 04 |  | Active Q GEN49 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41304 |  | 341305 | 04 |  | Active Q GEN50 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41305 |  | 341306 | 04 |  | Active Q GEN51 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41306 |  | 341307 | 04 |  | Active Q GEN52 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41307 |  | 341308 | 04 |  | Active Q GEN53 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41308 |  | 341309 | 04 |  | Active Q GEN54 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41309 |  | 341310 | 04 |  | Active Q GEN55 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41310 |  | 341311 | 04 |  | Active Q GEN56 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41311 |  | 341312 | 04 |  | Active Q GEN57 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41312 |  | 341313 | 04 |  | Active Q GEN58 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41313 |  | 341314 | 04 |  | Active Q GEN59 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41314 |  | 341315 | 04 |  | Active Q GEN60 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41315 |  | 341316 | 04 |  | Active Q GEN61 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41316 |  | 341317 | 04 |  | Active Q GEN62 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41317 |  | 341318 | 04 |  | Active Q GEN63 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41318 |  | 341319 | 04 |  | Active Q GEN64 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41319 |  | 341320 | 04 |  | Active Q GEN65 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41320 |  | 341321 | 04 |  | Active Q GEN66 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41321 |  | 341322 | 04 |  | Active Q GEN67 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41322 |  | 341323 | 04 |  | Active Q GEN68 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41323 |  | 341324 | 04 |  | Active Q GEN69 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41324 |  | 341325 | 04 |  | Active Q GEN70 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41325 |  | 341326 | 04 |  | Active Q GEN71 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41326 |  | 341327 | 04 |  | Active Q GEN72 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41327 |  | 341328 | 04 |  | Active Q GEN73 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41328 |  | 341329 | 04 |  | Active Q GEN74 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41329 |  | 341330 | 04 |  | Active Q GEN75 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41330 |  | 341331 | 04 |  | Active Q GEN76 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41331 |  | 341332 | 04 |  | Active Q GEN77 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41332 |  | 341333 | 04 |  | Active Q GEN78 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41333 |  | 341334 | 04 |  | Active Q GEN79 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41334 |  | 341335 | 04 |  | Active Q GEN80 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41335 |  | 341336 | 04 |  | Active Q GEN81 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41336 |  | 341337 | 04 |  | Active Q GEN82 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41337 |  | 341338 | 04 |  | Active Q GEN83 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41338 |  | 341339 | 04 |  | Active Q GEN84 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41339 |  | 341340 | 04 |  | Active Q GEN85 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41340 |  | 341341 | 04 |  | Active Q GEN86 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41341 |  | 341342 | 04 |  | Active Q GEN87 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41342 |  | 341343 | 04 |  | Active Q GEN88 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41343 |  | 341344 | 04 |  | Active Q GEN89 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41344 |  | 341345 | 04 |  | Active Q GEN90 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41345 |  | 341346 | 04 |  | Active Q GEN91 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41346 |  | 341347 | 04 |  | Active Q GEN92 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41347 |  | 341348 | 04 |  | Active Q GEN93 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41348 |  | 341349 | 04 |  | Active Q GEN94 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41349 |  | 341350 | 04 |  | Active Q GEN95 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41350 |  | 341351 | 04 |  | Active Q GEN96 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41351 |  | 341352 | 04 |  | Active Q GEN97 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41352 |  | 341353 | 04 |  | Active Q GEN98 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41353 |  | 341354 | 04 |  | Active Q GEN99 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41354 |  | 341355 | 04 |  | Active Q GEN100 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41355 |  | 341356 | 04 |  | Active Q GEN101 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41356 |  | 341357 | 04 |  | Active Q GEN102 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41357 |  | 341358 | 04 |  | Active Q GEN103 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41358 |  | 341359 | 04 |  | Active Q GEN104 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41359 |  | 341360 | 04 |  | Active Q GEN105 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41360 |  | 341361 | 04 |  | Active Q GEN106 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41361 |  | 341362 | 04 |  | Active Q GEN107 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41362 |  | 341363 | 04 |  | Active Q GEN108 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41363 |  | 341364 | 04 |  | Active Q GEN109 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41364 |  | 341365 | 04 |  | Active Q GEN110 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41365 |  | 341366 | 04 |  | Active Q GEN111 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41366 |  | 341367 | 04 |  | Active Q GEN112 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41367 |  | 341368 | 04 |  | Active Q GEN113 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41368 |  | 341369 | 04 |  | Active Q GEN114 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41369 |  | 341370 | 04 |  | Active Q GEN115 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41370 |  | 341371 | 04 |  | Active Q GEN116 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41371 |  | 341372 | 04 |  | Active Q GEN117 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41372 |  | 341373 | 04 |  | Active Q GEN118 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41373 |  | 341374 | 04 |  | Active Q GEN119 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41374 |  | 341375 | 04 |  | Active Q GEN120 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41375 |  | 341376 | 04 |  | Active Q GEN121 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41376 |  | 341377 | 04 |  | Active Q GEN122 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41377 |  | 341378 | 04 |  | Active Q GEN123 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41378 |  | 341379 | 04 |  | Active Q GEN124 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41379 |  | 341380 | 04 |  | Active Q GEN125 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41380 |  | 341381 | 04 |  | Active Q GEN126 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41381 |  | 341382 | 04 |  | Active Q GEN127 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41382 |  | 341383 | 04 |  | Active Q GEN128 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41383 |  | 341384 | 04 |  | Active Q GEN129 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41384 |  | 341385 | 04 |  | Active Q GEN130 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41385 |  | 341386 | 04 |  | Active Q GEN131 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41386 |  | 341387 | 04 |  | Active Q GEN132 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41387 |  | 341388 | 04 |  | Active Q GEN133 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41388 |  | 341389 | 04 |  | Active Q GEN134 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41389 |  | 341390 | 04 |  | Active Q GEN135 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41390 |  | 341391 | 04 |  | Active Q GEN136 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41391 |  | 341392 | 04 |  | Active Q GEN137 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41392 |  | 341393 | 04 |  | Active Q GEN138 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41393 |  | 341394 | 04 |  | Active Q GEN139 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41394 |  | 341395 | 04 |  | Active Q GEN140 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41395 |  | 341396 | 04 |  | Active Q GEN141 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41396 |  | 341397 | 04 |  | Active Q GEN142 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41397 |  | 341398 | 04 |  | Active Q GEN143 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41398 |  | 341399 | 04 |  | Active Q GEN144 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41399 |  | 341400 | 04 |  | Active Q GEN145 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41400 |  | 341401 | 04 |  | Active Q GEN146 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41401 |  | 341402 | 04 |  | Active Q GEN147 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41402 |  | 341403 | 04 |  | Active Q GEN148 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41403 |  | 341404 | 04 |  | Active Q GEN149 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41404 |  | 341405 | 04 |  | Active Q GEN150 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41405 |  | 341406 | 04 |  | Active Q GEN151 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41406 |  | 341407 | 04 |  | Active Q GEN152 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41407 |  | 341408 | 04 |  | Active Q GEN153 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41408 |  | 341409 | 04 |  | Active Q GEN154 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41409 |  | 341410 | 04 |  | Active Q GEN155 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41410 |  | 341411 | 04 |  | Active Q GEN156 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41411 |  | 341412 | 04 |  | Active Q GEN157 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41412 |  | 341413 | 04 |  | Active Q GEN158 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41413 |  | 341414 | 04 |  | Active Q GEN159 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41414 |  | 341415 | 04 |  | Active Q GEN160 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41415 |  | 341416 | 04 |  | Active Q GEN161 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41416 |  | 341417 | 04 |  | Active Q GEN162 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41417 |  | 341418 | 04 |  | Active Q GEN163 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41418 |  | 341419 | 04 |  | Active Q GEN164 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41419 |  | 341420 | 04 |  | Active Q GEN165 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41420 |  | 341421 | 04 |  | Active Q GEN166 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41421 |  | 341422 | 04 |  | Active Q GEN167 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41422 |  | 341423 | 04 |  | Active Q GEN168 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41423 |  | 341424 | 04 |  | Active Q GEN169 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41424 |  | 341425 | 04 |  | Active Q GEN170 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41425 |  | 341426 | 04 |  | Active Q GEN171 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41426 |  | 341427 | 04 |  | Active Q GEN172 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41427 |  | 341428 | 04 |  | Active Q GEN173 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41428 |  | 341429 | 04 |  | Active Q GEN174 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41429 |  | 341430 | 04 |  | Active Q GEN175 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41430 |  | 341431 | 04 |  | Active Q GEN176 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41431 |  | 341432 | 04 |  | Active Q GEN177 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41432 |  | 341433 | 04 |  | Active Q GEN178 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41433 |  | 341434 | 04 |  | Active Q GEN179 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41434 |  | 341435 | 04 |  | Active Q GEN180 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41435 |  | 341436 | 04 |  | Active Q GEN181 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41436 |  | 341437 | 04 |  | Active Q GEN182 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41437 |  | 341438 | 04 |  | Active Q GEN183 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41438 |  | 341439 | 04 |  | Active Q GEN184 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41439 |  | 341440 | 04 |  | Active Q GEN185 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41440 |  | 341441 | 04 |  | Active Q GEN186 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41441 |  | 341442 | 04 |  | Active Q GEN187 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41442 |  | 341443 | 04 |  | Active Q GEN188 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41443 |  | 341444 | 04 |  | Active Q GEN189 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41444 |  | 341445 | 04 |  | Active Q GEN190 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41445 |  | 341446 | 04 |  | Active Q GEN191 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41446 |  | 341447 | 04 |  | Active Q GEN192 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41447 |  | 341448 | 04 |  | Active Q GEN193 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41448 |  | 341449 | 04 |  | Active Q GEN194 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41449 |  | 341450 | 04 |  | Active Q GEN195 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41450 |  | 341451 | 04 |  | Active Q GEN196 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41451 |  | 341452 | 04 |  | Active Q GEN197 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41452 |  | 341453 | 04 |  | Active Q GEN198 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41453 |  | 341454 | 04 |  | Active Q GEN199 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41454 |  | 341455 | 04 |  | Active Q GEN200 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41455 |  | 341456 | 04 |  | Active Q GEN201 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41456 |  | 341457 | 04 |  | Active Q GEN202 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41457 |  | 341458 | 04 |  | Active Q GEN203 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41458 |  | 341459 | 04 |  | Active Q GEN204 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41459 |  | 341460 | 04 |  | Active Q GEN205 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41460 |  | 341461 | 04 |  | Active Q GEN206 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41461 |  | 341462 | 04 |  | Active Q GEN207 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41462 |  | 341463 | 04 |  | Active Q GEN208 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41463 |  | 341464 | 04 |  | Active Q GEN209 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41464 |  | 341465 | 04 |  | Active Q GEN210 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41465 |  | 341466 | 04 |  | Active Q GEN211 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41466 |  | 341467 | 04 |  | Active Q GEN212 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41467 |  | 341468 | 04 |  | Active Q GEN213 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41468 |  | 341469 | 04 |  | Active Q GEN214 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41469 |  | 341470 | 04 |  | Active Q GEN215 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41470 |  | 341471 | 04 |  | Active Q GEN216 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41471 |  | 341472 | 04 |  | Active Q GEN217 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41472 |  | 341473 | 04 |  | Active Q GEN218 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41473 |  | 341474 | 04 |  | Active Q GEN219 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41474 |  | 341475 | 04 |  | Active Q GEN220 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41475 |  | 341476 | 04 |  | Active Q GEN221 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41476 |  | 341477 | 04 |  | Active Q GEN222 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41477 |  | 341478 | 04 |  | Active Q GEN223 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41478 |  | 341479 | 04 |  | Active Q GEN224 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41479 |  | 341480 | 04 |  | Active Q GEN225 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41480 |  | 341481 | 04 |  | Active Q GEN226 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41481 |  | 341482 | 04 |  | Active Q GEN227 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41482 |  | 341483 | 04 |  | Active Q GEN228 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41483 |  | 341484 | 04 |  | Active Q GEN229 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41484 |  | 341485 | 04 |  | Active Q GEN230 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41485 |  | 341486 | 04 |  | Active Q GEN231 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41486 |  | 341487 | 04 |  | Active Q GEN232 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41487 |  | 341488 | 04 |  | Active Q GEN233 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41488 |  | 341489 | 04 |  | Active Q GEN234 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41489 |  | 341490 | 04 |  | Active Q GEN235 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41490 |  | 341491 | 04 |  | Active Q GEN236 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41491 |  | 341492 | 04 |  | Active Q GEN237 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41492 |  | 341493 | 04 |  | Active Q GEN238 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41493 |  | 341494 | 04 |  | Active Q GEN239 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41494 |  | 341495 | 04 |  | Active Q GEN240 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41495 |  | 341496 | 04 |  | Active Q GEN241 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41496 |  | 341497 | 04 |  | Active Q GEN242 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41497 |  | 341498 | 04 |  | Active Q GEN243 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41498 |  | 341499 | 04 |  | Active Q GEN244 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41499 |  | 341500 | 04 |  | Active Q GEN245 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41500 |  | 341501 | 04 |  | Active Q GEN246 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41501 |  | 341502 | 04 |  | Active Q GEN247 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41502 |  | 341503 | 04 |  | Active Q GEN248 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41503 |  | 341504 | 04 |  | Active Q GEN249 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41504 |  | 341505 | 04 |  | Active Q GEN250 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41505 |  | 341506 | 04 |  | Active Q GEN251 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41506 |  | 341507 | 04 |  | Active Q GEN252 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41507 |  | 341508 | 04 |  | Active Q GEN253 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41508 |  | 341509 | 04 |  | Active Q GEN254 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 41970 | 0 | 341971 | 04 |  | Multistart enabled GEN1 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 1 | 341971 | 04 |  | Multistart enabled GEN2 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 2 | 341971 | 04 |  | Multistart enabled GEN3 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 3 | 341971 | 04 |  | Multistart enabled GEN4 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 4 | 341971 | 04 |  | Multistart enabled GEN5 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 5 | 341971 | 04 |  | Multistart enabled GEN6 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 6 | 341971 | 04 |  | Multistart enabled GEN7 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 7 | 341971 | 04 |  | Multistart enabled GEN8 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 8 | 341971 | 04 |  | Multistart enabled GEN9 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 9 | 341971 | 04 |  | Multistart enabled GEN10 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 10 | 341971 | 04 |  | Multistart enabled GEN11 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 11 | 341971 | 04 |  | Multistart enabled GEN12 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 12 | 341971 | 04 |  | Multistart enabled GEN13 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 13 | 341971 | 04 |  | Multistart enabled GEN14 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 14 | 341971 | 04 |  | Multistart enabled GEN15 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41970 | 15 | 341971 | 04 |  | Multistart enabled GEN16 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 0 | 341972 | 04 |  | Multistart enabled GEN17 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 1 | 341972 | 04 |  | Multistart enabled GEN18 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 2 | 341972 | 04 |  | Multistart enabled GEN19 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 3 | 341972 | 04 |  | Multistart enabled GEN20 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 4 | 341972 | 04 |  | Multistart enabled GEN21 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 5 | 341972 | 04 |  | Multistart enabled GEN22 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 6 | 341972 | 04 |  | Multistart enabled GEN23 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 7 | 341972 | 04 |  | Multistart enabled GEN24 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 8 | 341972 | 04 |  | Multistart enabled GEN25 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 9 | 341972 | 04 |  | Multistart enabled GEN26 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 10 | 341972 | 04 |  | Multistart enabled GEN27 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 11 | 341972 | 04 |  | Multistart enabled GEN28 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 12 | 341972 | 04 |  | Multistart enabled GEN29 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 13 | 341972 | 04 |  | Multistart enabled GEN30 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 14 | 341972 | 04 |  | Multistart enabled GEN31 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41971 | 15 | 341972 | 04 |  | Multistart enabled GEN32 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 0 | 341973 | 04 |  | Multistart enabled GEN33 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 1 | 341973 | 04 |  | Multistart enabled GEN34 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 2 | 341973 | 04 |  | Multistart enabled GEN35 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 3 | 341973 | 04 |  | Multistart enabled GEN36 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 4 | 341973 | 04 |  | Multistart enabled GEN37 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 5 | 341973 | 04 |  | Multistart enabled GEN38 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 6 | 341973 | 04 |  | Multistart enabled GEN39 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 7 | 341973 | 04 |  | Multistart enabled GEN40 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 8 | 341973 | 04 |  | Multistart enabled GEN41 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 9 | 341973 | 04 |  | Multistart enabled GEN42 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 10 | 341973 | 04 |  | Multistart enabled GEN43 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 11 | 341973 | 04 |  | Multistart enabled GEN44 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 12 | 341973 | 04 |  | Multistart enabled GEN45 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 13 | 341973 | 04 |  | Multistart enabled GEN46 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 14 | 341973 | 04 |  | Multistart enabled GEN47 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41972 | 15 | 341973 | 04 |  | Multistart enabled GEN48 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 0 | 341974 | 04 |  | Multistart enabled GEN49 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 1 | 341974 | 04 |  | Multistart enabled GEN50 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 2 | 341974 | 04 |  | Multistart enabled GEN51 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 3 | 341974 | 04 |  | Multistart enabled GEN52 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 4 | 341974 | 04 |  | Multistart enabled GEN53 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 5 | 341974 | 04 |  | Multistart enabled GEN54 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 6 | 341974 | 04 |  | Multistart enabled GEN55 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 7 | 341974 | 04 |  | Multistart enabled GEN56 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 8 | 341974 | 04 |  | Multistart enabled GEN57 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 9 | 341974 | 04 |  | Multistart enabled GEN58 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 10 | 341974 | 04 |  | Multistart enabled GEN59 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 11 | 341974 | 04 |  | Multistart enabled GEN60 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 12 | 341974 | 04 |  | Multistart enabled GEN61 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 13 | 341974 | 04 |  | Multistart enabled GEN62 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 14 | 341974 | 04 |  | Multistart enabled GEN63 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41973 | 15 | 341974 | 04 |  | Multistart enabled GEN64 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 0 | 341975 | 04 |  | Multistart enabled GEN65 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 1 | 341975 | 04 |  | Multistart enabled GEN66 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 2 | 341975 | 04 |  | Multistart enabled GEN67 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 3 | 341975 | 04 |  | Multistart enabled GEN68 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 4 | 341975 | 04 |  | Multistart enabled GEN69 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 5 | 341975 | 04 |  | Multistart enabled GEN70 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 6 | 341975 | 04 |  | Multistart enabled GEN71 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 7 | 341975 | 04 |  | Multistart enabled GEN72 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 8 | 341975 | 04 |  | Multistart enabled GEN73 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 9 | 341975 | 04 |  | Multistart enabled GEN74 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 10 | 341975 | 04 |  | Multistart enabled GEN75 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 11 | 341975 | 04 |  | Multistart enabled GEN76 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 12 | 341975 | 04 |  | Multistart enabled GEN77 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 13 | 341975 | 04 |  | Multistart enabled GEN78 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 14 | 341975 | 04 |  | Multistart enabled GEN79 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41974 | 15 | 341975 | 04 |  | Multistart enabled GEN80 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 0 | 341976 | 04 |  | Multistart enabled GEN81 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 1 | 341976 | 04 |  | Multistart enabled GEN82 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 2 | 341976 | 04 |  | Multistart enabled GEN83 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 3 | 341976 | 04 |  | Multistart enabled GEN84 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 4 | 341976 | 04 |  | Multistart enabled GEN85 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 5 | 341976 | 04 |  | Multistart enabled GEN86 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 6 | 341976 | 04 |  | Multistart enabled GEN87 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 7 | 341976 | 04 |  | Multistart enabled GEN88 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 8 | 341976 | 04 |  | Multistart enabled GEN89 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 9 | 341976 | 04 |  | Multistart enabled GEN90 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 10 | 341976 | 04 |  | Multistart enabled GEN91 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 11 | 341976 | 04 |  | Multistart enabled GEN92 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 12 | 341976 | 04 |  | Multistart enabled GEN93 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 13 | 341976 | 04 |  | Multistart enabled GEN94 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 14 | 341976 | 04 |  | Multistart enabled GEN95 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41975 | 15 | 341976 | 04 |  | Multistart enabled GEN96 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 0 | 341977 | 04 |  | Multistart enabled GEN97 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 1 | 341977 | 04 |  | Multistart enabled GEN98 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 2 | 341977 | 04 |  | Multistart enabled GEN99 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 3 | 341977 | 04 |  | Multistart enabled GEN100 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 4 | 341977 | 04 |  | Multistart enabled GEN101 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 5 | 341977 | 04 |  | Multistart enabled GEN102 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 6 | 341977 | 04 |  | Multistart enabled GEN103 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 7 | 341977 | 04 |  | Multistart enabled GEN104 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 8 | 341977 | 04 |  | Multistart enabled GEN105 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 9 | 341977 | 04 |  | Multistart enabled GEN106 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 10 | 341977 | 04 |  | Multistart enabled GEN107 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 11 | 341977 | 04 |  | Multistart enabled GEN108 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 12 | 341977 | 04 |  | Multistart enabled GEN109 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 13 | 341977 | 04 |  | Multistart enabled GEN110 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 14 | 341977 | 04 |  | Multistart enabled GEN111 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41976 | 15 | 341977 | 04 |  | Multistart enabled GEN112 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 0 | 341978 | 04 |  | Multistart enabled GEN113 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 1 | 341978 | 04 |  | Multistart enabled GEN114 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 2 | 341978 | 04 |  | Multistart enabled GEN115 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 3 | 341978 | 04 |  | Multistart enabled GEN116 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 4 | 341978 | 04 |  | Multistart enabled GEN117 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 5 | 341978 | 04 |  | Multistart enabled GEN118 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 6 | 341978 | 04 |  | Multistart enabled GEN119 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 7 | 341978 | 04 |  | Multistart enabled GEN120 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 8 | 341978 | 04 |  | Multistart enabled GEN121 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 9 | 341978 | 04 |  | Multistart enabled GEN122 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 10 | 341978 | 04 |  | Multistart enabled GEN123 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 11 | 341978 | 04 |  | Multistart enabled GEN124 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 12 | 341978 | 04 |  | Multistart enabled GEN125 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 13 | 341978 | 04 |  | Multistart enabled GEN126 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 14 | 341978 | 04 |  | Multistart enabled GEN127 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41977 | 15 | 341978 | 04 |  | Multistart enabled GEN128 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 0 | 341979 | 04 |  | Multistart enabled GEN129 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 1 | 341979 | 04 |  | Multistart enabled GEN130 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 2 | 341979 | 04 |  | Multistart enabled GEN131 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 3 | 341979 | 04 |  | Multistart enabled GEN132 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 4 | 341979 | 04 |  | Multistart enabled GEN133 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 5 | 341979 | 04 |  | Multistart enabled GEN134 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 6 | 341979 | 04 |  | Multistart enabled GEN135 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 7 | 341979 | 04 |  | Multistart enabled GEN136 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 8 | 341979 | 04 |  | Multistart enabled GEN137 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 9 | 341979 | 04 |  | Multistart enabled GEN138 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 10 | 341979 | 04 |  | Multistart enabled GEN139 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 11 | 341979 | 04 |  | Multistart enabled GEN140 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 12 | 341979 | 04 |  | Multistart enabled GEN141 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 13 | 341979 | 04 |  | Multistart enabled GEN142 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 14 | 341979 | 04 |  | Multistart enabled GEN143 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41978 | 15 | 341979 | 04 |  | Multistart enabled GEN144 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 0 | 341980 | 04 |  | Multistart enabled GEN145 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 1 | 341980 | 04 |  | Multistart enabled GEN146 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 2 | 341980 | 04 |  | Multistart enabled GEN147 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 3 | 341980 | 04 |  | Multistart enabled GEN148 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 4 | 341980 | 04 |  | Multistart enabled GEN149 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 5 | 341980 | 04 |  | Multistart enabled GEN150 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 6 | 341980 | 04 |  | Multistart enabled GEN151 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 7 | 341980 | 04 |  | Multistart enabled GEN152 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 8 | 341980 | 04 |  | Multistart enabled GEN153 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 9 | 341980 | 04 |  | Multistart enabled GEN154 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 10 | 341980 | 04 |  | Multistart enabled GEN155 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 11 | 341980 | 04 |  | Multistart enabled GEN156 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 12 | 341980 | 04 |  | Multistart enabled GEN157 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 13 | 341980 | 04 |  | Multistart enabled GEN158 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 14 | 341980 | 04 |  | Multistart enabled GEN159 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41979 | 15 | 341980 | 04 |  | Multistart enabled GEN160 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 0 | 341981 | 04 |  | Multistart enabled GEN161 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 1 | 341981 | 04 |  | Multistart enabled GEN162 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 2 | 341981 | 04 |  | Multistart enabled GEN163 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 3 | 341981 | 04 |  | Multistart enabled GEN164 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 4 | 341981 | 04 |  | Multistart enabled GEN165 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 5 | 341981 | 04 |  | Multistart enabled GEN166 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 6 | 341981 | 04 |  | Multistart enabled GEN167 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 7 | 341981 | 04 |  | Multistart enabled GEN168 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 8 | 341981 | 04 |  | Multistart enabled GEN169 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 9 | 341981 | 04 |  | Multistart enabled GEN170 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 10 | 341981 | 04 |  | Multistart enabled GEN171 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 11 | 341981 | 04 |  | Multistart enabled GEN172 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 12 | 341981 | 04 |  | Multistart enabled GEN173 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 13 | 341981 | 04 |  | Multistart enabled GEN174 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 14 | 341981 | 04 |  | Multistart enabled GEN175 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41980 | 15 | 341981 | 04 |  | Multistart enabled GEN176 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 0 | 341982 | 04 |  | Multistart enabled GEN177 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 1 | 341982 | 04 |  | Multistart enabled GEN178 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 2 | 341982 | 04 |  | Multistart enabled GEN179 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 3 | 341982 | 04 |  | Multistart enabled GEN180 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 4 | 341982 | 04 |  | Multistart enabled GEN181 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 5 | 341982 | 04 |  | Multistart enabled GEN182 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 6 | 341982 | 04 |  | Multistart enabled GEN183 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 7 | 341982 | 04 |  | Multistart enabled GEN184 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 8 | 341982 | 04 |  | Multistart enabled GEN185 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 9 | 341982 | 04 |  | Multistart enabled GEN186 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 10 | 341982 | 04 |  | Multistart enabled GEN187 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 11 | 341982 | 04 |  | Multistart enabled GEN188 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 12 | 341982 | 04 |  | Multistart enabled GEN189 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 13 | 341982 | 04 |  | Multistart enabled GEN190 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 14 | 341982 | 04 |  | Multistart enabled GEN191 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41981 | 15 | 341982 | 04 |  | Multistart enabled GEN192 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 0 | 341983 | 04 |  | Multistart enabled GEN193 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 1 | 341983 | 04 |  | Multistart enabled GEN194 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 2 | 341983 | 04 |  | Multistart enabled GEN195 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 3 | 341983 | 04 |  | Multistart enabled GEN196 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 4 | 341983 | 04 |  | Multistart enabled GEN197 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 5 | 341983 | 04 |  | Multistart enabled GEN198 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 6 | 341983 | 04 |  | Multistart enabled GEN199 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 7 | 341983 | 04 |  | Multistart enabled GEN200 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 8 | 341983 | 04 |  | Multistart enabled GEN201 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 9 | 341983 | 04 |  | Multistart enabled GEN202 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 10 | 341983 | 04 |  | Multistart enabled GEN203 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 11 | 341983 | 04 |  | Multistart enabled GEN204 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 12 | 341983 | 04 |  | Multistart enabled GEN205 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 13 | 341983 | 04 |  | Multistart enabled GEN206 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 14 | 341983 | 04 |  | Multistart enabled GEN207 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41982 | 15 | 341983 | 04 |  | Multistart enabled GEN208 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 0 | 341984 | 04 |  | Multistart enabled GEN209 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 1 | 341984 | 04 |  | Multistart enabled GEN210 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 2 | 341984 | 04 |  | Multistart enabled GEN211 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 3 | 341984 | 04 |  | Multistart enabled GEN212 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 4 | 341984 | 04 |  | Multistart enabled GEN213 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 5 | 341984 | 04 |  | Multistart enabled GEN214 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 6 | 341984 | 04 |  | Multistart enabled GEN215 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 7 | 341984 | 04 |  | Multistart enabled GEN216 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 8 | 341984 | 04 |  | Multistart enabled GEN217 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 9 | 341984 | 04 |  | Multistart enabled GEN218 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 10 | 341984 | 04 |  | Multistart enabled GEN219 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 11 | 341984 | 04 |  | Multistart enabled GEN220 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 12 | 341984 | 04 |  | Multistart enabled GEN221 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 13 | 341984 | 04 |  | Multistart enabled GEN222 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 14 | 341984 | 04 |  | Multistart enabled GEN223 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41983 | 15 | 341984 | 04 |  | Multistart enabled GEN224 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 0 | 341985 | 04 |  | Multistart enabled GEN225 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 1 | 341985 | 04 |  | Multistart enabled GEN226 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 2 | 341985 | 04 |  | Multistart enabled GEN227 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 3 | 341985 | 04 |  | Multistart enabled GEN228 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 4 | 341985 | 04 |  | Multistart enabled GEN229 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 5 | 341985 | 04 |  | Multistart enabled GEN230 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 6 | 341985 | 04 |  | Multistart enabled GEN231 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 7 | 341985 | 04 |  | Multistart enabled GEN232 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 8 | 341985 | 04 |  | Multistart enabled GEN233 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 9 | 341985 | 04 |  | Multistart enabled GEN234 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 10 | 341985 | 04 |  | Multistart enabled GEN235 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 11 | 341985 | 04 |  | Multistart enabled GEN236 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 12 | 341985 | 04 |  | Multistart enabled GEN237 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 13 | 341985 | 04 |  | Multistart enabled GEN238 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 14 | 341985 | 04 |  | Multistart enabled GEN239 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41984 | 15 | 341985 | 04 |  | Multistart enabled GEN240 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 0 | 341986 | 04 |  | Multistart enabled GEN241 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 1 | 341986 | 04 |  | Multistart enabled GEN242 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 2 | 341986 | 04 |  | Multistart enabled GEN243 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 3 | 341986 | 04 |  | Multistart enabled GEN244 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 4 | 341986 | 04 |  | Multistart enabled GEN245 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 5 | 341986 | 04 |  | Multistart enabled GEN246 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 6 | 341986 | 04 |  | Multistart enabled GEN247 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 7 | 341986 | 04 |  | Multistart enabled GEN248 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 8 | 341986 | 04 |  | Multistart enabled GEN249 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 9 | 341986 | 04 |  | Multistart enabled GEN250 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 10 | 341986 | 04 |  | Multistart enabled GEN251 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 11 | 341986 | 04 |  | Multistart enabled GEN252 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 12 | 341986 | 04 |  | Multistart enabled GEN253 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 41985 | 13 | 341986 | 04 |  | Multistart enabled GEN254 (PMS lite) | BOOL | [5 empty] | X
PMS lite | 42000 |  | 342001 | 04 |  | BIT0-BIT7 Reserved ID GEN1, BIT8-BIT15 Reserved ID GEN2 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42001 |  | 342002 | 04 |  | BIT0-BIT7 Reserved ID GEN3, BIT8-BIT15 Reserved ID GEN4 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42002 |  | 342003 | 04 |  | BIT0-BIT7 Reserved ID GEN5, BIT8-BIT15 Reserved ID GEN6 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42003 |  | 342004 | 04 |  | BIT0-BIT7 Reserved ID GEN7, BIT8-BIT15 Reserved ID GEN8 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42004 |  | 342005 | 04 |  | BIT0-BIT7 Reserved ID GEN9, BIT8-BIT15 Reserved ID GEN10 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42005 |  | 342006 | 04 |  | BIT0-BIT7 Reserved ID GEN11, BIT8-BIT15 Reserved ID GEN12 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42006 |  | 342007 | 04 |  | BIT0-BIT7 Reserved ID GEN13, BIT8-BIT15 Reserved ID GEN14 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42007 |  | 342008 | 04 |  | BIT0-BIT7 Reserved ID GEN15, BIT8-BIT15 Reserved ID GEN16 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42008 |  | 342009 | 04 |  | BIT0-BIT7 Reserved ID GEN17, BIT8-BIT15 Reserved ID GEN18 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42009 |  | 342010 | 04 |  | BIT0-BIT7 Reserved ID GEN19, BIT8-BIT15 Reserved ID GEN20 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42010 |  | 342011 | 04 |  | BIT0-BIT7 Reserved ID GEN21, BIT8-BIT15 Reserved ID GEN22 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42011 |  | 342012 | 04 |  | BIT0-BIT7 Reserved ID GEN23, BIT8-BIT15 Reserved ID GEN24 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42012 |  | 342013 | 04 |  | BIT0-BIT7 Reserved ID GEN25, BIT8-BIT15 Reserved ID GEN26 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42013 |  | 342014 | 04 |  | BIT0-BIT7 Reserved ID GEN27, BIT8-BIT15 Reserved ID GEN28 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42014 |  | 342015 | 04 |  | BIT0-BIT7 Reserved ID GEN29, BIT8-BIT15 Reserved ID GEN30 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42015 |  | 342016 | 04 |  | BIT0-BIT7 Reserved ID GEN31, BIT8-BIT15 Reserved ID GEN32 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42016 |  | 342017 | 04 |  | BIT0-BIT7 Reserved ID GEN33, BIT8-BIT15 Reserved ID GEN34 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42017 |  | 342018 | 04 |  | BIT0-BIT7 Reserved ID GEN35, BIT8-BIT15 Reserved ID GEN36 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42018 |  | 342019 | 04 |  | BIT0-BIT7 Reserved ID GEN37, BIT8-BIT15 Reserved ID GEN38 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42019 |  | 342020 | 04 |  | BIT0-BIT7 Reserved ID GEN39, BIT8-BIT15 Reserved ID GEN40 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42020 |  | 342021 | 04 |  | BIT0-BIT7 Reserved ID GEN41, BIT8-BIT15 Reserved ID GEN42 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42021 |  | 342022 | 04 |  | BIT0-BIT7 Reserved ID GEN43, BIT8-BIT15 Reserved ID GEN44 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42022 |  | 342023 | 04 |  | BIT0-BIT7 Reserved ID GEN45, BIT8-BIT15 Reserved ID GEN46 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42023 |  | 342024 | 04 |  | BIT0-BIT7 Reserved ID GEN47, BIT8-BIT15 Reserved ID GEN48 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42024 |  | 342025 | 04 |  | BIT0-BIT7 Reserved ID GEN49, BIT8-BIT15 Reserved ID GEN50 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42025 |  | 342026 | 04 |  | BIT0-BIT7 Reserved ID GEN51, BIT8-BIT15 Reserved ID GEN52 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42026 |  | 342027 | 04 |  | BIT0-BIT7 Reserved ID GEN53, BIT8-BIT15 Reserved ID GEN54 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42027 |  | 342028 | 04 |  | BIT0-BIT7 Reserved ID GEN55, BIT8-BIT15 Reserved ID GEN56 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42028 |  | 342029 | 04 |  | BIT0-BIT7 Reserved ID GEN57, BIT8-BIT15 Reserved ID GEN58 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42029 |  | 342030 | 04 |  | BIT0-BIT7 Reserved ID GEN59, BIT8-BIT15 Reserved ID GEN60 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42030 |  | 342031 | 04 |  | BIT0-BIT7 Reserved ID GEN61, BIT8-BIT15 Reserved ID GEN62 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42031 |  | 342032 | 04 |  | BIT0-BIT7 Reserved ID GEN63, BIT8-BIT15 Reserved ID GEN64 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42032 |  | 342033 | 04 |  | BIT0-BIT7 Reserved ID GEN65, BIT8-BIT15 Reserved ID GEN66 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42033 |  | 342034 | 04 |  | BIT0-BIT7 Reserved ID GEN67, BIT8-BIT15 Reserved ID GEN68 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42034 |  | 342035 | 04 |  | BIT0-BIT7 Reserved ID GEN69, BIT8-BIT15 Reserved ID GEN70 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42035 |  | 342036 | 04 |  | BIT0-BIT7 Reserved ID GEN71, BIT8-BIT15 Reserved ID GEN72 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42036 |  | 342037 | 04 |  | BIT0-BIT7 Reserved ID GEN73, BIT8-BIT15 Reserved ID GEN74 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42037 |  | 342038 | 04 |  | BIT0-BIT7 Reserved ID GEN75, BIT8-BIT15 Reserved ID GEN76 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42038 |  | 342039 | 04 |  | BIT0-BIT7 Reserved ID GEN77, BIT8-BIT15 Reserved ID GEN78 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42039 |  | 342040 | 04 |  | BIT0-BIT7 Reserved ID GEN79, BIT8-BIT15 Reserved ID GEN80 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42040 |  | 342041 | 04 |  | BIT0-BIT7 Reserved ID GEN81, BIT8-BIT15 Reserved ID GEN82 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42041 |  | 342042 | 04 |  | BIT0-BIT7 Reserved ID GEN83, BIT8-BIT15 Reserved ID GEN84 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42042 |  | 342043 | 04 |  | BIT0-BIT7 Reserved ID GEN85, BIT8-BIT15 Reserved ID GEN86 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42043 |  | 342044 | 04 |  | BIT0-BIT7 Reserved ID GEN87, BIT8-BIT15 Reserved ID GEN88 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42044 |  | 342045 | 04 |  | BIT0-BIT7 Reserved ID GEN89, BIT8-BIT15 Reserved ID GEN90 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42045 |  | 342046 | 04 |  | BIT0-BIT7 Reserved ID GEN91, BIT8-BIT15 Reserved ID GEN92 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42046 |  | 342047 | 04 |  | BIT0-BIT7 Reserved ID GEN93, BIT8-BIT15 Reserved ID GEN94 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42047 |  | 342048 | 04 |  | BIT0-BIT7 Reserved ID GEN95, BIT8-BIT15 Reserved ID GEN96 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42048 |  | 342049 | 04 |  | BIT0-BIT7 Reserved ID GEN97, BIT8-BIT15 Reserved ID GEN98 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42049 |  | 342050 | 04 |  | BIT0-BIT7 Reserved ID GEN99, BIT8-BIT15 Reserved ID GEN100 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42050 |  | 342051 | 04 |  | BIT0-BIT7 Reserved ID GEN101, BIT8-BIT15 Reserved ID GEN102 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42051 |  | 342052 | 04 |  | BIT0-BIT7 Reserved ID GEN103, BIT8-BIT15 Reserved ID GEN104 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42052 |  | 342053 | 04 |  | BIT0-BIT7 Reserved ID GEN105, BIT8-BIT15 Reserved ID GEN106 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42053 |  | 342054 | 04 |  | BIT0-BIT7 Reserved ID GEN107, BIT8-BIT15 Reserved ID GEN108 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42054 |  | 342055 | 04 |  | BIT0-BIT7 Reserved ID GEN109, BIT8-BIT15 Reserved ID GEN110 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42055 |  | 342056 | 04 |  | BIT0-BIT7 Reserved ID GEN111, BIT8-BIT15 Reserved ID GEN112 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42056 |  | 342057 | 04 |  | BIT0-BIT7 Reserved ID GEN113, BIT8-BIT15 Reserved ID GEN114 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42057 |  | 342058 | 04 |  | BIT0-BIT7 Reserved ID GEN115, BIT8-BIT15 Reserved ID GEN116 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42058 |  | 342059 | 04 |  | BIT0-BIT7 Reserved ID GEN117, BIT8-BIT15 Reserved ID GEN118 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42059 |  | 342060 | 04 |  | BIT0-BIT7 Reserved ID GEN119, BIT8-BIT15 Reserved ID GEN120 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42060 |  | 342061 | 04 |  | BIT0-BIT7 Reserved ID GEN121, BIT8-BIT15 Reserved ID GEN122 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42061 |  | 342062 | 04 |  | BIT0-BIT7 Reserved ID GEN123, BIT8-BIT15 Reserved ID GEN124 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42062 |  | 342063 | 04 |  | BIT0-BIT7 Reserved ID GEN125, BIT8-BIT15 Reserved ID GEN126 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42063 |  | 342064 | 04 |  | BIT0-BIT7 Reserved ID GEN127, BIT8-BIT15 Reserved ID GEN128 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42064 |  | 342065 | 04 |  | BIT0-BIT7 Reserved ID GEN129, BIT8-BIT15 Reserved ID GEN130 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42065 |  | 342066 | 04 |  | BIT0-BIT7 Reserved ID GEN131, BIT8-BIT15 Reserved ID GEN132 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42066 |  | 342067 | 04 |  | BIT0-BIT7 Reserved ID GEN133, BIT8-BIT15 Reserved ID GEN134 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42067 |  | 342068 | 04 |  | BIT0-BIT7 Reserved ID GEN135, BIT8-BIT15 Reserved ID GEN136 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42068 |  | 342069 | 04 |  | BIT0-BIT7 Reserved ID GEN137, BIT8-BIT15 Reserved ID GEN138 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42069 |  | 342070 | 04 |  | BIT0-BIT7 Reserved ID GEN139, BIT8-BIT15 Reserved ID GEN140 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42070 |  | 342071 | 04 |  | BIT0-BIT7 Reserved ID GEN141, BIT8-BIT15 Reserved ID GEN142 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42071 |  | 342072 | 04 |  | BIT0-BIT7 Reserved ID GEN143, BIT8-BIT15 Reserved ID GEN144 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42072 |  | 342073 | 04 |  | BIT0-BIT7 Reserved ID GEN145, BIT8-BIT15 Reserved ID GEN146 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42073 |  | 342074 | 04 |  | BIT0-BIT7 Reserved ID GEN147, BIT8-BIT15 Reserved ID GEN148 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42074 |  | 342075 | 04 |  | BIT0-BIT7 Reserved ID GEN149, BIT8-BIT15 Reserved ID GEN150 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42075 |  | 342076 | 04 |  | BIT0-BIT7 Reserved ID GEN151, BIT8-BIT15 Reserved ID GEN152 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42076 |  | 342077 | 04 |  | BIT0-BIT7 Reserved ID GEN153, BIT8-BIT15 Reserved ID GEN154 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42077 |  | 342078 | 04 |  | BIT0-BIT7 Reserved ID GEN155, BIT8-BIT15 Reserved ID GEN156 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42078 |  | 342079 | 04 |  | BIT0-BIT7 Reserved ID GEN157, BIT8-BIT15 Reserved ID GEN158 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42079 |  | 342080 | 04 |  | BIT0-BIT7 Reserved ID GEN159, BIT8-BIT15 Reserved ID GEN160 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42080 |  | 342081 | 04 |  | BIT0-BIT7 Reserved ID GEN161, BIT8-BIT15 Reserved ID GEN162 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42081 |  | 342082 | 04 |  | BIT0-BIT7 Reserved ID GEN163, BIT8-BIT15 Reserved ID GEN164 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42082 |  | 342083 | 04 |  | BIT0-BIT7 Reserved ID GEN165, BIT8-BIT15 Reserved ID GEN166 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42083 |  | 342084 | 04 |  | BIT0-BIT7 Reserved ID GEN167, BIT8-BIT15 Reserved ID GEN168 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42084 |  | 342085 | 04 |  | BIT0-BIT7 Reserved ID GEN169, BIT8-BIT15 Reserved ID GEN170 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42085 |  | 342086 | 04 |  | BIT0-BIT7 Reserved ID GEN171, BIT8-BIT15 Reserved ID GEN172 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42086 |  | 342087 | 04 |  | BIT0-BIT7 Reserved ID GEN173, BIT8-BIT15 Reserved ID GEN174 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42087 |  | 342088 | 04 |  | BIT0-BIT7 Reserved ID GEN175, BIT8-BIT15 Reserved ID GEN176 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42088 |  | 342089 | 04 |  | BIT0-BIT7 Reserved ID GEN177, BIT8-BIT15 Reserved ID GEN178 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42089 |  | 342090 | 04 |  | BIT0-BIT7 Reserved ID GEN179, BIT8-BIT15 Reserved ID GEN180 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42090 |  | 342091 | 04 |  | BIT0-BIT7 Reserved ID GEN181, BIT8-BIT15 Reserved ID GEN182 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42091 |  | 342092 | 04 |  | BIT0-BIT7 Reserved ID GEN183, BIT8-BIT15 Reserved ID GEN184 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42092 |  | 342093 | 04 |  | BIT0-BIT7 Reserved ID GEN185, BIT8-BIT15 Reserved ID GEN186 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42093 |  | 342094 | 04 |  | BIT0-BIT7 Reserved ID GEN187, BIT8-BIT15 Reserved ID GEN188 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42094 |  | 342095 | 04 |  | BIT0-BIT7 Reserved ID GEN189, BIT8-BIT15 Reserved ID GEN190 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42095 |  | 342096 | 04 |  | BIT0-BIT7 Reserved ID GEN191, BIT8-BIT15 Reserved ID GEN192 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42096 |  | 342097 | 04 |  | BIT0-BIT7 Reserved ID GEN193, BIT8-BIT15 Reserved ID GEN194 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42097 |  | 342098 | 04 |  | BIT0-BIT7 Reserved ID GEN195, BIT8-BIT15 Reserved ID GEN196 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42098 |  | 342099 | 04 |  | BIT0-BIT7 Reserved ID GEN197, BIT8-BIT15 Reserved ID GEN198 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42099 |  | 342100 | 04 |  | BIT0-BIT7 Reserved ID GEN199, BIT8-BIT15 Reserved ID GEN200 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42100 |  | 342101 | 04 |  | BIT0-BIT7 Reserved ID GEN201, BIT8-BIT15 Reserved ID GEN202 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42101 |  | 342102 | 04 |  | BIT0-BIT7 Reserved ID GEN203, BIT8-BIT15 Reserved ID GEN204 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42102 |  | 342103 | 04 |  | BIT0-BIT7 Reserved ID GEN205, BIT8-BIT15 Reserved ID GEN206 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42103 |  | 342104 | 04 |  | BIT0-BIT7 Reserved ID GEN207, BIT8-BIT15 Reserved ID GEN208 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42104 |  | 342105 | 04 |  | BIT0-BIT7 Reserved ID GEN209, BIT8-BIT15 Reserved ID GEN210 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42105 |  | 342106 | 04 |  | BIT0-BIT7 Reserved ID GEN211, BIT8-BIT15 Reserved ID GEN212 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42106 |  | 342107 | 04 |  | BIT0-BIT7 Reserved ID GEN213, BIT8-BIT15 Reserved ID GEN214 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42107 |  | 342108 | 04 |  | BIT0-BIT7 Reserved ID GEN215, BIT8-BIT15 Reserved ID GEN216 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42108 |  | 342109 | 04 |  | BIT0-BIT7 Reserved ID GEN217, BIT8-BIT15 Reserved ID GEN218 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42109 |  | 342110 | 04 |  | BIT0-BIT7 Reserved ID GEN219, BIT8-BIT15 Reserved ID GEN220 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42110 |  | 342111 | 04 |  | BIT0-BIT7 Reserved ID GEN221, BIT8-BIT15 Reserved ID GEN222 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42111 |  | 342112 | 04 |  | BIT0-BIT7 Reserved ID GEN223, BIT8-BIT15 Reserved ID GEN224 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42112 |  | 342113 | 04 |  | BIT0-BIT7 Reserved ID GEN225, BIT8-BIT15 Reserved ID GEN226 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42113 |  | 342114 | 04 |  | BIT0-BIT7 Reserved ID GEN227, BIT8-BIT15 Reserved ID GEN228 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42114 |  | 342115 | 04 |  | BIT0-BIT7 Reserved ID GEN229, BIT8-BIT15 Reserved ID GEN230 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42115 |  | 342116 | 04 |  | BIT0-BIT7 Reserved ID GEN231, BIT8-BIT15 Reserved ID GEN232 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42116 |  | 342117 | 04 |  | BIT0-BIT7 Reserved ID GEN233, BIT8-BIT15 Reserved ID GEN234 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42117 |  | 342118 | 04 |  | BIT0-BIT7 Reserved ID GEN235, BIT8-BIT15 Reserved ID GEN236 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42118 |  | 342119 | 04 |  | BIT0-BIT7 Reserved ID GEN237, BIT8-BIT15 Reserved ID GEN238 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42119 |  | 342120 | 04 |  | BIT0-BIT7 Reserved ID GEN239, BIT8-BIT15 Reserved ID GEN240 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42120 |  | 342121 | 04 |  | BIT0-BIT7 Reserved ID GEN241, BIT8-BIT15 Reserved ID GEN242 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42121 |  | 342122 | 04 |  | BIT0-BIT7 Reserved ID GEN243, BIT8-BIT15 Reserved ID GEN244 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42122 |  | 342123 | 04 |  | BIT0-BIT7 Reserved ID GEN245, BIT8-BIT15 Reserved ID GEN246 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42123 |  | 342124 | 04 |  | BIT0-BIT7 Reserved ID GEN247, BIT8-BIT15 Reserved ID GEN248 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42124 |  | 342125 | 04 |  | BIT0-BIT7 Reserved ID GEN249, BIT8-BIT15 Reserved ID GEN250 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42125 |  | 342126 | 04 |  | BIT0-BIT7 Reserved ID GEN251, BIT8-BIT15 Reserved ID GEN252 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42126 |  | 342127 | 04 |  | BIT0-BIT7 Reserved ID GEN253, BIT8-BIT15 Reserved ID GEN254 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42159 |  | 342160 | 04 |  | BIT0-BIT7 Priority GEN1, BIT8-BIT15 Priority GEN2 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42160 |  | 342161 | 04 |  | BIT0-BIT7 Priority GEN3, BIT8-BIT15 Priority GEN4 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42161 |  | 342162 | 04 |  | BIT0-BIT7 Priority GEN5, BIT8-BIT15 Priority GEN6 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42162 |  | 342163 | 04 |  | BIT0-BIT7 Priority GEN7, BIT8-BIT15 Priority GEN8 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42163 |  | 342164 | 04 |  | BIT0-BIT7 Priority GEN9, BIT8-BIT15 Priority GEN10 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42164 |  | 342165 | 04 |  | BIT0-BIT7 Priority GEN11, BIT8-BIT15 Priority GEN12 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42165 |  | 342166 | 04 |  | BIT0-BIT7 Priority GEN13, BIT8-BIT15 Priority GEN14 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42166 |  | 342167 | 04 |  | BIT0-BIT7 Priority GEN15, BIT8-BIT15 Priority GEN16 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42167 |  | 342168 | 04 |  | BIT0-BIT7 Priority GEN17, BIT8-BIT15 Priority GEN18 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42168 |  | 342169 | 04 |  | BIT0-BIT7 Priority GEN19, BIT8-BIT15 Priority GEN20 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42169 |  | 342170 | 04 |  | BIT0-BIT7 Priority GEN21, BIT8-BIT15 Priority GEN22 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42170 |  | 342171 | 04 |  | BIT0-BIT7 Priority GEN23, BIT8-BIT15 Priority GEN24 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42171 |  | 342172 | 04 |  | BIT0-BIT7 Priority GEN25, BIT8-BIT15 Priority GEN26 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42172 |  | 342173 | 04 |  | BIT0-BIT7 Priority GEN27, BIT8-BIT15 Priority GEN28 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42173 |  | 342174 | 04 |  | BIT0-BIT7 Priority GEN29, BIT8-BIT15 Priority GEN30 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42174 |  | 342175 | 04 |  | BIT0-BIT7 Priority GEN31, BIT8-BIT15 Priority GEN32 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42175 |  | 342176 | 04 |  | BIT0-BIT7 Priority GEN33, BIT8-BIT15 Priority GEN34 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42176 |  | 342177 | 04 |  | BIT0-BIT7 Priority GEN35, BIT8-BIT15 Priority GEN36 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42177 |  | 342178 | 04 |  | BIT0-BIT7 Priority GEN37, BIT8-BIT15 Priority GEN38 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42178 |  | 342179 | 04 |  | BIT0-BIT7 Priority GEN39, BIT8-BIT15 Priority GEN40 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42179 |  | 342180 | 04 |  | BIT0-BIT7 Priority GEN41, BIT8-BIT15 Priority GEN42 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42180 |  | 342181 | 04 |  | BIT0-BIT7 Priority GEN43, BIT8-BIT15 Priority GEN44 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42181 |  | 342182 | 04 |  | BIT0-BIT7 Priority GEN45, BIT8-BIT15 Priority GEN46 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42182 |  | 342183 | 04 |  | BIT0-BIT7 Priority GEN47, BIT8-BIT15 Priority GEN48 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42183 |  | 342184 | 04 |  | BIT0-BIT7 Priority GEN49, BIT8-BIT15 Priority GEN50 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42184 |  | 342185 | 04 |  | BIT0-BIT7 Priority GEN51, BIT8-BIT15 Priority GEN52 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42185 |  | 342186 | 04 |  | BIT0-BIT7 Priority GEN53, BIT8-BIT15 Priority GEN54 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42186 |  | 342187 | 04 |  | BIT0-BIT7 Priority GEN55, BIT8-BIT15 Priority GEN56 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42187 |  | 342188 | 04 |  | BIT0-BIT7 Priority GEN57, BIT8-BIT15 Priority GEN58 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42188 |  | 342189 | 04 |  | BIT0-BIT7 Priority GEN59, BIT8-BIT15 Priority GEN60 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42189 |  | 342190 | 04 |  | BIT0-BIT7 Priority GEN61, BIT8-BIT15 Priority GEN62 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42190 |  | 342191 | 04 |  | BIT0-BIT7 Priority GEN63, BIT8-BIT15 Priority GEN64 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42191 |  | 342192 | 04 |  | BIT0-BIT7 Priority GEN65, BIT8-BIT15 Priority GEN66 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42192 |  | 342193 | 04 |  | BIT0-BIT7 Priority GEN67, BIT8-BIT15 Priority GEN68 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42193 |  | 342194 | 04 |  | BIT0-BIT7 Priority GEN69, BIT8-BIT15 Priority GEN70 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42194 |  | 342195 | 04 |  | BIT0-BIT7 Priority GEN71, BIT8-BIT15 Priority GEN72 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42195 |  | 342196 | 04 |  | BIT0-BIT7 Priority GEN73, BIT8-BIT15 Priority GEN74 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42196 |  | 342197 | 04 |  | BIT0-BIT7 Priority GEN75, BIT8-BIT15 Priority GEN76 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42197 |  | 342198 | 04 |  | BIT0-BIT7 Priority GEN77, BIT8-BIT15 Priority GEN78 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42198 |  | 342199 | 04 |  | BIT0-BIT7 Priority GEN79, BIT8-BIT15 Priority GEN80 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42199 |  | 342200 | 04 |  | BIT0-BIT7 Priority GEN81, BIT8-BIT15 Priority GEN82 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42200 |  | 342201 | 04 |  | BIT0-BIT7 Priority GEN83, BIT8-BIT15 Priority GEN84 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42201 |  | 342202 | 04 |  | BIT0-BIT7 Priority GEN85, BIT8-BIT15 Priority GEN86 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42202 |  | 342203 | 04 |  | BIT0-BIT7 Priority GEN87, BIT8-BIT15 Priority GEN88 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42203 |  | 342204 | 04 |  | BIT0-BIT7 Priority GEN89, BIT8-BIT15 Priority GEN90 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42204 |  | 342205 | 04 |  | BIT0-BIT7 Priority GEN91, BIT8-BIT15 Priority GEN92 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42205 |  | 342206 | 04 |  | BIT0-BIT7 Priority GEN93, BIT8-BIT15 Priority GEN94 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42206 |  | 342207 | 04 |  | BIT0-BIT7 Priority GEN95, BIT8-BIT15 Priority GEN96 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42207 |  | 342208 | 04 |  | BIT0-BIT7 Priority GEN97, BIT8-BIT15 Priority GEN98 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42208 |  | 342209 | 04 |  | BIT0-BIT7 Priority GEN99, BIT8-BIT15 Priority GEN100 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42209 |  | 342210 | 04 |  | BIT0-BIT7 Priority GEN101, BIT8-BIT15 Priority GEN102 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42210 |  | 342211 | 04 |  | BIT0-BIT7 Priority GEN103, BIT8-BIT15 Priority GEN104 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42211 |  | 342212 | 04 |  | BIT0-BIT7 Priority GEN105, BIT8-BIT15 Priority GEN106 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42212 |  | 342213 | 04 |  | BIT0-BIT7 Priority GEN107, BIT8-BIT15 Priority GEN108 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42213 |  | 342214 | 04 |  | BIT0-BIT7 Priority GEN109, BIT8-BIT15 Priority GEN110 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42214 |  | 342215 | 04 |  | BIT0-BIT7 Priority GEN111, BIT8-BIT15 Priority GEN112 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42215 |  | 342216 | 04 |  | BIT0-BIT7 Priority GEN113, BIT8-BIT15 Priority GEN114 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42216 |  | 342217 | 04 |  | BIT0-BIT7 Priority GEN115, BIT8-BIT15 Priority GEN116 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42217 |  | 342218 | 04 |  | BIT0-BIT7 Priority GEN117, BIT8-BIT15 Priority GEN118 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42218 |  | 342219 | 04 |  | BIT0-BIT7 Priority GEN119, BIT8-BIT15 Priority GEN120 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42219 |  | 342220 | 04 |  | BIT0-BIT7 Priority GEN121, BIT8-BIT15 Priority GEN122 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42220 |  | 342221 | 04 |  | BIT0-BIT7 Priority GEN123, BIT8-BIT15 Priority GEN124 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42221 |  | 342222 | 04 |  | BIT0-BIT7 Priority GEN125, BIT8-BIT15 Priority GEN126 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42222 |  | 342223 | 04 |  | BIT0-BIT7 Priority GEN127, BIT8-BIT15 Priority GEN128 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42223 |  | 342224 | 04 |  | BIT0-BIT7 Priority GEN129, BIT8-BIT15 Priority GEN130 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42224 |  | 342225 | 04 |  | BIT0-BIT7 Priority GEN131, BIT8-BIT15 Priority GEN132 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42225 |  | 342226 | 04 |  | BIT0-BIT7 Priority GEN133, BIT8-BIT15 Priority GEN134 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42226 |  | 342227 | 04 |  | BIT0-BIT7 Priority GEN135, BIT8-BIT15 Priority GEN136 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42227 |  | 342228 | 04 |  | BIT0-BIT7 Priority GEN137, BIT8-BIT15 Priority GEN138 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42228 |  | 342229 | 04 |  | BIT0-BIT7 Priority GEN139, BIT8-BIT15 Priority GEN140 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42229 |  | 342230 | 04 |  | BIT0-BIT7 Priority GEN141, BIT8-BIT15 Priority GEN142 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42230 |  | 342231 | 04 |  | BIT0-BIT7 Priority GEN143, BIT8-BIT15 Priority GEN144 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42231 |  | 342232 | 04 |  | BIT0-BIT7 Priority GEN145, BIT8-BIT15 Priority GEN146 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42232 |  | 342233 | 04 |  | BIT0-BIT7 Priority GEN147, BIT8-BIT15 Priority GEN148 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42233 |  | 342234 | 04 |  | BIT0-BIT7 Priority GEN149, BIT8-BIT15 Priority GEN150 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42234 |  | 342235 | 04 |  | BIT0-BIT7 Priority GEN151, BIT8-BIT15 Priority GEN152 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42235 |  | 342236 | 04 |  | BIT0-BIT7 Priority GEN153, BIT8-BIT15 Priority GEN154 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42236 |  | 342237 | 04 |  | BIT0-BIT7 Priority GEN155, BIT8-BIT15 Priority GEN156 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42237 |  | 342238 | 04 |  | BIT0-BIT7 Priority GEN157, BIT8-BIT15 Priority GEN158 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42238 |  | 342239 | 04 |  | BIT0-BIT7 Priority GEN159, BIT8-BIT15 Priority GEN160 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42239 |  | 342240 | 04 |  | BIT0-BIT7 Priority GEN161, BIT8-BIT15 Priority GEN162 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42240 |  | 342241 | 04 |  | BIT0-BIT7 Priority GEN163, BIT8-BIT15 Priority GEN164 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42241 |  | 342242 | 04 |  | BIT0-BIT7 Priority GEN165, BIT8-BIT15 Priority GEN166 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42242 |  | 342243 | 04 |  | BIT0-BIT7 Priority GEN167, BIT8-BIT15 Priority GEN168 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42243 |  | 342244 | 04 |  | BIT0-BIT7 Priority GEN169, BIT8-BIT15 Priority GEN170 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42244 |  | 342245 | 04 |  | BIT0-BIT7 Priority GEN171, BIT8-BIT15 Priority GEN172 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42245 |  | 342246 | 04 |  | BIT0-BIT7 Priority GEN173, BIT8-BIT15 Priority GEN174 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42246 |  | 342247 | 04 |  | BIT0-BIT7 Priority GEN175, BIT8-BIT15 Priority GEN176 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42247 |  | 342248 | 04 |  | BIT0-BIT7 Priority GEN177, BIT8-BIT15 Priority GEN178 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42248 |  | 342249 | 04 |  | BIT0-BIT7 Priority GEN179, BIT8-BIT15 Priority GEN180 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42249 |  | 342250 | 04 |  | BIT0-BIT7 Priority GEN181, BIT8-BIT15 Priority GEN182 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42250 |  | 342251 | 04 |  | BIT0-BIT7 Priority GEN183, BIT8-BIT15 Priority GEN184 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42251 |  | 342252 | 04 |  | BIT0-BIT7 Priority GEN185, BIT8-BIT15 Priority GEN186 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42252 |  | 342253 | 04 |  | BIT0-BIT7 Priority GEN187, BIT8-BIT15 Priority GEN188 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42253 |  | 342254 | 04 |  | BIT0-BIT7 Priority GEN189, BIT8-BIT15 Priority GEN190 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42254 |  | 342255 | 04 |  | BIT0-BIT7 Priority GEN191, BIT8-BIT15 Priority GEN192 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42255 |  | 342256 | 04 |  | BIT0-BIT7 Priority GEN193, BIT8-BIT15 Priority GEN194 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42256 |  | 342257 | 04 |  | BIT0-BIT7 Priority GEN195, BIT8-BIT15 Priority GEN196 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42257 |  | 342258 | 04 |  | BIT0-BIT7 Priority GEN197, BIT8-BIT15 Priority GEN198 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42258 |  | 342259 | 04 |  | BIT0-BIT7 Priority GEN199, BIT8-BIT15 Priority GEN200 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42259 |  | 342260 | 04 |  | BIT0-BIT7 Priority GEN201, BIT8-BIT15 Priority GEN202 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42260 |  | 342261 | 04 |  | BIT0-BIT7 Priority GEN203, BIT8-BIT15 Priority GEN204 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42261 |  | 342262 | 04 |  | BIT0-BIT7 Priority GEN205, BIT8-BIT15 Priority GEN206 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42262 |  | 342263 | 04 |  | BIT0-BIT7 Priority GEN207, BIT8-BIT15 Priority GEN208 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42263 |  | 342264 | 04 |  | BIT0-BIT7 Priority GEN209, BIT8-BIT15 Priority GEN210 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42264 |  | 342265 | 04 |  | BIT0-BIT7 Priority GEN211, BIT8-BIT15 Priority GEN212 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42265 |  | 342266 | 04 |  | BIT0-BIT7 Priority GEN213, BIT8-BIT15 Priority GEN214 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42266 |  | 342267 | 04 |  | BIT0-BIT7 Priority GEN215, BIT8-BIT15 Priority GEN216 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42267 |  | 342268 | 04 |  | BIT0-BIT7 Priority GEN217, BIT8-BIT15 Priority GEN218 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42268 |  | 342269 | 04 |  | BIT0-BIT7 Priority GEN219, BIT8-BIT15 Priority GEN220 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42269 |  | 342270 | 04 |  | BIT0-BIT7 Priority GEN221, BIT8-BIT15 Priority GEN222 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42270 |  | 342271 | 04 |  | BIT0-BIT7 Priority GEN223, BIT8-BIT15 Priority GEN224 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42271 |  | 342272 | 04 |  | BIT0-BIT7 Priority GEN225, BIT8-BIT15 Priority GEN226 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42272 |  | 342273 | 04 |  | BIT0-BIT7 Priority GEN227, BIT8-BIT15 Priority GEN228 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42273 |  | 342274 | 04 |  | BIT0-BIT7 Priority GEN229, BIT8-BIT15 Priority GEN230 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42274 |  | 342275 | 04 |  | BIT0-BIT7 Priority GEN231, BIT8-BIT15 Priority GEN232 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42275 |  | 342276 | 04 |  | BIT0-BIT7 Priority GEN233, BIT8-BIT15 Priority GEN234 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42276 |  | 342277 | 04 |  | BIT0-BIT7 Priority GEN235, BIT8-BIT15 Priority GEN236 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42277 |  | 342278 | 04 |  | BIT0-BIT7 Priority GEN237, BIT8-BIT15 Priority GEN238 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42278 |  | 342279 | 04 |  | BIT0-BIT7 Priority GEN239, BIT8-BIT15 Priority GEN240 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42279 |  | 342280 | 04 |  | BIT0-BIT7 Priority GEN241, BIT8-BIT15 Priority GEN242 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42280 |  | 342281 | 04 |  | BIT0-BIT7 Priority GEN243, BIT8-BIT15 Priority GEN244 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42281 |  | 342282 | 04 |  | BIT0-BIT7 Priority GEN245, BIT8-BIT15 Priority GEN246 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42282 |  | 342283 | 04 |  | BIT0-BIT7 Priority GEN247, BIT8-BIT15 Priority GEN248 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42283 |  | 342284 | 04 |  | BIT0-BIT7 Priority GEN249, BIT8-BIT15 Priority GEN250 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42284 |  | 342285 | 04 |  | BIT0-BIT7 Priority GEN251, BIT8-BIT15 Priority GEN252 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42285 |  | 342286 | 04 |  | BIT0-BIT7 Priority GEN253, BIT8-BIT15 Priority GEN254 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42286 |  | 342287 | 04 |  | Active P (%) GEN1 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42287 |  | 342288 | 04 |  | Active P (%) GEN2 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42288 |  | 342289 | 04 |  | Active P (%) GEN3 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42289 |  | 342290 | 04 |  | Active P (%) GEN4 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42290 |  | 342291 | 04 |  | Active P (%) GEN5 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42291 |  | 342292 | 04 |  | Active P (%) GEN6 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42292 |  | 342293 | 04 |  | Active P (%) GEN7 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42293 |  | 342294 | 04 |  | Active P (%) GEN8 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42294 |  | 342295 | 04 |  | Active P (%) GEN9 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42295 |  | 342296 | 04 |  | Active P (%) GEN10 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42296 |  | 342297 | 04 |  | Active P (%) GEN11 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42297 |  | 342298 | 04 |  | Active P (%) GEN12 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42298 |  | 342299 | 04 |  | Active P (%) GEN13 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42299 |  | 342300 | 04 |  | Active P (%) GEN14 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42300 |  | 342301 | 04 |  | Active P (%) GEN15 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42301 |  | 342302 | 04 |  | Active P (%) GEN16 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42302 |  | 342303 | 04 |  | Active P (%) GEN17 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42303 |  | 342304 | 04 |  | Active P (%) GEN18 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42304 |  | 342305 | 04 |  | Active P (%) GEN19 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42305 |  | 342306 | 04 |  | Active P (%) GEN20 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42306 |  | 342307 | 04 |  | Active P (%) GEN21 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42307 |  | 342308 | 04 |  | Active P (%) GEN22 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42308 |  | 342309 | 04 |  | Active P (%) GEN23 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42309 |  | 342310 | 04 |  | Active P (%) GEN24 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42310 |  | 342311 | 04 |  | Active P (%) GEN25 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42311 |  | 342312 | 04 |  | Active P (%) GEN26 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42312 |  | 342313 | 04 |  | Active P (%) GEN27 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42313 |  | 342314 | 04 |  | Active P (%) GEN28 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42314 |  | 342315 | 04 |  | Active P (%) GEN29 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42315 |  | 342316 | 04 |  | Active P (%) GEN30 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42316 |  | 342317 | 04 |  | Active P (%) GEN31 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42317 |  | 342318 | 04 |  | Active P (%) GEN32 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42318 |  | 342319 | 04 |  | Active P (%) GEN33 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42319 |  | 342320 | 04 |  | Active P (%) GEN34 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42320 |  | 342321 | 04 |  | Active P (%) GEN35 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42321 |  | 342322 | 04 |  | Active P (%) GEN36 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42322 |  | 342323 | 04 |  | Active P (%) GEN37 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42323 |  | 342324 | 04 |  | Active P (%) GEN38 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42324 |  | 342325 | 04 |  | Active P (%) GEN39 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42325 |  | 342326 | 04 |  | Active P (%) GEN40 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42326 |  | 342327 | 04 |  | Active P (%) GEN41 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42327 |  | 342328 | 04 |  | Active P (%) GEN42 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42328 |  | 342329 | 04 |  | Active P (%) GEN43 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42329 |  | 342330 | 04 |  | Active P (%) GEN44 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42330 |  | 342331 | 04 |  | Active P (%) GEN45 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42331 |  | 342332 | 04 |  | Active P (%) GEN46 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42332 |  | 342333 | 04 |  | Active P (%) GEN47 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42333 |  | 342334 | 04 |  | Active P (%) GEN48 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42334 |  | 342335 | 04 |  | Active P (%) GEN49 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42335 |  | 342336 | 04 |  | Active P (%) GEN50 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42336 |  | 342337 | 04 |  | Active P (%) GEN51 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42337 |  | 342338 | 04 |  | Active P (%) GEN52 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42338 |  | 342339 | 04 |  | Active P (%) GEN53 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42339 |  | 342340 | 04 |  | Active P (%) GEN54 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42340 |  | 342341 | 04 |  | Active P (%) GEN55 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42341 |  | 342342 | 04 |  | Active P (%) GEN56 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42342 |  | 342343 | 04 |  | Active P (%) GEN57 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42343 |  | 342344 | 04 |  | Active P (%) GEN58 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42344 |  | 342345 | 04 |  | Active P (%) GEN59 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42345 |  | 342346 | 04 |  | Active P (%) GEN60 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42346 |  | 342347 | 04 |  | Active P (%) GEN61 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42347 |  | 342348 | 04 |  | Active P (%) GEN62 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42348 |  | 342349 | 04 |  | Active P (%) GEN63 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42349 |  | 342350 | 04 |  | Active P (%) GEN64 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42350 |  | 342351 | 04 |  | Active P (%) GEN65 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42351 |  | 342352 | 04 |  | Active P (%) GEN66 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42352 |  | 342353 | 04 |  | Active P (%) GEN67 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42353 |  | 342354 | 04 |  | Active P (%) GEN68 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42354 |  | 342355 | 04 |  | Active P (%) GEN69 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42355 |  | 342356 | 04 |  | Active P (%) GEN70 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42356 |  | 342357 | 04 |  | Active P (%) GEN71 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42357 |  | 342358 | 04 |  | Active P (%) GEN72 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42358 |  | 342359 | 04 |  | Active P (%) GEN73 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42359 |  | 342360 | 04 |  | Active P (%) GEN74 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42360 |  | 342361 | 04 |  | Active P (%) GEN75 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42361 |  | 342362 | 04 |  | Active P (%) GEN76 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42362 |  | 342363 | 04 |  | Active P (%) GEN77 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42363 |  | 342364 | 04 |  | Active P (%) GEN78 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42364 |  | 342365 | 04 |  | Active P (%) GEN79 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42365 |  | 342366 | 04 |  | Active P (%) GEN80 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42366 |  | 342367 | 04 |  | Active P (%) GEN81 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42367 |  | 342368 | 04 |  | Active P (%) GEN82 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42368 |  | 342369 | 04 |  | Active P (%) GEN83 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42369 |  | 342370 | 04 |  | Active P (%) GEN84 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42370 |  | 342371 | 04 |  | Active P (%) GEN85 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42371 |  | 342372 | 04 |  | Active P (%) GEN86 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42372 |  | 342373 | 04 |  | Active P (%) GEN87 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42373 |  | 342374 | 04 |  | Active P (%) GEN88 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42374 |  | 342375 | 04 |  | Active P (%) GEN89 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42375 |  | 342376 | 04 |  | Active P (%) GEN90 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42376 |  | 342377 | 04 |  | Active P (%) GEN91 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42377 |  | 342378 | 04 |  | Active P (%) GEN92 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42378 |  | 342379 | 04 |  | Active P (%) GEN93 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42379 |  | 342380 | 04 |  | Active P (%) GEN94 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42380 |  | 342381 | 04 |  | Active P (%) GEN95 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42381 |  | 342382 | 04 |  | Active P (%) GEN96 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42382 |  | 342383 | 04 |  | Active P (%) GEN97 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42383 |  | 342384 | 04 |  | Active P (%) GEN98 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42384 |  | 342385 | 04 |  | Active P (%) GEN99 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42385 |  | 342386 | 04 |  | Active P (%) GEN100 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42386 |  | 342387 | 04 |  | Active P (%) GEN101 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42387 |  | 342388 | 04 |  | Active P (%) GEN102 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42388 |  | 342389 | 04 |  | Active P (%) GEN103 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42389 |  | 342390 | 04 |  | Active P (%) GEN104 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42390 |  | 342391 | 04 |  | Active P (%) GEN105 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42391 |  | 342392 | 04 |  | Active P (%) GEN106 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42392 |  | 342393 | 04 |  | Active P (%) GEN107 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42393 |  | 342394 | 04 |  | Active P (%) GEN108 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42394 |  | 342395 | 04 |  | Active P (%) GEN109 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42395 |  | 342396 | 04 |  | Active P (%) GEN110 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42396 |  | 342397 | 04 |  | Active P (%) GEN111 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42397 |  | 342398 | 04 |  | Active P (%) GEN112 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42398 |  | 342399 | 04 |  | Active P (%) GEN113 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42399 |  | 342400 | 04 |  | Active P (%) GEN114 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42400 |  | 342401 | 04 |  | Active P (%) GEN115 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42401 |  | 342402 | 04 |  | Active P (%) GEN116 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42402 |  | 342403 | 04 |  | Active P (%) GEN117 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42403 |  | 342404 | 04 |  | Active P (%) GEN118 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42404 |  | 342405 | 04 |  | Active P (%) GEN119 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42405 |  | 342406 | 04 |  | Active P (%) GEN120 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42406 |  | 342407 | 04 |  | Active P (%) GEN121 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42407 |  | 342408 | 04 |  | Active P (%) GEN122 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42408 |  | 342409 | 04 |  | Active P (%) GEN123 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42409 |  | 342410 | 04 |  | Active P (%) GEN124 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42410 |  | 342411 | 04 |  | Active P (%) GEN125 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42411 |  | 342412 | 04 |  | Active P (%) GEN126 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42412 |  | 342413 | 04 |  | Active P (%) GEN127 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42413 |  | 342414 | 04 |  | Active P (%) GEN128 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42414 |  | 342415 | 04 |  | Active P (%) GEN129 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42415 |  | 342416 | 04 |  | Active P (%) GEN130 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42416 |  | 342417 | 04 |  | Active P (%) GEN131 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42417 |  | 342418 | 04 |  | Active P (%) GEN132 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42418 |  | 342419 | 04 |  | Active P (%) GEN133 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42419 |  | 342420 | 04 |  | Active P (%) GEN134 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42420 |  | 342421 | 04 |  | Active P (%) GEN135 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42421 |  | 342422 | 04 |  | Active P (%) GEN136 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42422 |  | 342423 | 04 |  | Active P (%) GEN137 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42423 |  | 342424 | 04 |  | Active P (%) GEN138 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42424 |  | 342425 | 04 |  | Active P (%) GEN139 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42425 |  | 342426 | 04 |  | Active P (%) GEN140 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42426 |  | 342427 | 04 |  | Active P (%) GEN141 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42427 |  | 342428 | 04 |  | Active P (%) GEN142 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42428 |  | 342429 | 04 |  | Active P (%) GEN143 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42429 |  | 342430 | 04 |  | Active P (%) GEN144 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42430 |  | 342431 | 04 |  | Active P (%) GEN145 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42431 |  | 342432 | 04 |  | Active P (%) GEN146 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42432 |  | 342433 | 04 |  | Active P (%) GEN147 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42433 |  | 342434 | 04 |  | Active P (%) GEN148 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42434 |  | 342435 | 04 |  | Active P (%) GEN149 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42435 |  | 342436 | 04 |  | Active P (%) GEN150 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42436 |  | 342437 | 04 |  | Active P (%) GEN151 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42437 |  | 342438 | 04 |  | Active P (%) GEN152 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42438 |  | 342439 | 04 |  | Active P (%) GEN153 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42439 |  | 342440 | 04 |  | Active P (%) GEN154 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42440 |  | 342441 | 04 |  | Active P (%) GEN155 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42441 |  | 342442 | 04 |  | Active P (%) GEN156 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42442 |  | 342443 | 04 |  | Active P (%) GEN157 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42443 |  | 342444 | 04 |  | Active P (%) GEN158 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42444 |  | 342445 | 04 |  | Active P (%) GEN159 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42445 |  | 342446 | 04 |  | Active P (%) GEN160 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42446 |  | 342447 | 04 |  | Active P (%) GEN161 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42447 |  | 342448 | 04 |  | Active P (%) GEN162 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42448 |  | 342449 | 04 |  | Active P (%) GEN163 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42449 |  | 342450 | 04 |  | Active P (%) GEN164 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42450 |  | 342451 | 04 |  | Active P (%) GEN165 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42451 |  | 342452 | 04 |  | Active P (%) GEN166 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42452 |  | 342453 | 04 |  | Active P (%) GEN167 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42453 |  | 342454 | 04 |  | Active P (%) GEN168 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42454 |  | 342455 | 04 |  | Active P (%) GEN169 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42455 |  | 342456 | 04 |  | Active P (%) GEN170 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42456 |  | 342457 | 04 |  | Active P (%) GEN171 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42457 |  | 342458 | 04 |  | Active P (%) GEN172 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42458 |  | 342459 | 04 |  | Active P (%) GEN173 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42459 |  | 342460 | 04 |  | Active P (%) GEN174 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42460 |  | 342461 | 04 |  | Active P (%) GEN175 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42461 |  | 342462 | 04 |  | Active P (%) GEN176 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42462 |  | 342463 | 04 |  | Active P (%) GEN177 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42463 |  | 342464 | 04 |  | Active P (%) GEN178 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42464 |  | 342465 | 04 |  | Active P (%) GEN179 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42465 |  | 342466 | 04 |  | Active P (%) GEN180 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42466 |  | 342467 | 04 |  | Active P (%) GEN181 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42467 |  | 342468 | 04 |  | Active P (%) GEN182 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42468 |  | 342469 | 04 |  | Active P (%) GEN183 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42469 |  | 342470 | 04 |  | Active P (%) GEN184 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42470 |  | 342471 | 04 |  | Active P (%) GEN185 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42471 |  | 342472 | 04 |  | Active P (%) GEN186 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42472 |  | 342473 | 04 |  | Active P (%) GEN187 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42473 |  | 342474 | 04 |  | Active P (%) GEN188 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42474 |  | 342475 | 04 |  | Active P (%) GEN189 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42475 |  | 342476 | 04 |  | Active P (%) GEN190 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42476 |  | 342477 | 04 |  | Active P (%) GEN191 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42477 |  | 342478 | 04 |  | Active P (%) GEN192 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42478 |  | 342479 | 04 |  | Active P (%) GEN193 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42479 |  | 342480 | 04 |  | Active P (%) GEN194 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42480 |  | 342481 | 04 |  | Active P (%) GEN195 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42481 |  | 342482 | 04 |  | Active P (%) GEN196 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42482 |  | 342483 | 04 |  | Active P (%) GEN197 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42483 |  | 342484 | 04 |  | Active P (%) GEN198 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42484 |  | 342485 | 04 |  | Active P (%) GEN199 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42485 |  | 342486 | 04 |  | Active P (%) GEN200 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42486 |  | 342487 | 04 |  | Active P (%) GEN201 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42487 |  | 342488 | 04 |  | Active P (%) GEN202 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42488 |  | 342489 | 04 |  | Active P (%) GEN203 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42489 |  | 342490 | 04 |  | Active P (%) GEN204 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42490 |  | 342491 | 04 |  | Active P (%) GEN205 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42491 |  | 342492 | 04 |  | Active P (%) GEN206 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42492 |  | 342493 | 04 |  | Active P (%) GEN207 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42493 |  | 342494 | 04 |  | Active P (%) GEN208 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42494 |  | 342495 | 04 |  | Active P (%) GEN209 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42495 |  | 342496 | 04 |  | Active P (%) GEN210 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42496 |  | 342497 | 04 |  | Active P (%) GEN211 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42497 |  | 342498 | 04 |  | Active P (%) GEN212 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42498 |  | 342499 | 04 |  | Active P (%) GEN213 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42499 |  | 342500 | 04 |  | Active P (%) GEN214 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42500 |  | 342501 | 04 |  | Active P (%) GEN215 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42501 |  | 342502 | 04 |  | Active P (%) GEN216 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42502 |  | 342503 | 04 |  | Active P (%) GEN217 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42503 |  | 342504 | 04 |  | Active P (%) GEN218 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42504 |  | 342505 | 04 |  | Active P (%) GEN219 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42505 |  | 342506 | 04 |  | Active P (%) GEN220 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42506 |  | 342507 | 04 |  | Active P (%) GEN221 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42507 |  | 342508 | 04 |  | Active P (%) GEN222 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42508 |  | 342509 | 04 |  | Active P (%) GEN223 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42509 |  | 342510 | 04 |  | Active P (%) GEN224 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42510 |  | 342511 | 04 |  | Active P (%) GEN225 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42511 |  | 342512 | 04 |  | Active P (%) GEN226 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42512 |  | 342513 | 04 |  | Active P (%) GEN227 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42513 |  | 342514 | 04 |  | Active P (%) GEN228 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42514 |  | 342515 | 04 |  | Active P (%) GEN229 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42515 |  | 342516 | 04 |  | Active P (%) GEN230 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42516 |  | 342517 | 04 |  | Active P (%) GEN231 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42517 |  | 342518 | 04 |  | Active P (%) GEN232 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42518 |  | 342519 | 04 |  | Active P (%) GEN233 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42519 |  | 342520 | 04 |  | Active P (%) GEN234 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42520 |  | 342521 | 04 |  | Active P (%) GEN235 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42521 |  | 342522 | 04 |  | Active P (%) GEN236 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42522 |  | 342523 | 04 |  | Active P (%) GEN237 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42523 |  | 342524 | 04 |  | Active P (%) GEN238 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42524 |  | 342525 | 04 |  | Active P (%) GEN239 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42525 |  | 342526 | 04 |  | Active P (%) GEN240 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42526 |  | 342527 | 04 |  | Active P (%) GEN241 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42527 |  | 342528 | 04 |  | Active P (%) GEN242 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42528 |  | 342529 | 04 |  | Active P (%) GEN243 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42529 |  | 342530 | 04 |  | Active P (%) GEN244 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42530 |  | 342531 | 04 |  | Active P (%) GEN245 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42531 |  | 342532 | 04 |  | Active P (%) GEN246 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42532 |  | 342533 | 04 |  | Active P (%) GEN247 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42533 |  | 342534 | 04 |  | Active P (%) GEN248 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42534 |  | 342535 | 04 |  | Active P (%) GEN249 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42535 |  | 342536 | 04 |  | Active P (%) GEN250 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42536 |  | 342537 | 04 |  | Active P (%) GEN251 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42537 |  | 342538 | 04 |  | Active P (%) GEN252 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42538 |  | 342539 | 04 |  | Active P (%) GEN253 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42539 |  | 342540 | 04 |  | Active P (%) GEN254 (PMS lite) | INT16u | AB | 0 |  |  |  | X
PMS lite | 42540 |  | 342541 | 04 |  | BIT0-BIT7 DG-Mode GEN1, BIT8-BIT15 DG-Mode GEN2 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42541 |  | 342542 | 04 |  | BIT0-BIT7 DG-Mode GEN3, BIT8-BIT15 DG-Mode GEN4 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42542 |  | 342543 | 04 |  | BIT0-BIT7 DG-Mode GEN5, BIT8-BIT15 DG-Mode GEN6 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42543 |  | 342544 | 04 |  | BIT0-BIT7 DG-Mode GEN7, BIT8-BIT15 DG-Mode GEN8 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42544 |  | 342545 | 04 |  | BIT0-BIT7 DG-Mode GEN9, BIT8-BIT15 DG-Mode GEN10 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42545 |  | 342546 | 04 |  | BIT0-BIT7 DG-Mode GEN11, BIT8-BIT15 DG-Mode GEN12 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42546 |  | 342547 | 04 |  | BIT0-BIT7 DG-Mode GEN13, BIT8-BIT15 DG-Mode GEN14 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42547 |  | 342548 | 04 |  | BIT0-BIT7 DG-Mode GEN15, BIT8-BIT15 DG-Mode GEN16 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42548 |  | 342549 | 04 |  | BIT0-BIT7 DG-Mode GEN17, BIT8-BIT15 DG-Mode GEN18 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42549 |  | 342550 | 04 |  | BIT0-BIT7 DG-Mode GEN19, BIT8-BIT15 DG-Mode GEN20 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42550 |  | 342551 | 04 |  | BIT0-BIT7 DG-Mode GEN21, BIT8-BIT15 DG-Mode GEN22 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42551 |  | 342552 | 04 |  | BIT0-BIT7 DG-Mode GEN23, BIT8-BIT15 DG-Mode GEN24 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42552 |  | 342553 | 04 |  | BIT0-BIT7 DG-Mode GEN25, BIT8-BIT15 DG-Mode GEN26 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42553 |  | 342554 | 04 |  | BIT0-BIT7 DG-Mode GEN27, BIT8-BIT15 DG-Mode GEN28 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42554 |  | 342555 | 04 |  | BIT0-BIT7 DG-Mode GEN29, BIT8-BIT15 DG-Mode GEN30 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42555 |  | 342556 | 04 |  | BIT0-BIT7 DG-Mode GEN31, BIT8-BIT15 DG-Mode GEN32 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42556 |  | 342557 | 04 |  | BIT0-BIT7 DG-Mode GEN33, BIT8-BIT15 DG-Mode GEN34 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42557 |  | 342558 | 04 |  | BIT0-BIT7 DG-Mode GEN35, BIT8-BIT15 DG-Mode GEN36 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42558 |  | 342559 | 04 |  | BIT0-BIT7 DG-Mode GEN37, BIT8-BIT15 DG-Mode GEN38 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42559 |  | 342560 | 04 |  | BIT0-BIT7 DG-Mode GEN39, BIT8-BIT15 DG-Mode GEN40 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42560 |  | 342561 | 04 |  | BIT0-BIT7 DG-Mode GEN41, BIT8-BIT15 DG-Mode GEN42 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42561 |  | 342562 | 04 |  | BIT0-BIT7 DG-Mode GEN43, BIT8-BIT15 DG-Mode GEN44 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42562 |  | 342563 | 04 |  | BIT0-BIT7 DG-Mode GEN45, BIT8-BIT15 DG-Mode GEN46 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42563 |  | 342564 | 04 |  | BIT0-BIT7 DG-Mode GEN47, BIT8-BIT15 DG-Mode GEN48 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42564 |  | 342565 | 04 |  | BIT0-BIT7 DG-Mode GEN49, BIT8-BIT15 DG-Mode GEN50 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42565 |  | 342566 | 04 |  | BIT0-BIT7 DG-Mode GEN51, BIT8-BIT15 DG-Mode GEN52 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42566 |  | 342567 | 04 |  | BIT0-BIT7 DG-Mode GEN53, BIT8-BIT15 DG-Mode GEN54 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42567 |  | 342568 | 04 |  | BIT0-BIT7 DG-Mode GEN55, BIT8-BIT15 DG-Mode GEN56 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42568 |  | 342569 | 04 |  | BIT0-BIT7 DG-Mode GEN57, BIT8-BIT15 DG-Mode GEN58 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42569 |  | 342570 | 04 |  | BIT0-BIT7 DG-Mode GEN59, BIT8-BIT15 DG-Mode GEN60 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42570 |  | 342571 | 04 |  | BIT0-BIT7 DG-Mode GEN61, BIT8-BIT15 DG-Mode GEN62 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42571 |  | 342572 | 04 |  | BIT0-BIT7 DG-Mode GEN63, BIT8-BIT15 DG-Mode GEN64 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42572 |  | 342573 | 04 |  | BIT0-BIT7 DG-Mode GEN65, BIT8-BIT15 DG-Mode GEN66 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42573 |  | 342574 | 04 |  | BIT0-BIT7 DG-Mode GEN67, BIT8-BIT15 DG-Mode GEN68 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42574 |  | 342575 | 04 |  | BIT0-BIT7 DG-Mode GEN69, BIT8-BIT15 DG-Mode GEN70 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42575 |  | 342576 | 04 |  | BIT0-BIT7 DG-Mode GEN71, BIT8-BIT15 DG-Mode GEN72 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42576 |  | 342577 | 04 |  | BIT0-BIT7 DG-Mode GEN73, BIT8-BIT15 DG-Mode GEN74 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42577 |  | 342578 | 04 |  | BIT0-BIT7 DG-Mode GEN75, BIT8-BIT15 DG-Mode GEN76 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42578 |  | 342579 | 04 |  | BIT0-BIT7 DG-Mode GEN77, BIT8-BIT15 DG-Mode GEN78 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42579 |  | 342580 | 04 |  | BIT0-BIT7 DG-Mode GEN79, BIT8-BIT15 DG-Mode GEN80 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42580 |  | 342581 | 04 |  | BIT0-BIT7 DG-Mode GEN81, BIT8-BIT15 DG-Mode GEN82 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42581 |  | 342582 | 04 |  | BIT0-BIT7 DG-Mode GEN83, BIT8-BIT15 DG-Mode GEN84 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42582 |  | 342583 | 04 |  | BIT0-BIT7 DG-Mode GEN85, BIT8-BIT15 DG-Mode GEN86 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42583 |  | 342584 | 04 |  | BIT0-BIT7 DG-Mode GEN87, BIT8-BIT15 DG-Mode GEN88 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42584 |  | 342585 | 04 |  | BIT0-BIT7 DG-Mode GEN89, BIT8-BIT15 DG-Mode GEN90 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42585 |  | 342586 | 04 |  | BIT0-BIT7 DG-Mode GEN91, BIT8-BIT15 DG-Mode GEN92 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42586 |  | 342587 | 04 |  | BIT0-BIT7 DG-Mode GEN93, BIT8-BIT15 DG-Mode GEN94 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42587 |  | 342588 | 04 |  | BIT0-BIT7 DG-Mode GEN95, BIT8-BIT15 DG-Mode GEN96 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42588 |  | 342589 | 04 |  | BIT0-BIT7 DG-Mode GEN97, BIT8-BIT15 DG-Mode GEN98 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42589 |  | 342590 | 04 |  | BIT0-BIT7 DG-Mode GEN99, BIT8-BIT15 DG-Mode GEN100 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42590 |  | 342591 | 04 |  | BIT0-BIT7 DG-Mode GEN101, BIT8-BIT15 DG-Mode GEN102 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42591 |  | 342592 | 04 |  | BIT0-BIT7 DG-Mode GEN103, BIT8-BIT15 DG-Mode GEN104 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42592 |  | 342593 | 04 |  | BIT0-BIT7 DG-Mode GEN105, BIT8-BIT15 DG-Mode GEN106 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42593 |  | 342594 | 04 |  | BIT0-BIT7 DG-Mode GEN107, BIT8-BIT15 DG-Mode GEN108 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42594 |  | 342595 | 04 |  | BIT0-BIT7 DG-Mode GEN109, BIT8-BIT15 DG-Mode GEN110 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42595 |  | 342596 | 04 |  | BIT0-BIT7 DG-Mode GEN111, BIT8-BIT15 DG-Mode GEN112 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42596 |  | 342597 | 04 |  | BIT0-BIT7 DG-Mode GEN113, BIT8-BIT15 DG-Mode GEN114 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42597 |  | 342598 | 04 |  | BIT0-BIT7 DG-Mode GEN115, BIT8-BIT15 DG-Mode GEN116 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42598 |  | 342599 | 04 |  | BIT0-BIT7 DG-Mode GEN117, BIT8-BIT15 DG-Mode GEN118 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42599 |  | 342600 | 04 |  | BIT0-BIT7 DG-Mode GEN119, BIT8-BIT15 DG-Mode GEN120 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42600 |  | 342601 | 04 |  | BIT0-BIT7 DG-Mode GEN121, BIT8-BIT15 DG-Mode GEN122 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42601 |  | 342602 | 04 |  | BIT0-BIT7 DG-Mode GEN123, BIT8-BIT15 DG-Mode GEN124 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42602 |  | 342603 | 04 |  | BIT0-BIT7 DG-Mode GEN125, BIT8-BIT15 DG-Mode GEN126 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42603 |  | 342604 | 04 |  | BIT0-BIT7 DG-Mode GEN127, BIT8-BIT15 DG-Mode GEN128 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42604 |  | 342605 | 04 |  | BIT0-BIT7 DG-Mode GEN129, BIT8-BIT15 DG-Mode GEN130 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42605 |  | 342606 | 04 |  | BIT0-BIT7 DG-Mode GEN131, BIT8-BIT15 DG-Mode GEN132 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42606 |  | 342607 | 04 |  | BIT0-BIT7 DG-Mode GEN133, BIT8-BIT15 DG-Mode GEN134 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42607 |  | 342608 | 04 |  | BIT0-BIT7 DG-Mode GEN135, BIT8-BIT15 DG-Mode GEN136 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42608 |  | 342609 | 04 |  | BIT0-BIT7 DG-Mode GEN137, BIT8-BIT15 DG-Mode GEN138 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42609 |  | 342610 | 04 |  | BIT0-BIT7 DG-Mode GEN139, BIT8-BIT15 DG-Mode GEN140 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42610 |  | 342611 | 04 |  | BIT0-BIT7 DG-Mode GEN141, BIT8-BIT15 DG-Mode GEN142 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42611 |  | 342612 | 04 |  | BIT0-BIT7 DG-Mode GEN143, BIT8-BIT15 DG-Mode GEN144 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42612 |  | 342613 | 04 |  | BIT0-BIT7 DG-Mode GEN145, BIT8-BIT15 DG-Mode GEN146 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42613 |  | 342614 | 04 |  | BIT0-BIT7 DG-Mode GEN147, BIT8-BIT15 DG-Mode GEN148 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42614 |  | 342615 | 04 |  | BIT0-BIT7 DG-Mode GEN149, BIT8-BIT15 DG-Mode GEN150 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42615 |  | 342616 | 04 |  | BIT0-BIT7 DG-Mode GEN151, BIT8-BIT15 DG-Mode GEN152 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42616 |  | 342617 | 04 |  | BIT0-BIT7 DG-Mode GEN153, BIT8-BIT15 DG-Mode GEN154 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42617 |  | 342618 | 04 |  | BIT0-BIT7 DG-Mode GEN155, BIT8-BIT15 DG-Mode GEN156 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42618 |  | 342619 | 04 |  | BIT0-BIT7 DG-Mode GEN157, BIT8-BIT15 DG-Mode GEN158 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42619 |  | 342620 | 04 |  | BIT0-BIT7 DG-Mode GEN159, BIT8-BIT15 DG-Mode GEN160 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42620 |  | 342621 | 04 |  | BIT0-BIT7 DG-Mode GEN161, BIT8-BIT15 DG-Mode GEN162 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42621 |  | 342622 | 04 |  | BIT0-BIT7 DG-Mode GEN163, BIT8-BIT15 DG-Mode GEN164 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42622 |  | 342623 | 04 |  | BIT0-BIT7 DG-Mode GEN165, BIT8-BIT15 DG-Mode GEN166 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42623 |  | 342624 | 04 |  | BIT0-BIT7 DG-Mode GEN167, BIT8-BIT15 DG-Mode GEN168 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42624 |  | 342625 | 04 |  | BIT0-BIT7 DG-Mode GEN169, BIT8-BIT15 DG-Mode GEN170 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42625 |  | 342626 | 04 |  | BIT0-BIT7 DG-Mode GEN171, BIT8-BIT15 DG-Mode GEN172 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42626 |  | 342627 | 04 |  | BIT0-BIT7 DG-Mode GEN173, BIT8-BIT15 DG-Mode GEN174 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42627 |  | 342628 | 04 |  | BIT0-BIT7 DG-Mode GEN175, BIT8-BIT15 DG-Mode GEN176 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42628 |  | 342629 | 04 |  | BIT0-BIT7 DG-Mode GEN177, BIT8-BIT15 DG-Mode GEN178 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42629 |  | 342630 | 04 |  | BIT0-BIT7 DG-Mode GEN179, BIT8-BIT15 DG-Mode GEN180 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42630 |  | 342631 | 04 |  | BIT0-BIT7 DG-Mode GEN181, BIT8-BIT15 DG-Mode GEN182 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42631 |  | 342632 | 04 |  | BIT0-BIT7 DG-Mode GEN183, BIT8-BIT15 DG-Mode GEN184 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42632 |  | 342633 | 04 |  | BIT0-BIT7 DG-Mode GEN185, BIT8-BIT15 DG-Mode GEN186 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42633 |  | 342634 | 04 |  | BIT0-BIT7 DG-Mode GEN187, BIT8-BIT15 DG-Mode GEN188 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42634 |  | 342635 | 04 |  | BIT0-BIT7 DG-Mode GEN189, BIT8-BIT15 DG-Mode GEN190 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42635 |  | 342636 | 04 |  | BIT0-BIT7 DG-Mode GEN191, BIT8-BIT15 DG-Mode GEN192 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42636 |  | 342637 | 04 |  | BIT0-BIT7 DG-Mode GEN193, BIT8-BIT15 DG-Mode GEN194 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42637 |  | 342638 | 04 |  | BIT0-BIT7 DG-Mode GEN195, BIT8-BIT15 DG-Mode GEN196 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42638 |  | 342639 | 04 |  | BIT0-BIT7 DG-Mode GEN197, BIT8-BIT15 DG-Mode GEN198 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42639 |  | 342640 | 04 |  | BIT0-BIT7 DG-Mode GEN199, BIT8-BIT15 DG-Mode GEN200 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42640 |  | 342641 | 04 |  | BIT0-BIT7 DG-Mode GEN201, BIT8-BIT15 DG-Mode GEN202 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42641 |  | 342642 | 04 |  | BIT0-BIT7 DG-Mode GEN203, BIT8-BIT15 DG-Mode GEN204 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42642 |  | 342643 | 04 |  | BIT0-BIT7 DG-Mode GEN205, BIT8-BIT15 DG-Mode GEN206 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42643 |  | 342644 | 04 |  | BIT0-BIT7 DG-Mode GEN207, BIT8-BIT15 DG-Mode GEN208 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42644 |  | 342645 | 04 |  | BIT0-BIT7 DG-Mode GEN209, BIT8-BIT15 DG-Mode GEN210 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42645 |  | 342646 | 04 |  | BIT0-BIT7 DG-Mode GEN211, BIT8-BIT15 DG-Mode GEN212 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42646 |  | 342647 | 04 |  | BIT0-BIT7 DG-Mode GEN213, BIT8-BIT15 DG-Mode GEN214 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42647 |  | 342648 | 04 |  | BIT0-BIT7 DG-Mode GEN215, BIT8-BIT15 DG-Mode GEN216 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42648 |  | 342649 | 04 |  | BIT0-BIT7 DG-Mode GEN217, BIT8-BIT15 DG-Mode GEN218 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42649 |  | 342650 | 04 |  | BIT0-BIT7 DG-Mode GEN219, BIT8-BIT15 DG-Mode GEN220 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42650 |  | 342651 | 04 |  | BIT0-BIT7 DG-Mode GEN221, BIT8-BIT15 DG-Mode GEN222 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42651 |  | 342652 | 04 |  | BIT0-BIT7 DG-Mode GEN223, BIT8-BIT15 DG-Mode GEN224 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42652 |  | 342653 | 04 |  | BIT0-BIT7 DG-Mode GEN225, BIT8-BIT15 DG-Mode GEN226 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42653 |  | 342654 | 04 |  | BIT0-BIT7 DG-Mode GEN227, BIT8-BIT15 DG-Mode GEN228 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42654 |  | 342655 | 04 |  | BIT0-BIT7 DG-Mode GEN229, BIT8-BIT15 DG-Mode GEN230 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42655 |  | 342656 | 04 |  | BIT0-BIT7 DG-Mode GEN231, BIT8-BIT15 DG-Mode GEN232 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42656 |  | 342657 | 04 |  | BIT0-BIT7 DG-Mode GEN233, BIT8-BIT15 DG-Mode GEN234 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42657 |  | 342658 | 04 |  | BIT0-BIT7 DG-Mode GEN235, BIT8-BIT15 DG-Mode GEN236 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42658 |  | 342659 | 04 |  | BIT0-BIT7 DG-Mode GEN237, BIT8-BIT15 DG-Mode GEN238 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42659 |  | 342660 | 04 |  | BIT0-BIT7 DG-Mode GEN239, BIT8-BIT15 DG-Mode GEN240 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42660 |  | 342661 | 04 |  | BIT0-BIT7 DG-Mode GEN241, BIT8-BIT15 DG-Mode GEN242 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42661 |  | 342662 | 04 |  | BIT0-BIT7 DG-Mode GEN243, BIT8-BIT15 DG-Mode GEN244 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42662 |  | 342663 | 04 |  | BIT0-BIT7 DG-Mode GEN245, BIT8-BIT15 DG-Mode GEN246 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42663 |  | 342664 | 04 |  | BIT0-BIT7 DG-Mode GEN247, BIT8-BIT15 DG-Mode GEN248 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42664 |  | 342665 | 04 |  | BIT0-BIT7 DG-Mode GEN249, BIT8-BIT15 DG-Mode GEN250 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42665 |  | 342666 | 04 |  | BIT0-BIT7 DG-Mode GEN251, BIT8-BIT15 DG-Mode GEN252 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42666 |  | 342667 | 04 |  | BIT0-BIT7 DG-Mode GEN253, BIT8-BIT15 DG-Mode GEN254 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42667 |  | 342668 | 04 |  | BIT0-BIT7 DG-Status GEN1, BIT8-BIT15 DG-Status GEN2 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42668 |  | 342669 | 04 |  | BIT0-BIT7 DG-Status GEN3, BIT8-BIT15 DG-Status GEN4 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42669 |  | 342670 | 04 |  | BIT0-BIT7 DG-Status GEN5, BIT8-BIT15 DG-Status GEN6 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42670 |  | 342671 | 04 |  | BIT0-BIT7 DG-Status GEN7, BIT8-BIT15 DG-Status GEN8 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42671 |  | 342672 | 04 |  | BIT0-BIT7 DG-Status GEN9, BIT8-BIT15 DG-Status GEN10 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42672 |  | 342673 | 04 |  | BIT0-BIT7 DG-Status GEN11, BIT8-BIT15 DG-Status GEN12 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42673 |  | 342674 | 04 |  | BIT0-BIT7 DG-Status GEN13, BIT8-BIT15 DG-Status GEN14 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42674 |  | 342675 | 04 |  | BIT0-BIT7 DG-Status GEN15, BIT8-BIT15 DG-Status GEN16 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42675 |  | 342676 | 04 |  | BIT0-BIT7 DG-Status GEN17, BIT8-BIT15 DG-Status GEN18 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42676 |  | 342677 | 04 |  | BIT0-BIT7 DG-Status GEN19, BIT8-BIT15 DG-Status GEN20 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42677 |  | 342678 | 04 |  | BIT0-BIT7 DG-Status GEN21, BIT8-BIT15 DG-Status GEN22 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42678 |  | 342679 | 04 |  | BIT0-BIT7 DG-Status GEN23, BIT8-BIT15 DG-Status GEN24 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42679 |  | 342680 | 04 |  | BIT0-BIT7 DG-Status GEN25, BIT8-BIT15 DG-Status GEN26 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42680 |  | 342681 | 04 |  | BIT0-BIT7 DG-Status GEN27, BIT8-BIT15 DG-Status GEN28 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42681 |  | 342682 | 04 |  | BIT0-BIT7 DG-Status GEN29, BIT8-BIT15 DG-Status GEN30 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42682 |  | 342683 | 04 |  | BIT0-BIT7 DG-Status GEN31, BIT8-BIT15 DG-Status GEN32 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42683 |  | 342684 | 04 |  | BIT0-BIT7 DG-Status GEN33, BIT8-BIT15 DG-Status GEN34 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42684 |  | 342685 | 04 |  | BIT0-BIT7 DG-Status GEN35, BIT8-BIT15 DG-Status GEN36 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42685 |  | 342686 | 04 |  | BIT0-BIT7 DG-Status GEN37, BIT8-BIT15 DG-Status GEN38 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42686 |  | 342687 | 04 |  | BIT0-BIT7 DG-Status GEN39, BIT8-BIT15 DG-Status GEN40 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42687 |  | 342688 | 04 |  | BIT0-BIT7 DG-Status GEN41, BIT8-BIT15 DG-Status GEN42 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42688 |  | 342689 | 04 |  | BIT0-BIT7 DG-Status GEN43, BIT8-BIT15 DG-Status GEN44 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42689 |  | 342690 | 04 |  | BIT0-BIT7 DG-Status GEN45, BIT8-BIT15 DG-Status GEN46 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42690 |  | 342691 | 04 |  | BIT0-BIT7 DG-Status GEN47, BIT8-BIT15 DG-Status GEN48 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42691 |  | 342692 | 04 |  | BIT0-BIT7 DG-Status GEN49, BIT8-BIT15 DG-Status GEN50 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42692 |  | 342693 | 04 |  | BIT0-BIT7 DG-Status GEN51, BIT8-BIT15 DG-Status GEN52 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42693 |  | 342694 | 04 |  | BIT0-BIT7 DG-Status GEN53, BIT8-BIT15 DG-Status GEN54 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42694 |  | 342695 | 04 |  | BIT0-BIT7 DG-Status GEN55, BIT8-BIT15 DG-Status GEN56 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42695 |  | 342696 | 04 |  | BIT0-BIT7 DG-Status GEN57, BIT8-BIT15 DG-Status GEN58 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42696 |  | 342697 | 04 |  | BIT0-BIT7 DG-Status GEN59, BIT8-BIT15 DG-Status GEN60 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42697 |  | 342698 | 04 |  | BIT0-BIT7 DG-Status GEN61, BIT8-BIT15 DG-Status GEN62 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42698 |  | 342699 | 04 |  | BIT0-BIT7 DG-Status GEN63, BIT8-BIT15 DG-Status GEN64 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42699 |  | 342700 | 04 |  | BIT0-BIT7 DG-Status GEN65, BIT8-BIT15 DG-Status GEN66 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42700 |  | 342701 | 04 |  | BIT0-BIT7 DG-Status GEN67, BIT8-BIT15 DG-Status GEN68 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42701 |  | 342702 | 04 |  | BIT0-BIT7 DG-Status GEN69, BIT8-BIT15 DG-Status GEN70 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42702 |  | 342703 | 04 |  | BIT0-BIT7 DG-Status GEN71, BIT8-BIT15 DG-Status GEN72 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42703 |  | 342704 | 04 |  | BIT0-BIT7 DG-Status GEN73, BIT8-BIT15 DG-Status GEN74 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42704 |  | 342705 | 04 |  | BIT0-BIT7 DG-Status GEN75, BIT8-BIT15 DG-Status GEN76 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42705 |  | 342706 | 04 |  | BIT0-BIT7 DG-Status GEN77, BIT8-BIT15 DG-Status GEN78 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42706 |  | 342707 | 04 |  | BIT0-BIT7 DG-Status GEN79, BIT8-BIT15 DG-Status GEN80 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42707 |  | 342708 | 04 |  | BIT0-BIT7 DG-Status GEN81, BIT8-BIT15 DG-Status GEN82 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42708 |  | 342709 | 04 |  | BIT0-BIT7 DG-Status GEN83, BIT8-BIT15 DG-Status GEN84 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42709 |  | 342710 | 04 |  | BIT0-BIT7 DG-Status GEN85, BIT8-BIT15 DG-Status GEN86 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42710 |  | 342711 | 04 |  | BIT0-BIT7 DG-Status GEN87, BIT8-BIT15 DG-Status GEN88 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42711 |  | 342712 | 04 |  | BIT0-BIT7 DG-Status GEN89, BIT8-BIT15 DG-Status GEN90 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42712 |  | 342713 | 04 |  | BIT0-BIT7 DG-Status GEN91, BIT8-BIT15 DG-Status GEN92 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42713 |  | 342714 | 04 |  | BIT0-BIT7 DG-Status GEN93, BIT8-BIT15 DG-Status GEN94 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42714 |  | 342715 | 04 |  | BIT0-BIT7 DG-Status GEN95, BIT8-BIT15 DG-Status GEN96 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42715 |  | 342716 | 04 |  | BIT0-BIT7 DG-Status GEN97, BIT8-BIT15 DG-Status GEN98 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42716 |  | 342717 | 04 |  | BIT0-BIT7 DG-Status GEN99, BIT8-BIT15 DG-Status GEN100 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42717 |  | 342718 | 04 |  | BIT0-BIT7 DG-Status GEN101, BIT8-BIT15 DG-Status GEN102 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42718 |  | 342719 | 04 |  | BIT0-BIT7 DG-Status GEN103, BIT8-BIT15 DG-Status GEN104 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42719 |  | 342720 | 04 |  | BIT0-BIT7 DG-Status GEN105, BIT8-BIT15 DG-Status GEN106 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42720 |  | 342721 | 04 |  | BIT0-BIT7 DG-Status GEN107, BIT8-BIT15 DG-Status GEN108 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42721 |  | 342722 | 04 |  | BIT0-BIT7 DG-Status GEN109, BIT8-BIT15 DG-Status GEN110 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42722 |  | 342723 | 04 |  | BIT0-BIT7 DG-Status GEN111, BIT8-BIT15 DG-Status GEN112 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42723 |  | 342724 | 04 |  | BIT0-BIT7 DG-Status GEN113, BIT8-BIT15 DG-Status GEN114 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42724 |  | 342725 | 04 |  | BIT0-BIT7 DG-Status GEN115, BIT8-BIT15 DG-Status GEN116 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42725 |  | 342726 | 04 |  | BIT0-BIT7 DG-Status GEN117, BIT8-BIT15 DG-Status GEN118 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42726 |  | 342727 | 04 |  | BIT0-BIT7 DG-Status GEN119, BIT8-BIT15 DG-Status GEN120 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42727 |  | 342728 | 04 |  | BIT0-BIT7 DG-Status GEN121, BIT8-BIT15 DG-Status GEN122 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42728 |  | 342729 | 04 |  | BIT0-BIT7 DG-Status GEN123, BIT8-BIT15 DG-Status GEN124 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42729 |  | 342730 | 04 |  | BIT0-BIT7 DG-Status GEN125, BIT8-BIT15 DG-Status GEN126 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42730 |  | 342731 | 04 |  | BIT0-BIT7 DG-Status GEN127, BIT8-BIT15 DG-Status GEN128 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42731 |  | 342732 | 04 |  | BIT0-BIT7 DG-Status GEN129, BIT8-BIT15 DG-Status GEN130 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42732 |  | 342733 | 04 |  | BIT0-BIT7 DG-Status GEN131, BIT8-BIT15 DG-Status GEN132 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42733 |  | 342734 | 04 |  | BIT0-BIT7 DG-Status GEN133, BIT8-BIT15 DG-Status GEN134 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42734 |  | 342735 | 04 |  | BIT0-BIT7 DG-Status GEN135, BIT8-BIT15 DG-Status GEN136 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42735 |  | 342736 | 04 |  | BIT0-BIT7 DG-Status GEN137, BIT8-BIT15 DG-Status GEN138 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42736 |  | 342737 | 04 |  | BIT0-BIT7 DG-Status GEN139, BIT8-BIT15 DG-Status GEN140 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42737 |  | 342738 | 04 |  | BIT0-BIT7 DG-Status GEN141, BIT8-BIT15 DG-Status GEN142 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42738 |  | 342739 | 04 |  | BIT0-BIT7 DG-Status GEN143, BIT8-BIT15 DG-Status GEN144 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42739 |  | 342740 | 04 |  | BIT0-BIT7 DG-Status GEN145, BIT8-BIT15 DG-Status GEN146 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42740 |  | 342741 | 04 |  | BIT0-BIT7 DG-Status GEN147, BIT8-BIT15 DG-Status GEN148 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42741 |  | 342742 | 04 |  | BIT0-BIT7 DG-Status GEN149, BIT8-BIT15 DG-Status GEN150 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42742 |  | 342743 | 04 |  | BIT0-BIT7 DG-Status GEN151, BIT8-BIT15 DG-Status GEN152 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42743 |  | 342744 | 04 |  | BIT0-BIT7 DG-Status GEN153, BIT8-BIT15 DG-Status GEN154 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42744 |  | 342745 | 04 |  | BIT0-BIT7 DG-Status GEN155, BIT8-BIT15 DG-Status GEN156 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42745 |  | 342746 | 04 |  | BIT0-BIT7 DG-Status GEN157, BIT8-BIT15 DG-Status GEN158 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42746 |  | 342747 | 04 |  | BIT0-BIT7 DG-Status GEN159, BIT8-BIT15 DG-Status GEN160 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42747 |  | 342748 | 04 |  | BIT0-BIT7 DG-Status GEN161, BIT8-BIT15 DG-Status GEN162 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42748 |  | 342749 | 04 |  | BIT0-BIT7 DG-Status GEN163, BIT8-BIT15 DG-Status GEN164 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42749 |  | 342750 | 04 |  | BIT0-BIT7 DG-Status GEN165, BIT8-BIT15 DG-Status GEN166 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42750 |  | 342751 | 04 |  | BIT0-BIT7 DG-Status GEN167, BIT8-BIT15 DG-Status GEN168 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42751 |  | 342752 | 04 |  | BIT0-BIT7 DG-Status GEN169, BIT8-BIT15 DG-Status GEN170 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42752 |  | 342753 | 04 |  | BIT0-BIT7 DG-Status GEN171, BIT8-BIT15 DG-Status GEN172 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42753 |  | 342754 | 04 |  | BIT0-BIT7 DG-Status GEN173, BIT8-BIT15 DG-Status GEN174 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42754 |  | 342755 | 04 |  | BIT0-BIT7 DG-Status GEN175, BIT8-BIT15 DG-Status GEN176 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42755 |  | 342756 | 04 |  | BIT0-BIT7 DG-Status GEN177, BIT8-BIT15 DG-Status GEN178 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42756 |  | 342757 | 04 |  | BIT0-BIT7 DG-Status GEN179, BIT8-BIT15 DG-Status GEN180 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42757 |  | 342758 | 04 |  | BIT0-BIT7 DG-Status GEN181, BIT8-BIT15 DG-Status GEN182 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42758 |  | 342759 | 04 |  | BIT0-BIT7 DG-Status GEN183, BIT8-BIT15 DG-Status GEN184 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42759 |  | 342760 | 04 |  | BIT0-BIT7 DG-Status GEN185, BIT8-BIT15 DG-Status GEN186 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42760 |  | 342761 | 04 |  | BIT0-BIT7 DG-Status GEN187, BIT8-BIT15 DG-Status GEN188 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42761 |  | 342762 | 04 |  | BIT0-BIT7 DG-Status GEN189, BIT8-BIT15 DG-Status GEN190 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42762 |  | 342763 | 04 |  | BIT0-BIT7 DG-Status GEN191, BIT8-BIT15 DG-Status GEN192 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42763 |  | 342764 | 04 |  | BIT0-BIT7 DG-Status GEN193, BIT8-BIT15 DG-Status GEN194 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42764 |  | 342765 | 04 |  | BIT0-BIT7 DG-Status GEN195, BIT8-BIT15 DG-Status GEN196 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42765 |  | 342766 | 04 |  | BIT0-BIT7 DG-Status GEN197, BIT8-BIT15 DG-Status GEN198 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42766 |  | 342767 | 04 |  | BIT0-BIT7 DG-Status GEN199, BIT8-BIT15 DG-Status GEN200 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42767 |  | 342768 | 04 |  | BIT0-BIT7 DG-Status GEN201, BIT8-BIT15 DG-Status GEN202 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42768 |  | 342769 | 04 |  | BIT0-BIT7 DG-Status GEN203, BIT8-BIT15 DG-Status GEN204 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42769 |  | 342770 | 04 |  | BIT0-BIT7 DG-Status GEN205, BIT8-BIT15 DG-Status GEN206 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42770 |  | 342771 | 04 |  | BIT0-BIT7 DG-Status GEN207, BIT8-BIT15 DG-Status GEN208 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42771 |  | 342772 | 04 |  | BIT0-BIT7 DG-Status GEN209, BIT8-BIT15 DG-Status GEN210 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42772 |  | 342773 | 04 |  | BIT0-BIT7 DG-Status GEN211, BIT8-BIT15 DG-Status GEN212 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42773 |  | 342774 | 04 |  | BIT0-BIT7 DG-Status GEN213, BIT8-BIT15 DG-Status GEN214 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42774 |  | 342775 | 04 |  | BIT0-BIT7 DG-Status GEN215, BIT8-BIT15 DG-Status GEN216 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42775 |  | 342776 | 04 |  | BIT0-BIT7 DG-Status GEN217, BIT8-BIT15 DG-Status GEN218 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42776 |  | 342777 | 04 |  | BIT0-BIT7 DG-Status GEN219, BIT8-BIT15 DG-Status GEN220 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42777 |  | 342778 | 04 |  | BIT0-BIT7 DG-Status GEN221, BIT8-BIT15 DG-Status GEN222 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42778 |  | 342779 | 04 |  | BIT0-BIT7 DG-Status GEN223, BIT8-BIT15 DG-Status GEN224 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42779 |  | 342780 | 04 |  | BIT0-BIT7 DG-Status GEN225, BIT8-BIT15 DG-Status GEN226 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42780 |  | 342781 | 04 |  | BIT0-BIT7 DG-Status GEN227, BIT8-BIT15 DG-Status GEN228 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42781 |  | 342782 | 04 |  | BIT0-BIT7 DG-Status GEN229, BIT8-BIT15 DG-Status GEN230 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42782 |  | 342783 | 04 |  | BIT0-BIT7 DG-Status GEN231, BIT8-BIT15 DG-Status GEN232 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42783 |  | 342784 | 04 |  | BIT0-BIT7 DG-Status GEN233, BIT8-BIT15 DG-Status GEN234 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42784 |  | 342785 | 04 |  | BIT0-BIT7 DG-Status GEN235, BIT8-BIT15 DG-Status GEN236 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42785 |  | 342786 | 04 |  | BIT0-BIT7 DG-Status GEN237, BIT8-BIT15 DG-Status GEN238 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42786 |  | 342787 | 04 |  | BIT0-BIT7 DG-Status GEN239, BIT8-BIT15 DG-Status GEN240 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42787 |  | 342788 | 04 |  | BIT0-BIT7 DG-Status GEN241, BIT8-BIT15 DG-Status GEN242 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42788 |  | 342789 | 04 |  | BIT0-BIT7 DG-Status GEN243, BIT8-BIT15 DG-Status GEN244 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42789 |  | 342790 | 04 |  | BIT0-BIT7 DG-Status GEN245, BIT8-BIT15 DG-Status GEN246 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42790 |  | 342791 | 04 |  | BIT0-BIT7 DG-Status GEN247, BIT8-BIT15 DG-Status GEN248 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42791 |  | 342792 | 04 |  | BIT0-BIT7 DG-Status GEN249, BIT8-BIT15 DG-Status GEN250 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42792 |  | 342793 | 04 |  | BIT0-BIT7 DG-Status GEN251, BIT8-BIT15 DG-Status GEN252 (PMS lite) | INT8u | AB | 0 |  |  |  | X
PMS lite | 42793 |  | 342794 | 04 |  | BIT0-BIT7 DG-Status GEN253, BIT8-BIT15 DG-Status GEN254 (PMS lite) | INT8u | AB | 0 |  |  |  | X
EIC measurements value | 26000 |  | 326001 | 04 |  | Engine Speed (SPN 190) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26001 |  | 326002 | 04 |  | Engine Coolant Temperature (SPN 110) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26002 |  | 326003 | 04 |  | Engine Oil Pressure (SPN 100) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26003 |  | 326004 | 04 |  | Active Diagnostic Trouble Code Count (SPN 1218) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26004 |  | 326005 | 04 |  | Engine Oil Temperature 1 (SPN 175) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26005 |  | 326006 | 04 |  | Engine Fuel 1 Temperature 1 (SPN 174) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26006 |  | 326007 | 04 |  | Engine Intake Manifold #1 Pressure (SPN 102) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26007 |  | 326008 | 04 |  | Engine Intake 1 Air Temperature (SPN 172) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26008 |  | 326009 | 04 |  | Engine Coolant Level 1 (SPN 111) | INT16u | AB | 1 | perc |  |  | X | X | X
EIC measurements value | 26009 |  | 326010 | 04 |  | Engine Fuel Rate (SPN 183) | INT16u | AB | 1 | L/h |  |  | X | X | X
EIC measurements value | 26010 |  | 326011 | 04 |  | Charge air pressure (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26011 |  | 326012 | 04 |  | Engine Intake Manifold 1 Temperature (SPN 105) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26012 |  | 326013 | 04 |  | Driver's Demand Engine, Percent Torque (SPN 512) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26013 |  | 326014 | 04 |  | Actual Engine, Percent Torque (SPN 513) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26014 |  | 326015 | 04 |  | Accelerator Pedal Position 1 (SPN 91) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26015 |  | 326016 | 04 |  | Engine Percent Load At Current Speed (SPN 92) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26016 |  | 326017 | 04 |  | Engine Intake Air Pressure (SPN 106) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26017 |  | 326018 | 04 |  | Engine Exhaust Temperature (SPN 173) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26018 |  | 326019 | 04 |  | Engine Total Hours of Operation (SPN 247) | INT32u | ABCD | 0 | h |  |  | X | X | X
EIC measurements value | 26020 |  | 326021 | 04 |  | Engine Oil Filter Differential Pressure (SPN 99) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26021 |  | 326022 | 04 |  | Key Switch Battery Potential (SPN 158) | INT16u | AB | 1 | V |  |  | X | X | X
EIC measurements value | 26022 |  | 326023 | 04 |  | Engine Fuel Delivery Pressure (SPN 94) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26023 |  | 326024 | 04 |  | Engine Oil Level (SPN 98) | INT16u | AB | 1 | perc |  |  | X | X | X
EIC measurements value | 26024 |  | 326025 | 04 |  | Engine Crankcase Pressure 1 (SPN 101) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26025 |  | 326026 | 04 |  | Engine Coolant Pressure 1 (SPN 109) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26026 |  | 326027 | 04 |  | Water In Fuel Indicator 1 (SPN 97) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26027 |  | 326028 | 04 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26028 |  | 326029 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26029 |  | 326030 | 04 |  | Engine Air Filter 1 Differential Pressure (SPN 107) | INT16u | AB | 3 | bar/psi |  |  | X | X | X
EIC measurements value | 26030 |  | 326031 | 04 |  | Engine Coolant Filter Differential Pressure (SPN 112) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26031 |  | 326032 | 04 |  | Barometric Pressure (SPN 108) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26032 |  | 326033 | 04 |  | Ambient Air Temperature (SPN 171) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26033 |  | 326034 | 04 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26034 |  | 326035 | 04 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26035 |  | 326036 | 04 |  | Temp. Winding 1 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26036 |  | 326037 | 04 |  | Temp. Winding 2 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26037 |  | 326038 | 04 |  | Temp. Winding 3 (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26038 |  | 326039 | 04 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26039 |  | 326040 | 04 |  | Auxiliary_Analog_Info (ADEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26040 |  | 326041 | 04 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26041 |  | 326042 | 04 |  | Engine Intercooler Temperature (SPN 52) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26042 |  | 326043 | 04 |  | Engine Trip Fuel (SPN 182) | INT32u | ABCD | 0 | L |  |  | X | X | X
EIC measurements value | 26044 |  | 326045 | 04 |  | Engine Total Fuel Used (SPN 250) | INT32u | ABCD | 0 | kL |  |  | X | X | X
EIC measurements value | 26046 |  | 326047 | 04 |  | Trip Fuel (Gaseous) (SPN 1039) | INT32u | ABCD | 0 | kg |  |  | X | X | X
EIC measurements value | 26048 |  | 326049 | 04 |  | Total Fuel Used (Gaseous) (SPN 1040) | INT32u | ABCD | 1 | ton |  |  | X | X | X
EIC measurements value | 26050 |  | 326051 | 04 |  | Trip Average Fuel Rate (SPN 1029) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26051 |  | 326052 | 04 |  | Engine Rated Power (SPN 166) | INT16u | AB | 0 | kWm |  |  | X | X | X
EIC measurements value | 26052 |  | 326053 | 04 |  | Engine power (ADEC) | INT16u | AB | 0 | kW |  |  | X | X | X
EIC measurements value | 26053 |  | 326054 | 04 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26054 |  | 326055 | 04 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26055 |  | 326056 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26056 |  | 326057 | 04 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26057 |  | 326058 | 04 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26058 |  | 326059 | 04 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26059 |  | 326060 | 04 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26060 |  | 326061 | 04 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26061 |  | 326062 | 04 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26062 |  | 326063 | 04 |  | Engine Fuel Filter Differential Pressure (SPN 95) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26063 |  | 326064 | 04 |  | Speed demand Source (MDEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26064 |  | 326065 | 04 |  | P-Lube Oil Limit LO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26065 |  | 326066 | 04 |  | P-Lube Oil Limit LOLO (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26066 |  | 326067 | 04 |  | P-Fuel (MDEC) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26067 |  | 326068 | 04 |  | T-Coolant Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26068 |  | 326069 | 04 |  | T-Coolant Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26069 |  | 326070 | 04 |  | T-Coolant Intercooler (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26070 |  | 326071 | 04 |  | Engine ECU Temperature (SPN 1136) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26071 |  | 326072 | 04 |  | Actual Droop (MDEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26072 |  | 326073 | 04 |  | Injection Quantity Act.DBR % (MDEC) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26073 |  | 326074 | 04 |  | Engine Speed Camshaft (MDEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26074 |  | 326075 | 04 |  | T-Lube Oil Limit HI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26075 |  | 326076 | 04 |  | T-Lube Oil Limit HIHI (MDEC) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26076 |  | 326077 | 04 |  | Feedback Speed Demand analog (MDEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26077 |  | 326078 | 04 |  | Stop signal active (MDEC) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26078 |  | 326079 | 04 |  | Exhaust Port Temperature 01 (SPN 1137) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26079 |  | 326080 | 04 |  | Exhaust Port Temperature 02 (SPN 1138) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26080 |  | 326081 | 04 |  | Exhaust Port Temperature 03 (SPN 1139) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26081 |  | 326082 | 04 |  | Exhaust Port Temperature 04 (SPN 1140) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26082 |  | 326083 | 04 |  | Exhaust Port Temperature 05 (SPN 1141) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26083 |  | 326084 | 04 |  | Exhaust Port Temperature 06 (SPN 1142) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26084 |  | 326085 | 04 |  | Exhaust Port Temperature 07 (SPN 1143) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26085 |  | 326086 | 04 |  | Exhaust Port Temperature 08 (SPN 1144) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26086 |  | 326087 | 04 |  | Exhaust Port Temperature 09 (SPN 1145) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26087 |  | 326088 | 04 |  | Exhaust Port Temperature 10 (SPN 1146) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26088 |  | 326089 | 04 |  | Exhaust Port Temperature 11 (SPN 1147) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26089 |  | 326090 | 04 |  | Exhaust Port Temperature 12 (SPN 1148) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26090 |  | 326091 | 04 |  | Exhaust Port Temperature 13 (SPN 1149) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26091 |  | 326092 | 04 |  | Exhaust Port Temperature 14 (SPN 1150) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26092 |  | 326093 | 04 |  | Exhaust Port Temperature 15 (SPN 1151) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26093 |  | 326094 | 04 |  | Exhaust Port Temperature 16 (SPN 1152) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26094 |  | 326095 | 04 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26095 |  | 326096 | 04 |  | Engine Coolant Temperature 2 (SPN 4076) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26096 |  | 326097 | 04 |  | Engine Coolant Temperature 3 (SPN 6209) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26097 |  | 326098 | 04 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26098 |  | 326099 | 04 |  | Engine Auxiliary Coolant Temperature (SPN 1212) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26099 |  | 326100 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26100 |  | 326101 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26101 |  | 326102 | 04 |  | Engine Auxiliary Coolant Pressure (SPN 1203) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26102 |  | 326103 | 04 |  | Specific Humidity (SPN 4490) | INT16u | AB | 1 | g/kg |  |  | X | X | X
EIC measurements value | 26103 |  | 326104 | 04 |  | Engine Turbocharger 2 Speed (SPN 1169) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26104 |  | 326105 | 04 |  | Engine Turbocharger 3 Speed (SPN 1170) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26105 |  | 326106 | 04 |  | Trip Engine Running Time (SPN 1036) | INT32u | ABCD | 0 | h |  |  | X | X | X
EIC measurements value | 26107 |  | 326108 | 04 |  | Trip Idle Time (SPN 1037) | INT32u | ABCD | 0 | h |  |  | X | X | X
EIC measurements value | 26109 |  | 326110 | 04 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) | INT16u | AB | 1 | perc |  |  | X | X | X
EIC measurements value | 26110 |  | 326111 | 04 |  | Engine Turbocharger 1 Speed (SPN 103) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26111 |  | 326112 | 04 |  | Nominal Friction - Percent Torque (SPN 514) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26112 |  | 326113 | 04 |  | Engine's Desired Operating Speed (SPN 515) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26113 |  | 326114 | 04 |  | Engine Intake Manifold 2 Temperature (SPN 1131) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26114 |  | 326115 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) | INT16u | AB | 1 | perc |  |  | X | X | X
EIC measurements value | 26115 |  | 326116 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26116 |  | 326117 | 04 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26117 |  | 326118 | 04 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26118 |  | 326119 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) | INT16u | AB | 1 | g/h |  |  | X | X | X
EIC measurements value | 26119 |  | 326120 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26120 |  | 326121 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26121 |  | 326122 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) | INT16u | AB | 0 | g/h |  |  | X | X | X
EIC measurements value | 26122 |  | 326123 | 04 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26123 |  | 326124 | 04 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26124 |  | 326125 | 04 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26125 |  | 326126 | 04 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26126 |  | 326127 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26127 |  | 326128 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26128 |  | 326129 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26129 |  | 326130 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) | INT16u | AB | 1 | g/h |  |  | X | X | X
EIC measurements value | 26130 |  | 326131 | 04 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26131 |  | 326132 | 04 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26132 |  | 326133 | 04 |  | Engine Oil Filter Outlet Pressure (SPN 3549) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26133 |  | 326134 | 04 |  | Engine Operating State (SPN 3543) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26134 |  | 326135 | 04 |  | Source Address of Controlling Device for Engine Control (SPN 1483) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26135 |  | 326136 | 04 |  | Engine Rated Speed (SPN 189) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26136 |  | 326137 | 04 |  | Engine Speed At Idle, Point 1 (SPN 188) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26137 |  | 326138 | 04 |  | Fuel Consumption g/KWh (MTU) | INT16u | AB | 0 | g/kWh |  |  | X | X | X
EIC measurements value | 26138 |  | 326139 | 04 |  | Engine Status of Start procedure (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26139 |  | 326140 | 04 |  | Exhaust Port Temperature 17 (SPN 1153) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26140 |  | 326141 | 04 |  | Exhaust Port Temperature 18 (SPN 1154) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26141 |  | 326142 | 04 |  | Exhaust Port Temperature 19 (SPN 1155) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26142 |  | 326143 | 04 |  | Exhaust Port Temperature 20 (SPN 1156) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26143 |  | 326144 | 04 |  | UREA Level (Scania and Isuzu) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26144 |  | 326145 | 04 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26145 |  | 326146 | 04 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26146 |  | 326147 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26147 |  | 326148 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) | INT32u | ABCD | 1 | h |  |  | X | X | X
EIC measurements value | 26149 |  | 326150 | 04 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26150 |  | 326151 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26151 |  | 326152 | 04 |  | Purging Active (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26152 |  | 326153 | 04 |  | Limit Lamp Status (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26153 |  | 326154 | 04 |  | Battery Charger 1 Output Voltage (SPN 4992) | INT16u | AB | 0 | V |  |  | X | X | X
EIC measurements value | 26154 |  | 326155 | 04 |  | Battery Charger 1 Output Current (SPN 4993) | INT16u | AB | 0 | A |  |  | X | X | X
EIC measurements value | 26155 |  | 326156 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26156 |  | 326157 | 04 |  | Time left to torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26157 |  | 326158 | 04 |  | Time left to servere torque reduction (Volvo) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26158 |  | 326159 | 04 |  | SCR inducement severity (Volvo) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26159 |  | 326160 | 04 |  | SCR inducement reason (Volvo) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26160 |  | 326161 | 04 |  | Engine Derate Request (SPN 3644) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26161 |  | 326162 | 04 |  | Engine Demand, Percent Torque (SPN 2432) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26162 |  | 326163 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26163 |  | 326164 | 04 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26164 |  | 326165 | 04 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26165 |  | 326166 | 04 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26166 |  | 326167 | 04 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26167 |  | 326168 | 04 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26168 |  | 326169 | 04 |  | Engine Desired Ignition Timing 1 (SPN 1433) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26169 |  | 326170 | 04 |  | Engine Actual Ignition Timing (SPN 1436) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26170 |  | 326171 | 04 |  | EDC4 CAN Status (EMR) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26171 |  | 326172 | 04 |  | Engine Starter Mode (SPN 1675) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26172 |  | 326173 | 04 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) | INT16u | AB | 0 | perc |  |  | X | X | X
EIC measurements value | 26173 |  | 326174 | 04 |  | Engine Coolant Pre-heated State (SPN 3553) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26174 |  | 326175 | 04 |  | Engine Safety and Protection Override Status (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26175 |  | 326176 | 04 |  | Engine Cylinder Cut-off (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26176 |  | 326177 | 04 |  | Engine Running State (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26177 |  | 326178 | 04 |  | External Stop State (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26178 |  | 326179 | 04 |  | Requested Absolute Torque (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26179 |  | 326180 | 04 |  | Source of Current Speed Demand (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26180 |  | 326181 | 04 |  | Engine Demanded Operating Speed (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26181 |  | 326182 | 04 |  | Feedback of Speed Demand CAN (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26182 |  | 326183 | 04 |  | Feedback of Speed Demand Analogue Input (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26183 |  | 326184 | 04 |  | Speed Demand Fail Mode (MTU) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26184 |  | 326185 | 04 |  | Engine Shutdown Override Switch (SPN 1237) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26185 |  | 326186 | 04 |  | Engine Requested Speed (SPN 898) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26186 |  | 326187 | 04 |  | Escape Mode Enable Flag (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26187 |  | 326188 | 04 |  | Inducement Timer (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26188 |  | 326189 | 04 |  | Inducement Level (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26189 |  | 326190 | 04 |  | Urea Tank Level (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26190 |  | 326191 | 04 |  | Urea Tank Level Indicator (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26191 |  | 326192 | 04 |  | Level Indicator (Amber) Action (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26192 |  | 326193 | 04 |  | DPF Amber Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26193 |  | 326194 | 04 |  | EXH.SYSTEM lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26194 |  | 326195 | 04 |  | DPF Green Lamp Mode (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26195 |  | 326196 | 04 |  | NO POWER Lamp (Isuzu) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26196 |  | 326197 | 04 |  | Engine Intake Manifold 3 Temperature (SPN 1132) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26197 |  | 326198 | 04 |  | Engine Intake Manifold 4 Temperature (SPN 1133) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26198 |  | 326199 | 04 |  | Engine Oil Filter Intake Pressure (SPN 1208) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26199 |  | 326200 | 04 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26200 |  | 326201 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26201 |  | 326202 | 04 |  | Battery Potential / Power Input 1 (SPN 168) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26202 |  | 326203 | 04 |  | Dosing Module Status (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26203 |  | 326204 | 04 |  | Actual Reducing Agent Quantity (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26204 |  | 326205 | 04 |  | Aftertreatment Lamp (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26205 |  | 326206 | 04 |  | Refresh Status Byte (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26206 |  | 326207 | 04 |  | SCR Monitor (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26207 |  | 326208 | 04 |  | Successful Running Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26208 |  | 326209 | 04 |  | Successful Stationary Refreshes (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26209 |  | 326210 | 04 |  | Engine Rating (JCB) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26210 |  | 326211 | 04 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26211 |  | 326212 | 04 |  | Humidity Derate Percentage (Perkins/CAT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26212 |  | 326213 | 04 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26213 |  | 326214 | 04 |  | Number of EIO Activations (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26214 |  | 326215 | 04 |  | Accumulated EIO time (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26215 |  | 326216 | 04 |  | Time left of EIO Operation (Volvo EMS2.4) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26216 |  | 326217 | 04 |  | Remaining Service Hours (Hatz) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26217 |  | 326218 | 04 |  | Wheel Based Vehicle Speed (SPN 84) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26218 |  | 326219 | 04 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26219 |  | 326220 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26220 |  | 326221 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26221 |  | 326222 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26222 |  | 326223 | 04 |  | Phys. Injection quantity (Hatz) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26223 |  | 326224 | 04 |  | Phys. Torque (Hatz) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26224 |  | 326225 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26225 |  | 326226 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26226 |  | 326227 | 04 |  | Operator Inducement Time to Torque Derate Level 1 (SPN 7426) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26227 |  | 326228 | 04 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26228 |  | 326229 | 04 |  | Alternator 1 Status (SPN 3353) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26252 |  | 326253 | 04 |  | Engine Throttle Valve 1 Position 1 (SPN 51) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26253 |  | 326254 | 04 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26254 |  | 326255 | 04 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26255 |  | 326256 | 04 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) | INT16 | AB | 0 | Deg |  |  | X | X | X
EIC measurements value | 26256 |  | 326257 | 04 |  | Engine Intake Air Mass Flow Rate (SPN 132) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26257 |  | 326258 | 04 |  | Engine Lambda (Yuchai) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26258 |  | 326259 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26259 |  | 326260 | 04 |  | DPF Regeneration State (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26260 |  | 326261 | 04 |  | DPF Regeneration Countdown Timer (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26261 |  | 326262 | 04 |  | DEF Level (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26262 |  | 326263 | 04 |  | DEF Quality (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26263 |  | 326264 | 04 |  | DEF Technical Failure (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26264 |  | 326265 | 04 |  | Cold Start Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26265 |  | 326266 | 04 |  | Fuel Filter Heater Status (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26266 |  | 326267 | 04 |  | Low Idle Increase Desired (FPT) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26267 |  | 326268 | 04 |  | Urea level inducement state (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26268 |  | 326269 | 04 |  | Emission-OBD inducement state (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26269 |  | 326270 | 04 |  | Emission-OBD inducement failure reason (Scania) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26270 |  | 326271 | 04 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26271 |  | 326272 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26272 |  | 326273 | 04 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26273 |  | 326274 | 04 |  | Engine Oil Priming State (SPN 3551) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26274 |  | 326275 | 04 |  | Fuel Pump Primer Status (SPN 4083) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26275 |  | 326276 | 04 |  | Sensor supply voltage 1 (SPN 3509) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26276 |  | 326277 | 04 |  | Sensor supply voltage 2 (SPN 3510) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26277 |  | 326278 | 04 |  | Accelerator Pedal Position 2 (SPN 29) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26278 |  | 326279 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26279 |  | 326280 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26280 |  | 326281 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26281 |  | 326282 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26282 |  | 326283 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26283 |  | 326284 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26284 |  | 326285 | 04 |  | Feedback Engine Fueling State (SPN 5794) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26285 |  | 326286 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26286 |  | 326287 | 04 |  | Blowby flow (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26287 |  | 326288 | 04 |  | Fuel rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26288 |  | 326289 | 04 |  | Timing rail pressure (Cummins H6) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26289 |  | 326290 | 04 |  | Aftercooler water inlet temperature (Cummins H6) | INT16u | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurements value | 26290 |  | 326291 | 04 |  | Fuel Rank position left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26291 |  | 326292 | 04 |  | Fuel Rank position right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26292 |  | 326293 | 04 |  | Intake Manifold pressure left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26293 |  | 326294 | 04 |  | Intake Manifold pressure right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26294 |  | 326295 | 04 |  | Intake Manifold Temperature left (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26295 |  | 326296 | 04 |  | Intake Manifold Temperature right (Cummins H6) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26296 | 7 | 326297 | 04 |  | DPF lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 6 | 326297 | 04 |  | DPF lamp ON solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 5 | 326297 | 04 |  | DPF lamp ON blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 4 | 326297 | 04 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 3 | 326297 | 04 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 2 | 326297 | 04 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 1 | 326297 | 04 |  | DPF Regeneration not needed | BOOL | [5 empty] | X | X | X
EIC measurements value | 26296 | 0 | 326297 | 04 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 7 | 326298 | 04 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 6 | 326298 | 04 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 5 | 326298 | 04 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 4 | 326298 | 04 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 3 | 326298 | 04 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 2 | 326298 | 04 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 1 | 326298 | 04 |  | MTU limit lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26297 | 0 | 326298 | 04 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 7 | 326299 | 04 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 6 | 326299 | 04 |  | DEF level low lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 5 | 326299 | 04 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 4 | 326299 | 04 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 3 | 326299 | 04 |  | After run status | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 2 | 326299 | 04 |  | Volvo Penta Scr Inducement not ACTIVE | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 1 | 326299 | 04 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X | X | X
EIC measurements value | 26298 | 0 | 326299 | 04 |  | EMPTY | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 7 | 326300 | 04 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 6 | 326300 | 04 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 5 | 326300 | 04 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 4 | 326300 | 04 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 3 | 326300 | 04 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 2 | 326300 | 04 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 1 | 326300 | 04 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X | X | X
EIC measurements value | 26299 | 0 | 326300 | 04 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 7 | 326301 | 04 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 6 | 326301 | 04 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 5 | 326301 | 04 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 4 | 326301 | 04 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 3 | 326301 | 04 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 2 | 326301 | 04 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 1 | 326301 | 04 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X | X | X
EIC measurements value | 26300 | 0 | 326301 | 04 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 7 | 326302 | 04 |  | Alarm Red lamp ON | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 6 | 326302 | 04 |  | Engine fuel leak | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 5 | 326302 | 04 |  | Engine Wait to start | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 4 | 326302 | 04 |  | Engine Protect system shutdown | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 3 | 326302 | 04 |  | Engine Protect system appro shutdown | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 2 | 326302 | 04 |  | Engine alarm acknowledge | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 1 | 326302 | 04 |  | Engine ait shutoff command status | BOOL | [5 empty] | X | X | X
EIC measurements value | 26301 | 0 | 326302 | 04 |  | Engine overspeed test | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 7 | 326303 | 04 |  | Engine shutoff status | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 6 | 326303 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 5 | 326303 | 04 |  | Manual purge EIDSS | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 4 | 326303 | 04 |  | Force purge | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 3 | 326303 | 04 |  | JCB Amber blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 2 | 326303 | 04 |  | JCB Amber solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 1 | 326303 | 04 |  | JCB Red blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26302 | 0 | 326303 | 04 |  | JCB Red solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 7 | 326304 | 04 |  | JCB Engine emission system failure warning | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 6 | 326304 | 04 |  | JCB Engine emission system failure low | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 5 | 326304 | 04 |  | JCB Engine emission system failure high | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 4 | 326304 | 04 |  | JCB Particulate filter restricted high | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 3 | 326304 | 04 |  | JCB Particulate filter restricted very high | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 2 | 326304 | 04 |  | JCB Particulate filter restricted critical | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 1 | 326304 | 04 |  | DPF lamp - fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26303 | 0 | 326304 | 04 |  | DEF low level - Fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 7 | 326305 | 04 |  | Red lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 6 | 326305 | 04 |  | Red lamp solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 5 | 326305 | 04 |  | Red lamp blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 4 | 326305 | 04 |  | Red lamp fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 3 | 326305 | 04 |  | Yellow lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 2 | 326305 | 04 |  | Yellow lamp solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 1 | 326305 | 04 |  | Yellow lamp blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26304 | 0 | 326305 | 04 |  | Yellow lamp fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 7 | 326306 | 04 |  | MIL lamp OFF | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 6 | 326306 | 04 |  | MIL lamp solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 5 | 326306 | 04 |  | MIL lamp blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 4 | 326306 | 04 |  | MIL lamp fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 3 | 326306 | 04 |  | Engine emission system failure lamp off | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 2 | 326306 | 04 |  | Engine emission system failure lamp solid | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 1 | 326306 | 04 |  | Engine emission system failure lamp blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26305 | 0 | 326306 | 04 |  | Engine emission system failure lamp fast blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 7 | 326307 | 04 |  | DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 6 | 326307 | 04 |  | DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 5 | 326307 | 04 |  | DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 4 | 326307 | 04 |  | DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 3 | 326307 | 04 |  | Engine Running (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 2 | 326307 | 04 |  | Service Delay (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 1 | 326307 | 04 |  | Pre-glow Active (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26306 | 0 | 326307 | 04 |  | Oil Pressure Missing (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 7 | 326308 | 04 |  | Engine Diagnostic Lamp (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 6 | 326308 | 04 |  | Engine Overtemperature (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 5 | 326308 | 04 |  | Air Filter Switch (Hatz) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 4 | 326308 | 04 |  | Transmission Neutral Switch (SPN 604) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 3 | 326308 | 04 |  | Parking Brake Switch (SPN 70) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26307 | 2 | 326308 | 04 |  | Brake Switch (SPN 597) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 6 | 326310 | 04 |  | Exhaust Over Heat Condition (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 5 | 326310 | 04 |  | Engine Over Speed Warning (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 4 | 326310 | 04 |  | Urea Thawing Mode Active (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 3 | 326310 | 04 |  | Scr Injector Overheat Protection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 2 | 326310 | 04 |  | Turbo Charger Protection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 1 | 326310 | 04 |  | Engine Protection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26309 | 0 | 326310 | 04 |  | Water in Fuel Detection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 7 | 326311 | 04 |  | Fuel in Oil Detection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 6 | 326311 | 04 |  | Low Catalyst Efficiency (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 5 | 326311 | 04 |  | Bad Urea Quality (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 4 | 326311 | 04 |  | Nh3 Slip Detection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 3 | 326311 | 04 |  | Engine Oil Over Temperature (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 2 | 326311 | 04 |  | Smoke Limitation (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 1 | 326311 | 04 |  | Clogged DPF (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26310 | 0 | 326311 | 04 |  | Oil switch (Kubota) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26311 |  | 326312 | 04 |  | Trip Average Fuel Rate (SPN 1029) RAW | INT32u | ABCD | 0 |  |  |  | X | X | X
EIC measurements value | 26313 |  | 326314 | 04 |  | Engine Trip Fuel (SPN 182) RAW | INT32u | ABCD | 0 |  |  |  | X | X | X
EIC measurements value | 26315 |  | 326316 | 04 |  | Engine Total Fuel Used (SPN 250) RAW | INT32u | ABCD | 0 |  |  |  | X | X | X
EIC measurements value | 26317 |  | 326318 | 04 |  | Engine Controlled Shutdown Request (SPN 5795) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26318 |  | 326319 | 04 |  | Engine Oil Pre-Heated State (SPN 3552) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26319 |  | 326320 | 04 |  | Engine Ventilation Status (SPN 3554) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26320 |  | 326321 | 04 |  | Rail pressure (Jichai) | INT16u | AB | 2 |  |  |  | X | X | X
EIC measurements value | 26321 |  | 326322 | 04 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) | INT16u | AB | 2 |  |  |  | X | X | X
EIC measurements value | 26322 |  | 326323 | 04 |  | Jichai WYS Fault code 1.1 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26323 |  | 326324 | 04 |  | Jichai WYS Fault code 1.2 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26324 |  | 326325 | 04 |  | Jichai WYS Fault code 1.3 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26325 |  | 326326 | 04 |  | Jichai WYS Fault code 1.4 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26326 |  | 326327 | 04 |  | Jichai WYS Fault code 2.1 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26327 |  | 326328 | 04 |  | Jichai WYS Fault code 2.2 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26328 |  | 326329 | 04 |  | Jichai WYS Fault code 2.3 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26329 |  | 326330 | 04 |  | Jichai WYS Fault code 2.4 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26330 |  | 326331 | 04 |  | Jichai Engine torque | INT16u | AB | 0 | Nm |  |  | X | X | X
EIC measurements value | 26331 |  | 326332 | 04 |  | Jichai Engine reference torque | INT16u | AB | 0 | Nm |  |  | X | X | X
EIC measurements value | 26332 |  | 326333 | 04 |  | Jichai Oil pressure of boost | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26333 |  | 326334 | 04 |  | Jichai Oil pressure after filtration | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26334 |  | 326335 | 04 |  | Jichai High temperature water inlet temperature | INT16u | AB | 2 | C/F |  |  | X | X | X
EIC measurements value | 26335 |  | 326336 | 04 |  | Jichai Cooler inlet water temperature | INT16u | AB | 2 | C/F |  |  | X | X | X
EIC measurements value | 26336 |  | 326337 | 04 |  | Jichai Engine status | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26337 |  | 326338 | 04 |  | Jichai Engine target speed | INT16u | AB | 0 | RPM |  |  | X | X | X
EIC measurements value | 26338 |  | 326339 | 04 |  | Engine Fuel Valve 1 Position (SPN 1442) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26339 |  | 326340 | 04 |  | Engine Gaseous Fuel Supply Pressure 1 (SPN 159) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26340 |  | 326341 | 04 |  | Fuel Injection Quantity (Kubota) | INT16u | AB | 1 | mm3/st |  |  | X | X | X
EIC measurements value | 26341 |  | 326342 | 04 |  | Regeneration Status (Kubota) | INT16u | AB | 0 | None |  |  | X | X | X
EIC measurements value | 26342 |  | 326343 | 04 |  | Ash Accumulation Time (Kubota) | INT32u | ABCD | 1 | h |  |  | X | X | X
EIC measurements value | 26344 |  | 326345 | 04 |  | Operator Inducement Reason (Kubota) | INT16u | AB | 0 | None |  |  | X | X | X
EIC measurements value | 26345 |  | 326346 | 04 |  | Operator Inducement Severity (Kubota) | INT16u | AB | 0 | None |  |  | X | X | X
EIC measurements value | 26346 |  | 326347 | 04 |  | HC Evaporation Status (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26347 |  | 326348 | 04 |  | HC Evaporation Required Action (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26348 |  | 326349 | 04 |  | HC Evaporation Progress Countdown Timer (Scania EMS2 S8) | INT16u | AB | 0 | min |  |  | X | X | X
EIC measurements value | 26349 |  | 326350 | 04 |  | HC Evaporation Action Start Countdown Timer (Scania EMS2 S8) | INT16u | AB | 0 | min |  |  | X | X | X
EIC measurements value | 26350 |  | 326351 | 04 |  | Sulphur Regeneration request (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26351 |  | 326352 | 04 |  | deSOx heatup request (Scania EMS2 S8) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26352 |  | 326353 | 04 |  | Insulation resistance (KWG ISO5 isolation monitor) | INT32u | ABCD | 0 | ohm |  |  | X | X | X
EIC measurements value | 26354 | 7 | 326355 | 04 |  | Evaporation Not Required (Scania S8) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 6 | 326355 | 04 |  | Evaporation Required Less Urgent (Scania S8) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 5 | 326355 | 04 |  | Evaporation Required Urgent (Scania S8) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 4 | 326355 | 04 |  | Evaporation Is In Progress (Scania S8) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 3 | 326355 | 04 |  | Isolation Fault (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 2 | 326355 | 04 |  | Isolation Warning (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 1 | 326355 | 04 |  | Isolation Timeout (KWG ISO5 isolation monitor) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26354 | 0 | 326355 | 04 |  | Turbo heat protection (FPT) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 7 | 326356 | 04 |  | Doosan stage 5 ash lamp status > 100% | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 6 | 326356 | 04 |  | Doosan stage 5 ash lamp status 100%-105% | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 5 | 326356 | 04 |  | Doosan stage 5 ash lamp status 106%-110% | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 4 | 326356 | 04 |  | Doosan stage 5 ash lamp status 111%-120% | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 3 | 326356 | 04 |  | Doosan stage 5 ash lamp status < 121% | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 2 | 326356 | 04 |  | DPF Thermal Management Active (SPN 5399) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 1 | 326356 | 04 |  | SCR Thermal Management Active (SPN 5400) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26355 | 0 | 326356 | 04 |  | SCR System Cleaning Status (SPN 6916) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26356 |  | 326357 | 04 |  | Doosan stage 5 ash lamp status | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26357 | 7 | 326358 | 04 |  | SCR System Cleaning Inhibited Status (SPN 6917) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 6 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Inhibit Switch (SPN 6918) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 5 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Low Exhaust Temperature (SPN 6926) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 4 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to System Fault Active (SPN 6927) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 3 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Engine Not Warmed Up (SPN 6931) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 2 | 326358 | 04 |  | Yanmar Stage V Accelerator Interlock Switch feedback | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 1 | 326358 | 04 |  | Yanmar Stage V DPF regenaration acknowledge lamp | BOOL | [5 empty] | X | X | X
EIC measurements value | 26357 | 0 | 326358 | 04 |  | DEF low level -Slow blink | BOOL | [5 empty] | X | X | X
EIC measurements value | 26358 |  | 326359 | 04 |  | SCR System Cleaning Lamp Command (SPN 6915) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26359 |  | 326360 | 04 |  | SCR System Cleaning Forced Status (SPN 6934) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26360 |  | 326361 | 04 |  | JiChai JC15T JG Fuel Valve Self-Adjust | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26361 |  | 326362 | 04 |  | JiChai JC15T JG Fuel Valve CloseLoop-Adjust | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26362 |  | 326363 | 04 |  | JiChai JC15T JG Air Fuel Ratio | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26363 |  | 326364 | 04 |  | JiChai JC15T JG Natural Gas Temperature | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26364 |  | 326365 | 04 |  | JiChai JC15T JG Natural Gas Pressure | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26365 |  | 326366 | 04 |  | JiChai JC15T JG Gas Supply Amount Per Second | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26366 |  | 326367 | 04 |  | JiChai JC15T JG PHI | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26367 |  | 326368 | 04 |  | Doosan stage 5 Emission OBD Inducement lamp status | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26368 |  | 326369 | 04 |  | Doosan stage 5 Emission OBD lamp failure reason | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26369 |  | 326370 | 04 |  | Engine Fuel Valve 1 Differential Pressure | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26370 |  | 326371 | 04 |  | Engine Fuel Flow Rate 1 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26371 |  | 326372 | 04 |  | Weichai Engine Oil Pressure | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26372 |  | 326373 | 04 |  | Weichai Engine Oil Pressure | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26373 |  | 326374 | 04 |  | Weichai Pre-throttle Pressure 1 | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26374 |  | 326375 | 04 |  | Weichai Throttle 1 Position | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26375 |  | 326376 | 04 |  | Weichai Throttle 2 Position | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26376 |  | 326377 | 04 |  | Weichai Bypass Valve 1 Position | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26377 |  | 326378 | 04 |  | Weichai Altronic RPM | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26378 |  | 326379 | 04 |  | Weichai Altronic Supply Voltage | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26379 |  | 326380 | 04 |  | Weichai Relative Humidity | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26380 |  | 326381 | 04 |  | Weichai Humidity Sensor Air Temperature | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26381 |  | 326382 | 04 |  | Weichai Air Filter DP | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26382 |  | 326383 | 04 |  | Weichai CH4 Concentration | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26383 |  | 326384 | 04 |  | Weichai H2S Concentration | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26384 |  | 326385 | 04 |  | Weichai Closed Loop Correction | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26385 |  | 326386 | 04 |  | Weichai Engine Exhaust O2 Sensor Fueling Correction | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26386 |  | 326387 | 04 |  | Fan Speed (SPN 1639) | INT16u | AB | 0 | rpm |  |  | X | X | X
EIC measurements value | 26387 |  | 326388 | 04 |  | DPF Active Regeneration Inhibited Due to System Fault Active (SPN 3712) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26388 |  | 326389 | 04 |  | FPT HC level | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26389 |  | 326390 | 04 |  | FPT EGR / DPF operator inducement | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26390 |  | 326391 | 04 |  | Deutz EMR5 Standstill request reason | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26391 |  | 326392 | 04 |  | Deutz EMR5 SCR warning Lamp / EAT inducement Lamp | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26392 |  | 326393 | 04 |  | Jing Guan Fuel temperature | INT16u | AB | 0 | deg C/F |  |  | X | X | X
EIC measurements value | 26393 |  | 326394 | 04 |  | Jing Guan Exhaust temperature | INT16u | AB | 1 | deg C/F |  |  | X | X | X
EIC measurements value | 26394 |  | 326395 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time since Last Active Regeneration (SPN 3721) | INT32u | ABCD | 1 | h |  |  | X | X | X
EIC measurements value | 26396 |  | 326397 | 04 |  | Aftertreatment 1 SCR Intake NOx 2 (SPN 7649) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26397 |  | 326398 | 04 |  | Aftertreatment 2 SCR Intake NOx 2 (SPN 7671) | INT16u | AB | 0 | ppm |  |  | X | X | X
EIC measurements value | 26411 |  | 326412 | 04 |  | Engine Fuel Valve 2 Position (SPN 1443) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26412 |  | 326413 | 04 |  | Engine Fuel Valve 1 Outlet Absolute Pressure (SPN 2980) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26413 |  | 326414 | 04 |  | Engine Throttle 2 Position (SPN 3673) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26414 |  | 326415 | 04 |  | Engine Throttle Valve 1 Differential Pressure (SPN 5631) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26415 |  | 326416 | 04 |  | Engine Oil Priming Pump Switch (SPN 3550) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26416 |  | 326417 | 04 |  | Engine Gas Mass Flow Rate 1 (SPN 1241) | INT16u | AB | 0 | kg/h |  |  | X | X | X
EIC measurements value | 26417 |  | 326418 | 04 |  | Instantaneous Estimated Brake Power (SPN 1242) | INT16u | AB | 0 | kW |  |  | X | X | X
EIC measurements value | 26418 |  | 326419 | 04 |  | Accelerator Pedal 1 Low Idle Switch (SPN 558) | BOOL | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26419 |  | 326420 | 04 |  | Engine Cylinder 1 Knock Level (SPN 1352, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26420 |  | 326421 | 04 |  | Engine Cylinder 2 Knock Level (SPN 1353, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26421 |  | 326422 | 04 |  | Engine Cylinder 3 Knock Level (SPN 1354, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26422 |  | 326423 | 04 |  | Engine Cylinder 4 Knock Level (SPN 1355, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26423 |  | 326424 | 04 |  | Engine Cylinder 5 Knock Level (SPN 1356, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26424 |  | 326425 | 04 |  | Engine Cylinder 6 Knock Level (SPN 1357, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26425 |  | 326426 | 04 |  | Engine Cylinder 7 Knock Level (SPN 1358, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26426 |  | 326427 | 04 |  | Engine Cylinder 8 Knock Level (SPN 1359, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26427 |  | 326428 | 04 |  | Engine Cylinder 9 Knock Level (SPN 1360, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26428 |  | 326429 | 04 |  | Engine Cylinder 10 Knock Level (SPN 1361, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26429 |  | 326430 | 04 |  | Engine Cylinder 11 Knock Level (SPN 1362, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26430 |  | 326431 | 04 |  | Engine Cylinder 12 Knock Level (SPN 1363, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26431 |  | 326432 | 04 |  | Engine Cylinder 13 Knock Level (SPN 1364, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26432 |  | 326433 | 04 |  | Engine Cylinder 14 Knock Level (SPN 1365, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26433 |  | 326434 | 04 |  | Engine Cylinder 15 Knock Level (SPN 1366, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26434 |  | 326435 | 04 |  | Engine Cylinder 16 Knock Level (SPN 1367, Cummins) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26435 |  | 326436 | 04 |  | Cylinder 1 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26436 |  | 326437 | 04 |  | Cylinder 2 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26437 |  | 326438 | 04 |  | Cylinder 3 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26438 |  | 326439 | 04 |  | Cylinder 4 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26439 |  | 326440 | 04 |  | Cylinder 5 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26440 |  | 326441 | 04 |  | Cylinder 6 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26441 |  | 326442 | 04 |  | Cylinder 7 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26442 |  | 326443 | 04 |  | Cylinder 8 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26443 |  | 326444 | 04 |  | Cylinder 9 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26444 |  | 326445 | 04 |  | Cylinder 10 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26445 |  | 326446 | 04 |  | Cylinder 11 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26446 |  | 326447 | 04 |  | Cylinder 12 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26447 |  | 326448 | 04 |  | Cylinder 13 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26448 |  | 326449 | 04 |  | Cylinder 14 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26449 |  | 326450 | 04 |  | Cylinder 15 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26450 |  | 326451 | 04 |  | Cylinder 16 Knock Counter (Cummins proprietary) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26451 |  | 326452 | 04 |  | Engine Cylinder 2 Ignition Timing (SPN 1414, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26452 |  | 326453 | 04 |  | Engine Cylinder 3 Ignition Timing (SPN 1415, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26453 |  | 326454 | 04 |  | Engine Cylinder 4 Ignition Timing (SPN 1416, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26454 |  | 326455 | 04 |  | Engine Cylinder 5 Ignition Timing (SPN 1417, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26455 |  | 326456 | 04 |  | Engine Cylinder 6 Ignition Timing (SPN 1418, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26456 |  | 326457 | 04 |  | Engine Cylinder 7 Ignition Timing (SPN 1419, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26457 |  | 326458 | 04 |  | Engine Cylinder 8 Ignition Timing (SPN 1420, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26458 |  | 326459 | 04 |  | Engine Cylinder 9 Ignition Timing (SPN 1421, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26459 |  | 326460 | 04 |  | Engine Cylinder 10 Ignition Timing (SPN 1422, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26460 |  | 326461 | 04 |  | Engine Cylinder 11 Ignition Timing (SPN 1423, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26461 |  | 326462 | 04 |  | Engine Cylinder 12 Ignition Timing (SPN 1424, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26462 |  | 326463 | 04 |  | Engine Cylinder 13 Ignition Timing (SPN 1425, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26463 |  | 326464 | 04 |  | Engine Cylinder 14 Ignition Timing (SPN 1426, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26464 |  | 326465 | 04 |  | Engine Cylinder 15 Ignition Timing (SPN 1427, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26465 |  | 326466 | 04 |  | Engine Cylinder 16 Ignition Timing (SPN 1428, Cummins) | INT16 | AB | 1 | Deg |  |  | X | X | X
EIC measurements value | 26466 |  | 326467 | 04 |  | Engine Spark Plug 1 (SPN 1294, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26467 |  | 326468 | 04 |  | Engine Spark Plug 2 (SPN 1295, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26468 |  | 326469 | 04 |  | Engine Spark Plug 3 (SPN 1296, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26469 |  | 326470 | 04 |  | Engine Spark Plug 4 (SPN 1297, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26470 |  | 326471 | 04 |  | Engine Spark Plug 5 (SPN 1298, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26471 |  | 326472 | 04 |  | Engine Spark Plug 6 (SPN 1299, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26472 |  | 326473 | 04 |  | Engine Spark Plug 7 (SPN 1300, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26473 |  | 326474 | 04 |  | Engine Spark Plug 8 (SPN 1301, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26474 |  | 326475 | 04 |  | Engine Spark Plug 9 (SPN 1302, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26475 |  | 326476 | 04 |  | Engine Spark Plug 10 (SPN 1303, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26476 |  | 326477 | 04 |  | Engine Spark Plug 11 (SPN 1304, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26477 |  | 326478 | 04 |  | Engine Spark Plug 12 (SPN 1305, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26478 |  | 326479 | 04 |  | Engine Spark Plug 13 (SPN 1306, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26479 |  | 326480 | 04 |  | Engine Spark Plug 14 (SPN 1307, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26480 |  | 326481 | 04 |  | Engine Spark Plug 15 (SPN 1308, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26481 |  | 326482 | 04 |  | Engine Spark Plug 16 (SPN 1309, Cummins) | INT16u | AB | 2 | kV |  |  | X | X | X
EIC measurements value | 26482 |  | 326483 | 04 |  | Engine extended range oil filter diff press (SPN 6321) | INT16u | AB | 2/1 | bar/psi |  |  | X | X | X
EIC measurements value | 26483 |  | 326484 | 04 |  | Sea Water Pump Outlet Pressure (SPN 2435) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26484 |  | 326485 | 04 |  | Water In Fuel Indicator 2 (SPN 6301) | BOOL | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26485 |  | 326486 | 04 |  | Aftertreatment 1 SCR System Hydrocarbon (SPN 7934) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26486 |  | 326487 | 04 |  | Aftertreatment System Enable Status (SPN 7851) | BOOL | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26487 |  | 326488 | 04 |  | Aftertreatment DEF Dosing Mode Status (SPN 9176) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26488 |  | 326489 | 04 |  | Aftertreatment 1 SCR System State (SPN 4332) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26489 |  | 326490 | 04 |  | Aftertreatment 1 SCR Intake Pressure (SPN 6586) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26490 |  | 326491 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Pressure (SPN 6875) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26491 |  | 326492 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Temperature (SPN 4368) | INT16u | AB | 0 | C/F |  |  | X | X | X
EIC measurements value | 26492 |  | 326493 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Tank Volume (SPN 4367) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26493 |  | 326494 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Fill Valve Command (SPN 5434) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26494 |  | 326495 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Pump Drive Percentage (SPN 4375) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26495 |  | 326496 | 04 |  | Aftertreatment 1 Total Diesel Exhaust Fluid Used (SPN 5963) | INT32u | AB | 0 | L |  |  | X | X | X
EIC measurements value | 26497 |  | 326498 | 04 |  | Total Aftertreatment Operating Hours (SPN 8629) | INT16u | AB | 0 | h |  |  | X | X | X
EIC measurements value | 26499 |  | 326500 | 04 |  | Engine Fuel Rate (High Resolution) (SPN 1600) | INT16u | AB | 2 | L/h |  |  | X | X | X
EIC measurements value | 26501 |  | 326502 | 04 |  | Engine Fuel Leakage 1 (SPN 1239) | BOOL | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26502 |  | 326503 | 04 |  | Restriction level according to DEF tank level | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26503 |  | 326504 | 04 |  | DEF tank level – Thresholds | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26504 |  | 326505 | 04 |  | Restriction caused by standstill request | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26505 |  | 326506 | 04 |  | Restriction level according to NOx reduction | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26506 |  | 326507 | 04 |  | Restriction level according to anti-tampering | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26507 |  | 326508 | 04 |  | SCR operator inducement reason | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26508 |  | 326509 | 04 |  | Pedal Input Delay (Kohler KDI3404) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26509 |  | 326510 | 04 |  | Driver Warning System Indicator Status (SPN 5825) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26510 |  | 326511 | 04 |  | Emission Control System Operator Inducement Severity (SPN 5826) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26511 |  | 326512 | 04 |  | EIC Time remaining to inducement act (Kohler KDI3404) | INT16u | AB | 0 | min |  |  | X | X | X
EIC measurements value | 26512 |  | 326513 | 04 |  | EIC Fuel Main Fltr Out Press L (Mitsubishi MGS3100) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26513 |  | 326514 | 04 |  | EIC Fuel Pre Fltr Dif Press (Mitsubishi MGS3100) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26514 |  | 326515 | 04 |  | EIC Engine Fuel Supply Pump Intake Pressure #2 (YC-ECU-A) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26515 |  | 326516 | 04 |  | EIC Engine Fuel Filter (suction side) Differential Pressure #2 (YC-ECU-A) | INT16u | AB | 2 | bar |  |  | X | X | X
EIC measurements value | 26516 |  | 326517 | 04 |  | EIC Engine Torque Mode (SPN 899) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26517 |  | 326518 | 04 |  | EIC Actual Engine - Percent Torque (Fractional) (SPN 4154) | INT16u | AB | 3 | % |  |  | X | X | X
EIC measurements value | 26518 |  | 326519 | 04 |  | EIC Engine Desired Speed Asymmetrical Adjustment (SPN 519) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26519 |  | 326520 | 04 |  | EIC Estimated Engine Parasitic Losses (SPN 2978) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26520 |  | 326521 | 04 |  | EIC Aftertreatment 1 Intake Dew Point (SPN 3237) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26521 |  | 326522 | 04 |  | EIC Aftertreatment 1 Exhaust Dew Point (SPN 3238) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26522 |  | 326523 | 04 |  | EIC Aftertreatment 2 Intake Dew Point (SPN 3239) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26523 |  | 326524 | 04 |  | EIC Aftertreatment 2 Exhaust Dew Point (SPN 3240) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26524 |  | 326525 | 04 |  | EIC Charge Air Cooler Thermostat Opening (SPN 1134) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26525 |  | 326526 | 04 |  | EIC Engine Extended Crankcase Blowby Pressure (SPN 22) | INT16u | AB | 2 | bar/psi |  |  | X | X | X
EIC measurements value | 26526 |  | 326527 | 04 |  | EIC Accelerator Pedal Kickdown Switch (SPN 559) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26527 |  | 326528 | 04 |  | EIC Road Speed Limit Status (SPN 1437) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26528 |  | 326529 | 04 |  | EIC Accelerator Pedal 2 Low Idle Switch (SPN 2970) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26529 |  | 326530 | 04 |  | EIC Remote Accelerator Pedal Position (SPN 974) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26530 |  | 326531 | 04 |  | EIC Vehicle Acceleration Rate Limit Status (SPN 2979) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26531 |  | 326532 | 04 |  | EIC Momentary Engine Maximum Power Enable Feedback (SPN 5021) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26532 |  | 326533 | 04 |  | EIC Estimated Pumping Percentage Torque (SPN 5398) | INT16u | AB | 0 | % |  |  | X | X | X
EIC measurements value | 26533 |  | 326534 | 04 |  | EIC Engine Total Revolutions (SPN 249) | INT32u | ABCD | 0 | h |  |  | X | X | X
EIC measurements value | 26535 |  | 326536 | 04 |  | EIC Cab Interior Temperature (SPN 170) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26536 |  | 326537 | 04 |  | EIC Road Surface Temperature (SPN 79) | INT16u | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurements value | 26537 |  | 326538 | 04 |  | EIC Transmission Oil Temperature 1 (SPN 177, CVT transmission) | INT16u | AB | 1 | bar |  |  | X | X | X
EIC measurements value | 26538 |  | 326539 | 04 |  | EIC Transmission Actual Gear Ratio (SPN 526, CVT transmission) | INT16u | AB | 3 | none |  |  | X | X | X
EIC measurements value | 26539 |  | 326540 | 04 |  | EIC Transmission Engine Crank Enable (SPN 2900, CVT transmission) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26540 |  | 326541 | 04 |  | EIC Transmission Shift Inhibit Indicator (SPN 1851, CVT transmission) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26542 |  | 326543 | 04 |  | Isuzu Engine Derate Lamp | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26543 |  | 326544 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser Pressure (SPN 6876) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26544 |  | 326545 | 04 |  | Engine Friction Percent Torque At Idle, Point 1 (SPN 5471) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26545 |  | 326546 | 04 |  | Engine Friction Percent Torque, Point 2 (SPN 5472) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26546 |  | 326547 | 04 |  | Engine Friction Percent Torque, Point 3 (SPN 5473) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26547 |  | 326548 | 04 |  | Engine Friction Percent Torque, Point 4 (SPN 5474) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26548 |  | 326549 | 04 |  | Engine Friction Percent Torque, Point 5 (SPN 5475) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26549 |  | 326550 | 04 |  | Engine Friction Percent Torque, Point 6 (SPN 5476) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26550 |  | 326551 | 04 |  | Engine Friction Percent Torque, Point 7 (SPN 5477) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26551 |  | 326552 | 04 |  | Aftertreatment 2 SCR Differential Pressure Preliminary FMI (SPN 4412) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26552 |  | 326553 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Pressure (SPN 3610) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26553 |  | 326554 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intermediate Temperature Preliminary FMI (SPN 3254) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26554 |  | 326555 | 04 |  | Operator Inducement Time to Torque Derate Level 3/FINAL (SPN 7719) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26555 |  | 326556 | 04 |  | OBD Malfunction Indicator Lamp Command (SPN 5080) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26556 |  | 326557 | 04 |  | Engine Throttle position 2 (Kingbang) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26557 |  | 326558 | 04 |  | Aftertreatment 2 Intake %O2 (SPN 3256) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26558 | 7 | 326559 | 04 |  | Engine Over Temperature - Coolant Pre-Warning (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 6 | 326559 | 04 |  | Engine Over Temperature - Coolant Warning (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 5 | 326559 | 04 |  | Engine Overspeed (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 4 | 326559 | 04 |  | Engine High Oil Temperature (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 3 | 326559 | 04 |  | Engine Oil Low Pressure (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 2 | 326559 | 04 |  | Low oil pressure (VecV E694) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 1 | 326559 | 04 |  | High coolant temperature (VecV E694) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 0 | 326559 | 04 |  | Engine Oil Change (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 7 | 326560 | 04 |  | DEF Level Fill Operator Warning lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 6 | 326560 | 04 |  | DEF Level Mid Level Inducement lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 5 | 326560 | 04 |  | DEF Level Severe Inducement lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 4 | 326560 | 04 |  | HC burn off lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 3 | 326560 | 04 |  | Fuel Filter Clogging lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 2 | 326560 | 04 |  | Air Filter Clogging lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 1 | 326560 | 04 |  | DEF Warning lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 0 | 326560 | 04 |  | DEF Shutdown lamp (FPT Stage V) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26560 | 7 | 326561 | 04 |  | AdBlue lamp (VecV E694) | BOOL | [5 empty] | X | X | X
EIC measurements value | 26561 |  | 326562 | 04 |  | Diesel Particulate Filter Active Regeneration Forced Status (SPN 4175) | INT16u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26562 |  | 326563 | 04 |  | Engine Total Fuel Consumption Liquid (SPN 5054) RAW | INT32u | AB | 0 |  |  |  | X | X | X
EIC measurements value | 26564 |  | 326565 | 04 |  | Transmission Oil Pressure 1 (SPN 127) | INT16u | AB | 1 |  |  |  | X | X | X
EIC measurements value | 26565 |  | 326566 | 04 |  | Fuel rail pressure (Wise10) | INT32u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26567 |  | 326568 | 04 |  | Downstream fuel filter pressure (Wise10) | INT32u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26569 |  | 326570 | 04 |  | Intake post air filter pressure (Wise10) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26570 |  | 326571 | 04 |  | Fuel pressure pre filter (Wise10) | INT32u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26572 |  | 326573 | 04 |  | Fuel pressure post filter (Wise10) | INT32u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26574 |  | 326575 | 04 |  | Pre filter oil pressure (Wise10) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26575 |  | 326576 | 04 |  | Post filter oil pressure (Wise10) | INT16u | AB | 0 | bar/psi |  |  | X | X | X
EIC measurements value | 26576 |  | 326577 | 04 |  | Pre turbo exhaust gas temperature A (Wise10) | INT16u | AB | 0 | degC/degF |  |  | X | X | X
EIC measurements value | 26577 |  | 326578 | 04 |  | Pre turbo exhaust gas temperature B (Wise10) | INT16u | AB | 0 | degC/degF |  |  | X | X | X
EIC measurements value | 26578 |  | 326579 | 04 |  | Fuel temperature (Wise10) | INT32u | AB | 0 | degC/degF |  |  | X | X | X
EIC measurements value | 26580 |  | 326581 | 04 |  | Low temperature coolant temperature (Wise10) | INT16u | AB | 0 | degC/degF |  |  | X | X | X
EIC measurements validity | 26296 | 15 | 326297 | 04 |  | DPF lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 14 | 326297 | 04 |  | DPF lamp ON solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 13 | 326297 | 04 |  | DPF lamp ON blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 12 | 326297 | 04 |  | DPF Active Regeneration not activated Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 11 | 326297 | 04 |  | DPF Active Regeneration activated Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 10 | 326297 | 04 |  | DPF Active Regeneration needed Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 9 | 326297 | 04 |  | DPF Regeneration not needed Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26296 | 8 | 326297 | 04 |  | DPF Regeneration needed Lowest Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 15 | 326298 | 04 |  | DPF Regeneration needed Moderate Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 14 | 326298 | 04 |  | DPF Regeneration needed Highest Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 13 | 326298 | 04 |  | DPF Regeneration Not Inhibit Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 12 | 326298 | 04 |  | DPF Regeneration Inhibit Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 11 | 326298 | 04 |  | Exhaust system high temperature OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 10 | 326298 | 04 |  | Exhaust system high temperature ON Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 9 | 326298 | 04 |  | MTU limit lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26297 | 8 | 326298 | 04 |  | MTU limit lamp ON solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 15 | 326299 | 04 |  | MTU limit lamp ON blink 1Hz Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 14 | 326299 | 04 |  | DEF level low lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 13 | 326299 | 04 |  | DEF level low lamp ON solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 12 | 326299 | 04 |  | DEF level low lamp ON blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 11 | 326299 | 04 |  | After run status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 10 | 326299 | 04 |  | Volvo Penta Scr Inducement not ACTIVE Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 9 | 326299 | 04 |  | Volvo Penta Scr Inducement WARNING Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26298 | 8 | 326299 | 04 |  | EMPTY validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 15 | 326300 | 04 |  | Volvo Penta Scr Derate ACTIVE Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 14 | 326300 | 04 |  | Volvo Penta Pre severe Derate WARNING Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 13 | 326300 | 04 |  | Volvo Penta Severe Derate Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 12 | 326300 | 04 |  | Volvo Penta Temperature Override Derate Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 11 | 326300 | 04 |  | Volvo Penta Scr Inducement Reason OK Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 10 | 326300 | 04 |  | Volvo Penta Reagent Tank low Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 9 | 326300 | 04 |  | Volvo Penta Incorrect Reagent Quality Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26299 | 8 | 326300 | 04 |  | Volvo Penta Absence of Reagent Dosing Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 15 | 326301 | 04 |  | MTU TIER4 lamp ON blink 2Hz Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 14 | 326301 | 04 |  | MTU buzzer lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 13 | 326301 | 04 |  | MTU buzzer lamp ON solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 12 | 326301 | 04 |  | MTU buzzer lamp ON blink 1Hz Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 11 | 326301 | 04 |  | MTU buzzer lamp ON blink 2Hz Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 10 | 326301 | 04 |  | Alarm Yellow lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 9 | 326301 | 04 |  | Alarm Yellow lamp ON Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26300 | 8 | 326301 | 04 |  | Alarm Red lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 15 | 326302 | 04 |  | Alarm Red lamp ON Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 14 | 326302 | 04 |  | Engine fuel leak Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 13 | 326302 | 04 |  | Engine Wait to start Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 12 | 326302 | 04 |  | Engine Protect system shutdown Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 11 | 326302 | 04 |  | Engine Protect system appro shutdown Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 10 | 326302 | 04 |  | Engine alarm acknowledg Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 9 | 326302 | 04 |  | Engine ait shutoff command status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26301 | 8 | 326302 | 04 |  | Engine overspeed test Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 15 | 326303 | 04 |  | Engine shutoff status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 14 | 326303 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 13 | 326303 | 04 |  | Manual purge EIDSS Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 12 | 326303 | 04 |  | Force purge Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 11 | 326303 | 04 |  | JCB Amber blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 10 | 326303 | 04 |  | JCB Amber solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 9 | 326303 | 04 |  | JCB Red blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26302 | 8 | 326303 | 04 |  | JCB Red solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 15 | 326304 | 04 |  | JCB Engine emission system failure warning Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 14 | 326304 | 04 |  | JCB Engine emission system failure low Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 13 | 326304 | 04 |  | JCB Engine emission system failure high Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 12 | 326304 | 04 |  | JCB Particulate filter restricted high Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 11 | 326304 | 04 |  | JCB Particulate filter restricted very high Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 10 | 326304 | 04 |  | JCB Particulate filter restricted critical Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 9 | 326304 | 04 |  | DPF lamp - fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26303 | 8 | 326304 | 04 |  | DEF low level - Fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 15 | 326305 | 04 |  | Red lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 14 | 326305 | 04 |  | Red lamp solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 13 | 326305 | 04 |  | Red lamp blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 12 | 326305 | 04 |  | Red lamp fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 11 | 326305 | 04 |  | Yellow lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 10 | 326305 | 04 |  | Yellow lamp solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 9 | 326305 | 04 |  | Yellow lamp blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26304 | 8 | 326305 | 04 |  | Yellow lamp fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 15 | 326306 | 04 |  | MIL lamp OFF Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 14 | 326306 | 04 |  | MIL lamp solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 13 | 326306 | 04 |  | MIL lamp blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 12 | 326306 | 04 |  | MIL lamp fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 11 | 326306 | 04 |  | Engine emission system failure lamp off Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 10 | 326306 | 04 |  | Engine emission system failure lamp solid Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 9 | 326306 | 04 |  | Engine emission system failure lamp blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26305 | 8 | 326306 | 04 |  | Engine emission system failure lamp fast blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 15 | 326307 | 04 |  | DPF Regeneration Not Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 14 | 326307 | 04 |  | DPF Regeneration Inhibit Park Brake Not Set Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 13 | 326307 | 04 |  | DPF Regeneration Not Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 12 | 326307 | 04 |  | DPF Regeneration Inhibit Out Of Neutral Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 11 | 326307 | 04 |  | Engine Running (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 10 | 326307 | 04 |  | Service Delay (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 9 | 326307 | 04 |  | Pre-glow Active (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26306 | 8 | 326307 | 04 |  | Oil Pressure Missing (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 15 | 326308 | 04 |  | Engine Diagnostic Lamp (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 14 | 326308 | 04 |  | Engine Overtemperature (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 13 | 326308 | 04 |  | Air Filter Switch (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 12 | 326308 | 04 |  | Transmission Neutral Switch (SPN 604) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 11 | 326308 | 04 |  | Parking Brake Switch (SPN 70) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26307 | 10 | 326308 | 04 |  | Brake Switch (SPN 597) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 14 | 326310 | 04 |  | Exhaust Over Heat Condition (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 13 | 326310 | 04 |  | Engine Over Speed Warning (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 12 | 326310 | 04 |  | Urea Thawing Mode Active (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 11 | 326310 | 04 |  | Scr Injector Overheat Protection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 10 | 326310 | 04 |  | Turbo Charger Protection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 9 | 326310 | 04 |  | Engine Protection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26309 | 8 | 326310 | 04 |  | Water in Fuel Detection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 15 | 326311 | 04 |  | Fuel in Oil Detection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 14 | 326311 | 04 |  | Low Catalyst Efficiency (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 13 | 326311 | 04 |  | Bad Urea Quality (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 12 | 326311 | 04 |  | Nh3 Slip Detection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 11 | 326311 | 04 |  | Engine Oil Over Temperature (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 10 | 326311 | 04 |  | Smoke Limitation (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 9 | 326311 | 04 |  | Clogged DPF (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26310 | 8 | 326311 | 04 |  | Oil switch (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 15 | 326355 | 04 |  | Evaporation Not Required (Scania S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 14 | 326355 | 04 |  | Evaporation Required Less Urgent (Scania S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 13 | 326355 | 04 |  | Evaporation Required Urgent (Scania S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 12 | 326355 | 04 |  | Evaporation Is In Progress (Scania S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 11 | 326355 | 04 |  | Isolation Fault (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 10 | 326355 | 04 |  | Isolation Warning (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 9 | 326355 | 04 |  | Isolation Timeout (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26354 | 8 | 326355 | 04 |  | Turbo heat protection (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 15 | 326356 | 04 |  | Doosan stage 5 ash lamp status > 100% Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 14 | 326356 | 04 |  | Doosan stage 5 ash lamp status 100%-105% Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 13 | 326356 | 04 |  | Doosan stage 5 ash lamp status 106%-110% Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 12 | 326356 | 04 |  | Doosan stage 5 ash lamp status 111%-120% Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 11 | 326356 | 04 |  | Doosan stage 5 ash lamp status < 121% Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 10 | 326356 | 04 |  | DPF Thermal Management Active (SPN 5399) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 9 | 326356 | 04 |  | SCR Thermal Management Active (SPN 5400) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26355 | 8 | 326356 | 04 |  | SCR System Cleaning Status (SPN 6916) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 15 | 326358 | 04 |  | SCR System Cleaning Inhibited Status (SPN 6917) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 14 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Inhibit Switch (SPN 6918) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 13 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Low Exhaust Temperature (SPN 6926) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 12 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to System Fault Active (SPN 6927) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 11 | 326358 | 04 |  | SCR System Cleaning Inhibited Due to Engine Not Warmed Up (SPN 6931) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 10 | 326358 | 04 |  | Yanmar Stage V Accelerator Interlock Switch feedback Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 9 | 326358 | 04 |  | Yanmar Stage V DPF regenaration acknowledge lamp Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26357 | 8 | 326358 | 04 |  | DEF low level -Slow blink Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 15 | 326559 | 04 |  | Engine Over Temperature - Coolant Pre-Warning (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 14 | 326559 | 04 |  | Engine Over Temperature - Coolant Warning (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 13 | 326559 | 04 |  | Engine Overspeed (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 12 | 326559 | 04 |  | Engine High Oil Temperature (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 11 | 326559 | 04 |  | Engine Oil Low Pressure (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 10 | 326559 | 04 |  | Low oil pressure (VecV E694) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 9 | 326559 | 04 |  | High coolant temperature (VecV E694) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26558 | 8 | 326559 | 04 |  | Engine Oil Change (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 15 | 326560 | 04 |  | DEF Level Fill Operator Warning lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 14 | 326560 | 04 |  | DEF Level Mid Level Inducement lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 13 | 326560 | 04 |  | DEF Level Severe Inducement lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 12 | 326560 | 04 |  | HC burn off lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 11 | 326560 | 04 |  | Fuel Filter Clogging lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 10 | 326560 | 04 |  | Air Filter Clogging lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 9 | 326560 | 04 |  | DEF Warning lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26559 | 8 | 326560 | 04 |  | DEF Shutdown lamp (FPT Stage V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26560 | 15 | 326561 | 04 |  | AdBlue lamp (VecV E694) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 15 | 326901 | 04 |  | Engine Speed (SPN 190) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 14 | 326901 | 04 |  | Engine Coolant Temperature (SPN 110) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 13 | 326901 | 04 |  | Engine Oil Pressure (SPN 100) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 12 | 326901 | 04 |  | Active Diagnostic Trouble Code Count (SPN 1218) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 11 | 326901 | 04 |  | Engine Oil Temperature 1 (SPN 175) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 10 | 326901 | 04 |  | Engine Fuel 1 Temperature 1 (SPN 174) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 9 | 326901 | 04 |  | Engine Intake Manifold #1 Pressure (SPN 102) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 8 | 326901 | 04 |  | Engine Intake 1 Air Temperature (SPN 172) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 7 | 326901 | 04 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 6 | 326901 | 04 |  | Engine Fuel Rate (SPN 183) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 5 | 326901 | 04 |  | Charge air pressure (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 4 | 326901 | 04 |  | Engine Intake Manifold 1 Temperature (SPN 105) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 3 | 326901 | 04 |  | Driver's Demand Engine, Percent Torque (SPN 512) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 2 | 326901 | 04 |  | Actual Engine, Percent Torque (SPN 513) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 1 | 326901 | 04 |  | Accelerator Pedal Position 1 (SPN 91) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26900 | 0 | 326901 | 04 |  | Engine Percent Load At Current Speed (SPN 92) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 15 | 326902 | 04 |  | Engine Intake Air Pressure (SPN 106) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 14 | 326902 | 04 |  | Engine Exhaust Temperature (SPN 173) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 13 | 326902 | 04 |  | Engine Total Hours of Operation (SPN 247) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 11 | 326902 | 04 |  | Engine Oil Filter Differential Pressure (SPN 99) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 10 | 326902 | 04 |  | Key Switch Battery Potential (SPN 158) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 9 | 326902 | 04 |  | Engine Fuel Delivery Pressure (SPN 94) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 8 | 326902 | 04 |  | Engine Oil Level (SPN 98) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 7 | 326902 | 04 |  | Engine Crankcase Pressure 1 (SPN 101) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 6 | 326902 | 04 |  | Engine Coolant Pressure 1 (SPN 109) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 5 | 326902 | 04 |  | Water In Fuel Indicator 1 (SPN 97) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 4 | 326902 | 04 |  | Engine Turbocharger 1 Oil Temperature (SPN 176) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 3 | 326902 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Pressure (SPN 81) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 2 | 326902 | 04 |  | Engine Air Filter 1 Differential Pressure (SPN 107) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 1 | 326902 | 04 |  | Engine Coolant Filter Differential Pressure (SPN 112) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26901 | 0 | 326902 | 04 |  | Barometric Pressure (SPN 108) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 15 | 326903 | 04 |  | Ambient Air Temperature (SPN 171) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 14 | 326903 | 04 |  | Engine Exhaust Manifold Bank 2 Temperature 1 (SPN 2433) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 13 | 326903 | 04 |  | Engine Exhaust Manifold Bank 1 Temperature 1 (SPN 2434) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 12 | 326903 | 04 |  | Temp. Winding 1 (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 11 | 326903 | 04 |  | Temp. Winding 2 (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 10 | 326903 | 04 |  | Temp. Winding 3 (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 9 | 326903 | 04 |  | Auxiliary_Analog_Info (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 8 | 326903 | 04 |  | Auxiliary_Analog_Info Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 7 | 326903 | 04 |  | Engine Turbocharger 1 Compressor Outlet Temperature (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 6 | 326903 | 04 |  | Engine Intercooler Temperature (SPN 52) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 5 | 326903 | 04 |  | Engine Trip Fuel (SPN 182) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 3 | 326903 | 04 |  | Engine Total Fuel Used (SPN 250) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26902 | 1 | 326903 | 04 |  | Trip Fuel (Gaseous) (SPN 1039) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 15 | 326904 | 04 |  | Total Fuel Used (Gaseous) (SPN 1040) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 13 | 326904 | 04 |  | Trip Average Fuel Rate (SPN 1029) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 12 | 326904 | 04 |  | Engine Rated Power (SPN 166) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 11 | 326904 | 04 |  | Engine power (ADEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 10 | 326904 | 04 |  | Engine Intake Manifold #1 Absolute Pressure (SPN 3563) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 9 | 326904 | 04 |  | Diesel Particulate Filter Lamp Command (SPN 3697) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 8 | 326904 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Inhibit Switch (SPN 3703) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 7 | 326904 | 04 |  | Aftertreatment Diesel Particulate Filter Active Regeneration Status (SPN 3700) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 6 | 326904 | 04 |  | Aftertreatment Diesel Particulate Filter Status (SPN 3701) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 5 | 326904 | 04 |  | Exhaust System High Temperature Lamp Command (SPN 3698) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 4 | 326904 | 04 |  | Engine Air Filter 2 Differential Pressure (SPN 2809) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 3 | 326904 | 04 |  | Engine Fuel Supply Pump Intake Absolute Pressure (SPN 1381) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 2 | 326904 | 04 |  | Engine Fuel Filter (suction side) Differential Pressure (SPN 1382) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 1 | 326904 | 04 |  | Engine Fuel Filter Differential Pressure (SPN 95) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26903 | 0 | 326904 | 04 |  | Speed demand Source (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 15 | 326905 | 04 |  | P-Lube Oil Limit LO (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 14 | 326905 | 04 |  | P-Lube Oil Limit LOLO (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 13 | 326905 | 04 |  | P-Fuel (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 12 | 326905 | 04 |  | T-Coolant Limit HI (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 11 | 326905 | 04 |  | T-Coolant Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 10 | 326905 | 04 |  | T-Coolant Intercooler (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 9 | 326905 | 04 |  | Engine ECU Temperature (SPN 1136) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 8 | 326905 | 04 |  | Actual Droop (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 7 | 326905 | 04 |  | Injection Quantity Act.DBR % (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 6 | 326905 | 04 |  | Engine Speed Camshaft (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 5 | 326905 | 04 |  | T-Lube Oil Limit HI (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 4 | 326905 | 04 |  | T-Lube Oil Limit HIHI (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 3 | 326905 | 04 |  | Feedback Speed Demand analog (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 2 | 326905 | 04 |  | Stop signal active (MDEC) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 1 | 326905 | 04 |  | Exhaust Port Temperature 01 (SPN 1137) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26904 | 0 | 326905 | 04 |  | Exhaust Port Temperature 02 (SPN 1138) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 15 | 326906 | 04 |  | Exhaust Port Temperature 03 (SPN 1139) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 14 | 326906 | 04 |  | Exhaust Port Temperature 04 (SPN 1140) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 13 | 326906 | 04 |  | Exhaust Port Temperature 05 (SPN 1141) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 12 | 326906 | 04 |  | Exhaust Port Temperature 06 (SPN 1142) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 11 | 326906 | 04 |  | Exhaust Port Temperature 07 (SPN 1143) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 10 | 326906 | 04 |  | Exhaust Port Temperature 08 (SPN 1144) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 9 | 326906 | 04 |  | Exhaust Port Temperature 09 (SPN 1145) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 8 | 326906 | 04 |  | Exhaust Port Temperature 10 (SPN 1146) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 7 | 326906 | 04 |  | Exhaust Port Temperature 11 (SPN 1147) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 6 | 326906 | 04 |  | Exhaust Port Temperature 12 (SPN 1148) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 5 | 326906 | 04 |  | Exhaust Port Temperature 13 (SPN 1149) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 4 | 326906 | 04 |  | Exhaust Port Temperature 14 (SPN 1150) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 3 | 326906 | 04 |  | Exhaust Port Temperature 15 (SPN 1151) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 2 | 326906 | 04 |  | Exhaust Port Temperature 16 (SPN 1152) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 1 | 326906 | 04 |  | Engine Filtered Fuel Delivery Pressure (SPN 5579) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26905 | 0 | 326906 | 04 |  | Engine Coolant Temperature 2 (SPN 4076) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 15 | 326907 | 04 |  | Engine Coolant Temperature 3 (SPN 6209) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 14 | 326907 | 04 |  | Engine Coolant Pump Outlet Temperature (SPN 4193) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 13 | 326907 | 04 |  | Engine Auxiliary Coolant Temperature (SPN 1212) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 12 | 326907 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature (SPN 1180) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 11 | 326907 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature (SPN 1181) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 10 | 326907 | 04 |  | Engine Auxiliary Coolant Pressure (SPN 1203) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 9 | 326907 | 04 |  | Specific Humidity (SPN 4490) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 8 | 326907 | 04 |  | Engine Turbocharger 2 Speed (SPN 1169) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 7 | 326907 | 04 |  | Engine Turbocharger 3 Speed (SPN 1170) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 6 | 326907 | 04 |  | Trip Engine Running Time (SPN 1036) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 4 | 326907 | 04 |  | Trip Idle Time (SPN 1037) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 2 | 326907 | 04 |  | Engine Fan 1 Estimated Percent Speed (SPN 975) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 1 | 326907 | 04 |  | Engine Turbocharger 1 Speed (SPN 103) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26906 | 0 | 326907 | 04 |  | Nominal Friction - Percent Torque (SPN 514) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 15 | 326908 | 04 |  | Engine's Desired Operating Speed (SPN 515) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 14 | 326908 | 04 |  | Engine Intake Manifold 2 Temperature (SPN 1131) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 13 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Volume (SPN 1761) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 12 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature 1 (SPN 3031) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 11 | 326908 | 04 |  | Aftertreatment 1 SCR Intake NOx 1 (SPN 3216) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 10 | 326908 | 04 |  | Aftertreatment 1 Outlet NOx 1 (SPN 3226) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 9 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4331) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 8 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4334) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 7 | 326908 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve (SPN 4336) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 6 | 326908 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4348) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 5 | 326908 | 04 |  | Aftertreatment 1 SCR Intake Temperature (SPN 4360) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 4 | 326908 | 04 |  | Aftertreatment 1 SCR Outlet Temperature (SPN 4363) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 3 | 326908 | 04 |  | Aftertreatment 2 SCR Intake NOx 1 (SPN 3255) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 2 | 326908 | 04 |  | Aftertreatment 2 Outlet NOx 1 (SPN 3265) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 1 | 326908 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity (SPN 4384) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26907 | 0 | 326908 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Absolute Pressure (SPN 4387) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 15 | 326909 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser 1 Temperature (SPN 4390) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 14 | 326909 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity (SPN 4401) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 13 | 326909 | 04 |  | Aftertreatment 2 SCR Intake Temperature (SPN 4413) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 12 | 326909 | 04 |  | Aftertreatment 2 SCR Outlet Temperature (SPN 4415) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 11 | 326909 | 04 |  | Engine Oil Filter Outlet Pressure (SPN 3549) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 10 | 326909 | 04 |  | Engine Operating State (SPN 3543) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 9 | 326909 | 04 |  | Source Address of Controlling Device for Engine Control (SPN 1483) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 8 | 326909 | 04 |  | Engine Rated Speed (SPN 189) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 7 | 326909 | 04 |  | Engine Speed At Idle, Point 1 (SPN 188) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 6 | 326909 | 04 |  | Fuel Consumption g/KWh (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 5 | 326909 | 04 |  | Engine Status of Start procedure (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 4 | 326909 | 04 |  | Exhaust Port Temperature 17 (SPN 1153) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 3 | 326909 | 04 |  | Exhaust Port Temperature 18 (SPN 1154) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 2 | 326909 | 04 |  | Exhaust Port Temperature 19 (SPN 1155) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 1 | 326909 | 04 |  | Exhaust Port Temperature 20 (SPN 1156) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26908 | 0 | 326909 | 04 |  | UREA Level (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 15 | 326910 | 04 |  | Aftertreatment SCR Operator Inducement Severity (SPN 5246) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 14 | 326910 | 04 |  | Aftertreatment Diesel Exhaust Fluid Tank Low Level Indicator (SPN 5245) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 13 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Temperature (SPN 3246) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 12 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time to Next Active Regeneration (SPN 5978) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 10 | 326910 | 04 |  | Engine Charge Air Cooler 1 Outlet Temperature (SPN 2630) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 9 | 326910 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Soot Load Percent (SPN 3719) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 8 | 326910 | 04 |  | Purging Active (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 7 | 326910 | 04 |  | Limit Lamp Status (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 6 | 326910 | 04 |  | Battery Charger 1 Output Voltage (SPN 4992) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 5 | 326910 | 04 |  | Battery Charger 1 Output Current (SPN 4993) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 4 | 326910 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption (SPN 3829) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 3 | 326910 | 04 |  | Time left to torque reduction (Volvo) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 2 | 326910 | 04 |  | Time left to servere torque reduction (Volvo) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 1 | 326910 | 04 |  | SCR inducement severity (Volvo) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26909 | 0 | 326910 | 04 |  | SCR inducement reason (Volvo) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 15 | 326911 | 04 |  | Engine Derate Request (SPN 3644) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 14 | 326911 | 04 |  | Engine Demand, Percent Torque (SPN 2432) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 13 | 326911 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 (SPN 3217) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 12 | 326911 | 04 |  | Aftertreatment 1 Outlet Percent Oxygen 1 (SPN 3227) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 11 | 326911 | 04 |  | Engine Throttle Actuator 1 Control Command (SPN 3464) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 10 | 326911 | 04 |  | Long-term Fuel Trim - Bank 1 (SPN 4237) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 9 | 326911 | 04 |  | Short-term Fuel Trim - Bank 1 (SPN 4236) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 8 | 326911 | 04 |  | Engine Exhaust Bank 1 O2 Sensor Closed Loop Operation (SPN 4240) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 7 | 326911 | 04 |  | Engine Desired Ignition Timing 1 (SPN 1433) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 6 | 326911 | 04 |  | Engine Actual Ignition Timing (SPN 1436) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 5 | 326911 | 04 |  | EDC4 CAN Status (EMR) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 4 | 326911 | 04 |  | Engine Starter Mode (SPN 1675) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 3 | 326911 | 04 |  | Actual Maximum Available Engine - Percent Torque (SPN 3357) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 2 | 326911 | 04 |  | Engine Coolant Pre-heated State (SPN 3553) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 1 | 326911 | 04 |  | Engine Safety and Protection Override Status (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26910 | 0 | 326911 | 04 |  | Engine Cylinder Cut-off (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 15 | 326912 | 04 |  | Engine Running State (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 14 | 326912 | 04 |  | External Stop State (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 13 | 326912 | 04 |  | Requested Absolute Torque (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 12 | 326912 | 04 |  | Source of Current Speed Demand (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 11 | 326912 | 04 |  | Engine Demanded Operating Speed (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 10 | 326912 | 04 |  | Feedback of Speed Demand CAN (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 9 | 326912 | 04 |  | Feedback of Speed Demand Analogue Input (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 8 | 326912 | 04 |  | Speed Demand Fail Mode (MTU) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 7 | 326912 | 04 |  | Engine Shutdown Override Switch (SPN 1237) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 6 | 326912 | 04 |  | Engine Requested Speed (SPN 898) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 5 | 326912 | 04 |  | Escape Mode Enable Flag (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 4 | 326912 | 04 |  | Inducement Timer (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 3 | 326912 | 04 |  | Inducement Level (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 2 | 326912 | 04 |  | Urea Tank Level (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 1 | 326912 | 04 |  | Urea Tank Level Indicator (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26911 | 0 | 326912 | 04 |  | Level Indicator (Amber) Action (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 15 | 326913 | 04 |  | DPF Amber Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 14 | 326913 | 04 |  | EXH.SYSTEM lamp (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 13 | 326913 | 04 |  | DPF Green Lamp Mode (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 12 | 326913 | 04 |  | NO POWER Lamp (Isuzu) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 11 | 326913 | 04 |  | Engine Intake Manifold 3 Temperature (SPN 1132) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 10 | 326913 | 04 |  | Engine Intake Manifold 4 Temperature (SPN 1133) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 9 | 326913 | 04 |  | Engine Oil Filter Intake Pressure (SPN 1208) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 8 | 326913 | 04 |  | Engine Turbocharger 2 Boost Pressure (SPN 1128) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 7 | 326913 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure (SPN 157) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 6 | 326913 | 04 |  | Battery Potential / Power Input 1 (SPN 168) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 5 | 326913 | 04 |  | Dosing Module Status (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 4 | 326913 | 04 |  | Actual Reducing Agent Quantity (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 3 | 326913 | 04 |  | Aftertreatment Lamp (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 2 | 326913 | 04 |  | Refresh Status Byte (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 1 | 326913 | 04 |  | SCR Monitor (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26912 | 0 | 326913 | 04 |  | Successful Running Refreshes (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 15 | 326914 | 04 |  | Successful Stationary Refreshes (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 14 | 326914 | 04 |  | Engine Rating (JCB) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 13 | 326914 | 04 |  | Aftertreatment 1 Exhaust Temperature 1 (SPN 3241) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 12 | 326914 | 04 |  | Humidity Derate Percentage (Perkins/CAT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 11 | 326914 | 04 |  | Engine Emergency (Immediate) Shutdown Indication (SPN 3607 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 10 | 326914 | 04 |  | Number of EIO Activations (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 9 | 326914 | 04 |  | Accumulated EIO time (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 8 | 326914 | 04 |  | Time left of EIO Operation (Volvo EMS2.4) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 7 | 326914 | 04 |  | Remaining Service Hours (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 6 | 326914 | 04 |  | Wheel Based Vehicle Speed (SPN 84) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 5 | 326914 | 04 |  | Aftertreatment 1 Exhaust Gas Mass Flow Rate (SPN 3236) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 4 | 326914 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Differential Pressure (SPN 3251) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 3 | 326914 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 2 | 326914 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intake Temperature (SPN 3242) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 1 | 326914 | 04 |  | Phys. Injection quantity (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26913 | 0 | 326914 | 04 |  | Phys. Torque (Hatz) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26914 | 15 | 326915 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral (SPN 3708) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26914 | 14 | 326915 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set (SPN 3710) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26914 | 13 | 326915 | 04 |  | Engine Coolant Level 1 (SPN 111) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26914 | 12 | 326915 | 04 |  | Operator Inducement Time to Torque Derate Level 2 (SPN 7428) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26914 | 11 | 326915 | 04 |  | Alternator 1 Status (SPN 3353) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26915 | 3 | 326916 | 04 |  | Engine Throttle Valve 1 Position 1 (SPN 51) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26915 | 2 | 326916 | 04 |  | Engine Fuel Valve 1 Intake Absolute Pressure (SPN 1390) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26915 | 1 | 326916 | 04 |  | Engine Turbocharger 1 Boost Pressure (SPN 1127) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26915 | 0 | 326916 | 04 |  | Engine Cylinder 1 Ignition Timing (SPN 1413) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 15 | 326917 | 04 |  | Engine Intake Air Mass Flow Rate (SPN 132) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 14 | 326917 | 04 |  | Engine Lambda (Yuchai) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 13 | 326917 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent (SPN 3720) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 12 | 326917 | 04 |  | DPF Regeneration State (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 11 | 326917 | 04 |  | DPF Regeneration Countdown Timer (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 10 | 326917 | 04 |  | DEF Level (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 9 | 326917 | 04 |  | DEF Quality (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 8 | 326917 | 04 |  | DEF Technical Failure (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 7 | 326917 | 04 |  | Cold Start Heater Status (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 6 | 326917 | 04 |  | Fuel Filter Heater Status (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 5 | 326917 | 04 |  | Low Idle Increase Desired (FPT) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 4 | 326917 | 04 |  | Urea level inducement state (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 3 | 326917 | 04 |  | Emission-OBD inducement state (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 2 | 326917 | 04 |  | Emission-OBD inducement failure reason (Scania) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 1 | 326917 | 04 |  | Engine Diesel Particulate Filter Regeneration State (JDEC STAGE V) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26916 | 0 | 326917 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration (SPN 3516) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 15 | 326918 | 04 |  | Engine Requested Fuel Valve 1 Position (SPN 1765) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 14 | 326918 | 04 |  | Engine Oil Priming State (SPN 3551) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 13 | 326918 | 04 |  | Fuel Pump Primer Status (SPN 4083) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 12 | 326918 | 04 |  | Sensor supply voltage 1 (SPN 3509) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 11 | 326918 | 04 |  | Sensor supply voltage 2 (SPN 3510) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 10 | 326918 | 04 |  | Accelerator Pedal Position 2 (SPN 29) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 9 | 326918 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 8 | 326918 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 7 | 326918 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 6 | 326918 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 5 | 326918 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 4 | 326918 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 3 | 326918 | 04 |  | Feedback Engine Fueling State (SPN 5794) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 2 | 326918 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 1 | 326918 | 04 |  | Blowby flow (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26917 | 0 | 326918 | 04 |  | Fuel rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 15 | 326919 | 04 |  | Timing rail pressure (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 14 | 326919 | 04 |  | Aftercooler water inlet temperature (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 13 | 326919 | 04 |  | Fuel Rank position left (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 12 | 326919 | 04 |  | Fuel Rank position right (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 11 | 326919 | 04 |  | Intake Manifold pressure left (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 10 | 326919 | 04 |  | Intake Manifold pressure right (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 9 | 326919 | 04 |  | Intake Manifold Temperature left (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 8 | 326919 | 04 |  | Intake Manifold Temperature right (Cummins H6) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 7 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 6 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 5 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 4 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 3 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 2 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 1 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26918 | 0 | 326919 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 15 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 14 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 13 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 12 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 11 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 10 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 9 | 326920 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 8 | 326920 | 04 |  | Trip Average Fuel Rate (SPN 1029) RAW Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 6 | 326920 | 04 |  | Engine Trip Fuel (SPN 182) RAW Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 4 | 326920 | 04 |  | Engine Total Fuel Used (SPN 250) RAW Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 2 | 326920 | 04 |  | Engine Controlled Shutdown Request (SPN 5795) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 1 | 326920 | 04 |  | Engine Oil Pre-Heated State (SPN 3552) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26919 | 0 | 326920 | 04 |  | Engine Ventilation Status (SPN 3554) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 15 | 326921 | 04 |  | Rail pressure (Jichai) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 14 | 326921 | 04 |  | Engine Actual Exhaust 1 Oxygen (SPN 1119) Validity | INT16u | AB |  |  |  |  | X | X | X
EIC measurements validity | 26920 | 13 | 326921 | 04 |  | Jichai WYS Fault code 1.1 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 12 | 326921 | 04 |  | Jichai WYS Fault code 1.2 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 11 | 326921 | 04 |  | Jichai WYS Fault code 1.3 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 10 | 326921 | 04 |  | Jichai WYS Fault code 1.4 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 9 | 326921 | 04 |  | Jichai WYS Fault code 2.1 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 8 | 326921 | 04 |  | Jichai WYS Fault code 2.2 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 7 | 326921 | 04 |  | Jichai WYS Fault code 2.3 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 6 | 326921 | 04 |  | Jichai WYS Fault code 2.4 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 5 | 326921 | 04 |  | Jichai Engine torque Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 4 | 326921 | 04 |  | Jichai Engine reference torque Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 3 | 326921 | 04 |  | Jichai Oil pressure of boost Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 2 | 326921 | 04 |  | Jichai Oil pressure after filtration Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 1 | 326921 | 04 |  | Jichai High temperature water inlet temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26920 | 0 | 326921 | 04 |  | Jichai Cooler inlet water temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 15 | 326922 | 04 |  | Jichai Engine status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 14 | 326922 | 04 |  | Jichai Engine target speed Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 13 | 326922 | 04 |  | Engine Fuel Valve 1 Position (SPN 1442) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 12 | 326922 | 04 |  | Engine Gaseous Fuel Supply Pressure 1 (SPN 159) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 11 | 326922 | 04 |  | Fuel Injection Quantity (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 10 | 326922 | 04 |  | Regeneration Status (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 9 | 326922 | 04 |  | Ash Accumulation Time (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 7 | 326922 | 04 |  | Operator Inducement Reason (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 6 | 326922 | 04 |  | Operator Inducement Severity (Kubota) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 5 | 326922 | 04 |  | HC Evaporation Status (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 4 | 326922 | 04 |  | HC Evaporation Required Action (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 3 | 326922 | 04 |  | HC Evaporation Progress Countdown Timer (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 2 | 326922 | 04 |  | HC Evaporation Action Start Countdown Timer (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 1 | 326922 | 04 |  | Sulphur Regeneration request (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26921 | 0 | 326922 | 04 |  | deSOx heatup request (Scania EMS2 S8) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 15 | 326923 | 04 |  | Insulation resistance (KWG ISO5 isolation monitor) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 13 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 12 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 11 | 326923 | 04 |  | Doosan stage 5 ash lamp status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 10 | 326923 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 9 | 326923 | 04 |  | SCR System Cleaning Lamp Command (SPN 6915) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 8 | 326923 | 04 |  | SCR System Cleaning Forced Status (SPN 6934) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 7 | 326923 | 04 |  | JiChai JC15T JG Fuel Valve Self-Adjust Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 6 | 326923 | 04 |  | JiChai JC15T JG Fuel Valve CloseLoop-Adjust Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 5 | 326923 | 04 |  | JiChai JC15T JG Air Fuel Ratio Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 4 | 326923 | 04 |  | JiChai JC15T JG Natural Gas Temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 3 | 326923 | 04 |  | JiChai JC15T JG PHI Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 2 | 326923 | 04 |  | JiChai JC15T JG Natural Gas Pressure Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 1 | 326923 | 04 |  | JiChai JC15T JG Gas Supply Amount Per Second Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 0 | 326923 | 04 |  | Doosan stage 5 Emission OBD Inducement lamp status Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 15 | 326924 | 04 |  | Doosan stage 5 Emission OBD lamp failure reason Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 14 | 326923 | 04 |  | Engine Fuel Valve 1 Differential Pressure Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 13 | 326923 | 04 |  | Engine Fuel Flow Rate 1 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26922 | 12 | 326923 | 04 |  | Weichai Engine Oil Pressure Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 11 | 326924 | 04 |  | Weichai Engine Oil Pressure Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 10 | 326924 | 04 |  | Weichai Pre-throttle Pressure 1 Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 9 | 326924 | 04 |  | Weichai Throttle 1 Position Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 8 | 326924 | 04 |  | Weichai Throttle 2 Position Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 7 | 326924 | 04 |  | Weichai Bypass Valve 1 Position Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 6 | 326924 | 04 |  | Weichai Altronic RPM Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 5 | 326924 | 04 |  | Weichai Altronic Supply Voltage Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 4 | 326924 | 04 |  | Weichai Relative Humidity Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 3 | 326924 | 04 |  | Weichai Humidity Sensor Air Temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 2 | 326924 | 04 |  | Weichai Air Filter DP Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 1 | 326924 | 04 |  | Weichai CH4 Concentration Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26923 | 0 | 326924 | 04 |  | Weichai H2S Concentration Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 15 | 326925 | 04 |  | Weichai Closed Loop Correction Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 14 | 326925 | 04 |  | Weichai Engine Exhaust O2 Sensor Fueling Correction Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 13 | 326925 | 04 |  | Fan Speed (SPN 1639) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 12 | 326925 | 04 |  | DPF Active Regeneration Inhibited Due to System Fault Active (SPN 3712) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 11 | 326925 | 04 |  | FPT HC level Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 10 | 326925 | 04 |  | FPT EGR / DPF operator inducement Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 9 | 326925 | 04 |  | Deutz EMR5 Standstill request reason Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 8 | 326925 | 04 |  | Deutz EMR5 SCR warning Lamp / EAT inducement Lamp Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 7 | 326925 | 04 |  | Jing Guan Fuel temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 6 | 326925 | 04 |  | Jing Guan Exhaust temperature Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 5 | 326925 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Time since Last Active Regeneration (SPN 3721) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 3 | 326925 | 04 |  | Aftertreatment 1 SCR Intake NOx 2 (SPN 7649) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26924 | 2 | 326925 | 04 |  | Aftertreatment 2 SCR Intake NOx 2 (SPN 7671) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26925 | 4 | 326926 | 04 |  | Engine Fuel Valve 2 Position (SPN 1443) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26925 | 3 | 326926 | 04 |  | Engine Fuel Valve 1 Outlet Absolute Pressure (SPN 2980) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26925 | 2 | 326926 | 04 |  | Engine Throttle 2 Position (SPN 3673) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26925 | 1 | 326926 | 04 |  | Engine Throttle Valve 1 Differential Pressure (SPN 5631) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26925 | 0 | 326926 | 04 |  | Engine Oil Priming Pump Switch (SPN 3550) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 15 | 326927 | 04 |  | Engine Gas Mass Flow Rate 1 (SPN 1241) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 14 | 326927 | 04 |  | Instantaneous Estimated Brake Power (SPN 1242) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 13 | 326927 | 04 |  | Accelerator Pedal 1 Low Idle Switch (SPN 558) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 12 | 326927 | 04 |  | Engine Cylinder 1 Knock Level (SPN 1352, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 11 | 326927 | 04 |  | Engine Cylinder 2 Knock Level (SPN 1353, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 10 | 326927 | 04 |  | Engine Cylinder 3 Knock Level (SPN 1354, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 9 | 326927 | 04 |  | Engine Cylinder 4 Knock Level (SPN 1355, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 8 | 326927 | 04 |  | Engine Cylinder 5 Knock Level (SPN 1356, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 7 | 326927 | 04 |  | Engine Cylinder 6 Knock Level (SPN 1357, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 6 | 326927 | 04 |  | Engine Cylinder 7 Knock Level (SPN 1358, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 5 | 326927 | 04 |  | Engine Cylinder 8 Knock Level (SPN 1359, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 4 | 326927 | 04 |  | Engine Cylinder 9 Knock Level (SPN 1360, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 3 | 326927 | 04 |  | Engine Cylinder 10 Knock Level (SPN 1361, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 2 | 326927 | 04 |  | Engine Cylinder 11 Knock Level (SPN 1362, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 1 | 326927 | 04 |  | Engine Cylinder 12 Knock Level (SPN 1363, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26926 | 0 | 326927 | 04 |  | Engine Cylinder 13 Knock Level (SPN 1364, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 15 | 326928 | 04 |  | Engine Cylinder 14 Knock Level (SPN 1365, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 14 | 326928 | 04 |  | Engine Cylinder 15 Knock Level (SPN 1366, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 13 | 326928 | 04 |  | Engine Cylinder 16 Knock Level (SPN 1367, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 12 | 326928 | 04 |  | Cylinder 1 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 11 | 326928 | 04 |  | Cylinder 2 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 10 | 326928 | 04 |  | Cylinder 3 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 9 | 326928 | 04 |  | Cylinder 4 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 8 | 326928 | 04 |  | Cylinder 5 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 7 | 326928 | 04 |  | Cylinder 6 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 6 | 326928 | 04 |  | Cylinder 7 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 5 | 326928 | 04 |  | Cylinder 8 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 4 | 326928 | 04 |  | Cylinder 9 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 3 | 326928 | 04 |  | Cylinder 10 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 2 | 326928 | 04 |  | Cylinder 11 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 1 | 326928 | 04 |  | Cylinder 12 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26927 | 0 | 326928 | 04 |  | Cylinder 13 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 15 | 326929 | 04 |  | Cylinder 14 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 14 | 326929 | 04 |  | Cylinder 15 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 13 | 326929 | 04 |  | Cylinder 16 Knock Counter (Cummins proprietary) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 12 | 326929 | 04 |  | Engine Cylinder 2 Ignition Timing (SPN 1414, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 11 | 326929 | 04 |  | Engine Cylinder 3 Ignition Timing (SPN 1415, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 10 | 326929 | 04 |  | Engine Cylinder 4 Ignition Timing (SPN 1416, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 9 | 326929 | 04 |  | Engine Cylinder 5 Ignition Timing (SPN 1417, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 8 | 326929 | 04 |  | Engine Cylinder 6 Ignition Timing (SPN 1418, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 7 | 326929 | 04 |  | Engine Cylinder 7 Ignition Timing (SPN 1419, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 6 | 326929 | 04 |  | Engine Cylinder 8 Ignition Timing (SPN 1420, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 5 | 326929 | 04 |  | Engine Cylinder 9 Ignition Timing (SPN 1421, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 4 | 326929 | 04 |  | Engine Cylinder 10 Ignition Timing (SPN 1422, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 3 | 326929 | 04 |  | Engine Cylinder 11 Ignition Timing (SPN 1423, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 2 | 326929 | 04 |  | Engine Cylinder 12 Ignition Timing (SPN 1424, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 1 | 326929 | 04 |  | Engine Cylinder 13 Ignition Timing (SPN 1425, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26928 | 0 | 326929 | 04 |  | Engine Cylinder 14 Ignition Timing (SPN 1426, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 15 | 326930 | 04 |  | Engine Cylinder 15 Ignition Timing (SPN 1427, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 14 | 326930 | 04 |  | Engine Cylinder 16 Ignition Timing (SPN 1428, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 13 | 326930 | 04 |  | Engine Spark Plug 1 (SPN 1294, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 12 | 326930 | 04 |  | Engine Spark Plug 2 (SPN 1295, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 11 | 326930 | 04 |  | Engine Spark Plug 3 (SPN 1296, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 10 | 326930 | 04 |  | Engine Spark Plug 4 (SPN 1297, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 9 | 326930 | 04 |  | Engine Spark Plug 5 (SPN 1298, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 8 | 326930 | 04 |  | Engine Spark Plug 6 (SPN 1299, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 7 | 326930 | 04 |  | Engine Spark Plug 7 (SPN 1300, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 6 | 326930 | 04 |  | Engine Spark Plug 8 (SPN 1301, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 5 | 326930 | 04 |  | Engine Spark Plug 9 (SPN 1302, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 4 | 326930 | 04 |  | Engine Spark Plug 10 (SPN 1303, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 3 | 326930 | 04 |  | Engine Spark Plug 11 (SPN 1304, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 2 | 326930 | 04 |  | Engine Spark Plug 12 (SPN 1305, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 1 | 326930 | 04 |  | Engine Spark Plug 13 (SPN 1306, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26929 | 0 | 326930 | 04 |  | Engine Spark Plug 14 (SPN 1307, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 15 | 326931 | 04 |  | Engine Spark Plug 15 (SPN 1308, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 14 | 326931 | 04 |  | Engine Spark Plug 16 (SPN 1309, Cummins) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 13 | 326931 | 04 |  | Engine extended range oil filter diff press (SPN 6321) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 12 | 326931 | 04 |  | Sea Water Pump Outlet Pressure (SPN 2435) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 11 | 326931 | 04 |  | Water In Fuel Indicator 2 (SPN 6301) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 10 | 326931 | 04 |  | Aftertreatment 1 SCR System Hydrocarbon (SPN 7934) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 9 | 326931 | 04 |  | Aftertreatment System Enable Status (SPN 7851) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 8 | 326931 | 04 |  | Aftertreatment DEF Dosing Mode Status (SPN 9176) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 7 | 326931 | 04 |  | Aftertreatment 1 SCR System State (SPN 4332) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 6 | 326931 | 04 |  | Aftertreatment 1 SCR Intake Pressure (SPN 6586) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 5 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Pressure (SPN 6875) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 4 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Temperature (SPN 4368) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 3 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Quick Thaw Tank Volume (SPN 4367) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 2 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Fill Valve Command (SPN 5434) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 1 | 326931 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Pump Drive Percentage (SPN 4375) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26930 | 0 | 326931 | 04 |  | Aftertreatment 1 Total Diesel Exhaust Fluid Used (SPN 5963) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 14 | 326932 | 04 |  | Total Aftertreatment Operating Hours (SPN 8629) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 12 | 326932 | 04 |  | Engine Fuel Rate (High Resolution) (SPN 1600) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 10 | 326932 | 04 |  | Engine Fuel Leakage 1 (SPN 1239) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 9 | 326932 | 04 |  | Restriction level according to DEF tank level Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 8 | 326932 | 04 |  | DEF tank level – Thresholds Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 7 | 326932 | 04 |  | Restriction caused by standstill request Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 6 | 326932 | 04 |  | Restriction level according to NOx reduction Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 5 | 326932 | 04 |  | Restriction level according to anti-tampering Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 4 | 326932 | 04 |  | SCR operator inducement reason Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 3 | 326932 | 04 |  | Pedal Input Delay (Kohler KDI3404) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 2 | 326932 | 04 |  | Driver Warning System Indicator Status (SPN 5825) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 1 | 326932 | 04 |  | Emission Control System Operator Inducement Severity (SPN 5826) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26931 | 0 | 326932 | 04 |  | EIC Time remaining to inducement act (Kohler KDI3404) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 15 | 326933 | 04 |  | EIC Fuel Main Fltr Out Press L (Mitsubishi MGS3100) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 14 | 326933 | 04 |  | EIC Fuel Pre Fltr Dif Press (Mitsubishi MGS3100) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 13 | 326933 | 04 |  | EIC Engine Fuel Supply Pump Intake Pressure #2 (YC-ECU-A) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 12 | 326933 | 04 |  | EIC Engine Fuel Filter (suction side) Differential Pressure #2 (YC-ECU-A) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 11 | 326933 | 04 |  | EIC Engine Torque Mode (SPN 899) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 10 | 326933 | 04 |  | EIC Actual Engine - Percent Torque (Fractional) (SPN 4154) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 9 | 326933 | 04 |  | EIC Engine Desired Speed Asymmetrical Adjustment (SPN 519) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 8 | 326933 | 04 |  | EIC Estimated Engine Parasitic Losses (SPN 2978) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 7 | 326933 | 04 |  | EIC Aftertreatment 1 Intake Dew Point (SPN 3237) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 6 | 326933 | 04 |  | EIC Aftertreatment 1 Exhaust Dew Point (SPN 3238) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 5 | 326933 | 04 |  | EIC Aftertreatment 2 Intake Dew Point (SPN 3239) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 4 | 326933 | 04 |  | EIC Aftertreatment 2 Exhaust Dew Point (SPN 3240) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 3 | 326933 | 04 |  | EIC Charge Air Cooler Thermostat Opening (SPN 1134) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 2 | 326933 | 04 |  | EIC Engine Extended Crankcase Blowby Pressure (SPN 22) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 1 | 326933 | 04 |  | EIC Accelerator Pedal Kickdown Switch (SPN 559) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26932 | 0 | 326933 | 04 |  | EIC Road Speed Limit Status (SPN 1437) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 15 | 326934 | 04 |  | EIC Accelerator Pedal 2 Low Idle Switch (SPN 2970) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 14 | 326934 | 04 |  | EIC Remote Accelerator Pedal Position (SPN 974) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 13 | 326934 | 04 |  | EIC Vehicle Acceleration Rate Limit Status (SPN 2979) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 12 | 326934 | 04 |  | EIC Momentary Engine Maximum Power Enable Feedback (SPN 5021) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 11 | 326934 | 04 |  | EIC Estimated Pumping Percentage Torque (SPN 5398) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 10 | 326934 | 04 |  | EIC Engine Total Revolutions (SPN 249) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 8 | 326934 | 04 |  | EIC Cab Interior Temperature (SPN 170) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 7 | 326934 | 04 |  | EIC Road Surface Temperature (SPN 79) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 6 | 326934 | 04 |  | EIC Transmission Oil Temperature 1 (SPN 177, CVT transmission) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 5 | 326934 | 04 |  | EIC Transmission Actual Gear Ratio (SPN 526, CVT transmission) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 4 | 326934 | 04 |  | EIC Transmission Engine Crank Enable (SPN 2900, CVT transmission) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26933 | 3 | 326934 | 04 |  | EIC Transmission Shift Inhibit Indicator (SPN 1851, CVT transmission) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26033 | 1 | 326034 | 04 |  | Isuzu Engine Derate Lamp | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26033 | 0 | 326034 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Doser Pressure (SPN 6876) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 15 | 326035 | 04 |  | Engine Friction Percent Torque At Idle, Point 1 (SPN 5471) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 14 | 326035 | 04 |  | Engine Friction Percent Torque, Point 2 (SPN 5472) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 13 | 326035 | 04 |  | Engine Friction Percent Torque, Point 3 (SPN 5473) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 12 | 326035 | 04 |  | Engine Friction Percent Torque, Point 4 (SPN 5474) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 11 | 326035 | 04 |  | Engine Friction Percent Torque, Point 5 (SPN 5475) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 10 | 326035 | 04 |  | Engine Friction Percent Torque, Point 6 (SPN 5476) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 9 | 326035 | 04 |  | Engine Friction Percent Torque, Point 7 (SPN 5477) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 8 | 326035 | 04 |  | Aftertreatment 2 SCR Differential Pressure Preliminary FMI (SPN 4412) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 7 | 326035 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Outlet Pressure (SPN 3610) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements value | 26034 | 6 | 326035 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Intermediate Temperature Preliminary FMI (SPN 3254) | INT16u | AB | 0 | none |  |  | X | X | X
EIC measurements validity | 26934 | 5 | 326935 | 04 |  | Operator Inducement Time to Torque Derate Level 3/FINAL (SPN 7719) Validity | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26934 | 4 | 326935 | 04 |  | OBD Malfunction Indicator Lamp Command (SPN 5080) | BOOL | AB |  |  |  |  | X | X | X
EIC measurements validity | 26934 | 3 | 326935 | 04 |  | Engine Throttle position 2 (Kingbang) | BOOL | AB |  |  |  |  | X | X | X
EIC measurements validity | 26934 | 2 | 326935 | 04 |  | Aftertreatment 2 Intake %O2 (SPN 3256) | BOOL | AB |  |  |  |  | X | X | X
EIC measurements validity | 26934 | 1 | 326935 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26934 | 0 | 326935 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26935 | 15 | 326936 | 04 |  | Reserved for BOOL | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26935 | 14 | 326936 | 04 |  | Diesel Particulate Filter Active Regeneration Forced Status (SPN 4175) Validity | BOOL | [5 empty] | X | X | X
EIC measurements value | 26035 | 13 | 326036 | 04 |  | Engine Total Fuel Consumption Liquid (SPN 5054) RAW | INT32u | AB |  |  |  |  | X | X | X
EIC measurements validity | 26935 | 11 | 326936 | 04 |  | Transmission Oil Pressure 1 (SPN 127) | BOOL | [5 empty] | X | X | X
EIC measurements validity | 26935 | 9 | 326936 | 04 |  | Fuel rail pressure (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 7 | 326936 | 04 |  | Downstream fuel filter pressure (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 6 | 326936 | 04 |  | Intake post air filter pressure (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 4 | 326936 | 04 |  | Fuel pressure pre filter (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 2 | 326936 | 04 |  | Fuel pressure post filter (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 1 | 326936 | 04 |  | Pre filter oil pressure (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26935 | 0 | 326936 | 04 |  | Post filter oil pressure (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26936 | 15 | 326937 | 04 |  | Pre turbo exhaust gas temperature A (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26936 | 14 | 326937 | 04 |  | Pre turbo exhaust gas temperature B (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26936 | 12 | 326937 | 04 |  | Fuel temperature (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
EIC measurements validity | 26936 | 11 | 326937 | 04 |  | Low temperature coolant temperature (Wise10) validity | BOOL | AB |  | none |  |  | X | X | X
Plant config | 36000 |  | 336001 | 04 |  | Plant option - Plant type | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36001 |  | 336002 | 04 |  | Plant option - PMS CAN | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36002 |  | 336003 | 04 |  | Plant source ID 1 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36003 |  | 336004 | 04 |  | Plant source ID 2 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36004 |  | 336005 | 04 |  | Plant source ID 3 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36005 |  | 336006 | 04 |  | Plant source ID 4 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36006 |  | 336007 | 04 |  | Plant source ID 5 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36007 |  | 336008 | 04 |  | Plant source ID 6 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36008 |  | 336009 | 04 |  | Plant source ID 7 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36009 |  | 336010 | 04 |  | Plant source ID 8 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36010 |  | 336011 | 04 |  | Plant source ID 9 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36011 |  | 336012 | 04 |  | Plant source ID 10 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36012 |  | 336013 | 04 |  | Plant source ID 11 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36013 |  | 336014 | 04 |  | Plant source ID 12 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36014 |  | 336015 | 04 |  | Plant source ID 13 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36015 |  | 336016 | 04 |  | Plant source ID 14 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36016 |  | 336017 | 04 |  | Plant source ID 15 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36017 |  | 336018 | 04 |  | Plant source ID 16 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36018 |  | 336019 | 04 |  | Plant source ID 17 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36019 |  | 336020 | 04 |  | Plant source ID 18 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36020 |  | 336021 | 04 |  | Plant source ID 19 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36021 |  | 336022 | 04 |  | Plant source ID 20 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36022 |  | 336023 | 04 |  | Plant source ID 21 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36023 |  | 336024 | 04 |  | Plant source ID 22 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36024 |  | 336025 | 04 |  | Plant source ID 23 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36025 |  | 336026 | 04 |  | Plant source ID 24 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36026 |  | 336027 | 04 |  | Plant source ID 25 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36027 |  | 336028 | 04 |  | Plant source ID 26 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36028 |  | 336029 | 04 |  | Plant source ID 27 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36029 |  | 336030 | 04 |  | Plant source ID 28 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36030 |  | 336031 | 04 |  | Plant source ID 29 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36031 |  | 336032 | 04 |  | Plant source ID 30 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36032 |  | 336033 | 04 |  | Plant source ID 31 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36033 |  | 336034 | 04 |  | Plant source ID 32 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36034 |  | 336035 | 04 |  | Plant source ID 33 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36035 |  | 336036 | 04 |  | Plant source ID 34 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36036 |  | 336037 | 04 |  | Plant source ID 35 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36037 |  | 336038 | 04 |  | Plant source ID 36 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36038 |  | 336039 | 04 |  | Plant source ID 37 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36039 |  | 336040 | 04 |  | Plant source ID 38 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36040 |  | 336041 | 04 |  | Plant source ID 39 | INT16s | AB | 0 |  | X | X | X | X | X | X
Plant config | 36041 |  | 336042 | 04 |  | Plant source ID 40 | INT16s | AB | 0 |  | X | X | X | X | X | X
APPL version | 500 |  | 300501 | 04 |  | Application version | INT16s | AB | 0 |  | X | X | X | X | X | X
AC measurement | 501 |  | 300502 | 04 |  | S1 Voltage L1-L2 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 501 |  | 300502 | 04 |  | Generator voltage L1-L2 | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 501 |  | 300502 | 04 |  | Mains voltage L1-L2 | INT16s | AB | 0 | V |  | X
AC measurement | 501 |  | 300502 | 04 |  | Bus A voltage L1-L2 | INT16s | AB | 0 | V | X
AC measurement | 502 |  | 300503 | 04 |  | S1 Voltage L2-L3 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 502 |  | 300503 | 04 |  | Generator voltage L2-L3 | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 502 |  | 300503 | 04 |  | Mains voltage L2-L3 | INT16s | AB | 0 | V |  | X
AC measurement | 502 |  | 300503 | 04 |  | Bus A voltage L2-L3 | INT16s | AB | 0 | V | X
AC measurement | 503 |  | 300504 | 04 |  | S1 Voltage L3-L1 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 503 |  | 300504 | 04 |  | Generator voltage L3-L1 | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 503 |  | 300504 | 04 |  | Mains voltage L3-L1 | INT16s | AB | 0 | V |  | X
AC measurement | 503 |  | 300504 | 04 |  | Bus A voltage L3-L1 | INT16s | AB | 0 | V | X
AC measurement | 504 |  | 300505 | 04 |  | S1 Voltage L1-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 504 |  | 300505 | 04 |  | Generator voltage L1-N | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 504 |  | 300505 | 04 |  | Mains voltage L1-N | INT16s | AB | 0 | V |  | X
AC measurement | 504 |  | 300505 | 04 |  | Bus A voltage L1-N | INT16s | AB | 0 | V | X
AC measurement | 505 |  | 300506 | 04 |  | S1 Voltage L2-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 505 |  | 300506 | 04 |  | Generator voltage L2-N | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 505 |  | 300506 | 04 |  | Mains voltage L2-N | INT16s | AB | 0 | V |  | X
AC measurement | 505 |  | 300506 | 04 |  | Bus A voltage L2-N | INT16s | AB | 0 | V | X
AC measurement | 506 |  | 300507 | 04 |  | S1 Voltage L2-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 506 |  | 300507 | 04 |  | Generator voltage L3-N | INT16s | AB | 0 | V |  |  | X | X
AC measurement | 506 |  | 300507 | 04 |  | Mains voltage L3-N | INT16s | AB | 0 | V |  | X
AC measurement | 506 |  | 300507 | 04 |  | Bus A voltage L3-N | INT16s | AB | 0 | V | X
AC measurement | 507 |  | 300508 | 04 |  | S1 frequency L1 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 507 |  | 300508 | 04 |  | Generator frequency L1 | INT16s | AB | 2 | Hz |  |  | X | X
AC measurement | 507 |  | 300508 | 04 |  | Mains frequency L1 | INT16s | AB | 2 | Hz |  | X
AC measurement | 507 |  | 300508 | 04 |  | Bus A frequency L1 | INT16s | AB | 2 | Hz | X
AC measurement | 508 |  | 300509 | 04 |  | S1 frequency L2 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 508 |  | 300509 | 04 |  | Generator frequency L2 | INT16s | AB | 2 | Hz |  |  | X | X
AC measurement | 508 |  | 300509 | 04 |  | Mains frequency L2 | INT16s | AB | 2 | Hz |  | X
AC measurement | 508 |  | 300509 | 04 |  | Bus A frequency L2 | INT16s | AB | 2 | Hz | X
AC measurement | 509 |  | 300510 | 04 |  | S1 frequency L3 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 509 |  | 300510 | 04 |  | Generator frequency L3 | INT16s | AB | 2 | Hz |  |  | X | X
AC measurement | 509 |  | 300510 | 04 |  | Mains frequency L3 | INT16s | AB | 2 | Hz |  | X
AC measurement | 509 |  | 300510 | 04 |  | Bus A frequency L3 | INT16s | AB | 2 | Hz | X
AC measurement | 510 |  | 300511 | 04 |  | S1 voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 510 |  | 300511 | 04 |  | Generator voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 510 |  | 300511 | 04 |  | Mains voltage phase angle L1-L2 | INT16s | AB | 1 | Deg |  | X
AC measurement | 510 |  | 300511 | 04 |  | Bus A voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X
AC measurement | 511 |  | 300512 | 04 |  | S1 voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 511 |  | 300512 | 04 |  | Generator voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 511 |  | 300512 | 04 |  | Mains voltage phase angle L2-L3 | INT16s | AB | 1 | Deg |  | X
AC measurement | 511 |  | 300512 | 04 |  | Bus A voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X
AC measurement | 512 |  | 300513 | 04 |  | S1 voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 512 |  | 300513 | 04 |  | Generator voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 512 |  | 300513 | 04 |  | Mains voltage phase angle L3-L1 | INT16s | AB | 1 | Deg |  | X
AC measurement | 512 |  | 300513 | 04 |  | Bus A voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X
AC measurement | 513 |  | 300514 | 04 |  | S1 current L1 | INT16s | AB | 0 | A | [5 empty] | X
AC measurement | 513 |  | 300514 | 04 |  | Generator current L1 | INT16s | AB | 0 | A |  |  | X | X
AC measurement | 513 |  | 300514 | 04 |  | Mains current L1 | INT16s | AB | 0 | A |  | X
AC measurement | 513 |  | 300514 | 04 |  | Bus A current L1 | INT16s | AB | 0 | A | X
AC measurement | 514 |  | 300515 | 04 |  | S1 current L2 | INT16s | AB | 0 | A | [5 empty] | X
AC measurement | 514 |  | 300515 | 04 |  | Generator current L2 | INT16s | AB | 0 | A |  |  | X | X
AC measurement | 514 |  | 300515 | 04 |  | Mains current L2 | INT16s | AB | 0 | A |  | X
AC measurement | 514 |  | 300515 | 04 |  | Bus A current L2 | INT16s | AB | 0 | A | X
AC measurement | 515 |  | 300516 | 04 |  | Generator current L3 | INT16s | AB | 0 | A |  |  | X | X
AC measurement | 515 |  | 300516 | 04 |  | Mains current L3 | INT16s | AB | 0 | A |  | X
AC measurement | 515 |  | 300516 | 04 |  | S1 current L3 | INT16s | AB | 0 | A | [5 empty] | X
AC measurement | 515 |  | 300516 | 04 |  | Bus A current L3 | INT16s | AB | 0 | A | X
AC measurement | 516 |  | 300517 | 04 |  | Generator power L1 | INT16s | AB | 0 | kW |  |  | X | X
AC measurement | 516 |  | 300517 | 04 |  | Mains power L1 | INT16s | AB | 0 | kW |  | X
AC measurement | 516 |  | 300517 | 04 |  | S1 power L1 | INT16s | AB | 0 | kW | [5 empty] | X
AC measurement | 516 |  | 300517 | 04 |  | Bus A power L1 | INT16s | AB | 0 | kW | X
AC measurement | 517 |  | 300518 | 04 |  | S1 power L2 | INT16s | AB | 0 | kW | [5 empty] | X
AC measurement | 517 |  | 300518 | 04 |  | Generator power L2 | INT16s | AB | 0 | kW |  |  | X | X
AC measurement | 517 |  | 300518 | 04 |  | Mains power L2 | INT16s | AB | 0 | kW |  | X
AC measurement | 517 |  | 300518 | 04 |  | Bus A power L2 | INT16s | AB | 0 | kW | X
AC measurement | 518 |  | 300519 | 04 |  | S1 power L3 | INT16s | AB | 0 | kW | [5 empty] | X
AC measurement | 518 |  | 300519 | 04 |  | Generator power L3 | INT16s | AB | 0 | kW |  |  | X | X
AC measurement | 518 |  | 300519 | 04 |  | Mains power L3 | INT16s | AB | 0 | kW |  | X
AC measurement | 518 |  | 300519 | 04 |  | Bus A power L3 | INT16s | AB | 0 | kW | X
AC measurement | 519 |  | 300520 | 04 |  | S1 power | INT16s | AB | 0 | kW | [5 empty] | X
AC measurement | 519 |  | 300520 | 04 |  | Generator power | INT16s | AB | 0 | kW |  |  | X | X
AC measurement | 519 |  | 300520 | 04 |  | Mains power | INT16s | AB | 0 | kW |  | X
AC measurement | 519 |  | 300520 | 04 |  | Bus A power | INT16s | AB | 0 | kW | X
AC measurement | 520 |  | 300521 | 04 |  | S1 reactive power L1 | INT16s | AB | 0 | kVAr | [5 empty] | X
AC measurement | 520 |  | 300521 | 04 |  | Mains reactive power L1 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 520 |  | 300521 | 04 |  | Generator reactive power L1 | INT16s | AB | 0 | kVAr |  |  | X | X
AC measurement | 520 |  | 300521 | 04 |  | Bus A reactive power L1 | INT16s | AB | 0 | kVAr | X
AC measurement | 521 |  | 300522 | 04 |  | S1 reactive power L2 | INT16s | AB | 0 | kVAr | [5 empty] | X
AC measurement | 521 |  | 300522 | 04 |  | Generator reactive power L2 | INT16s | AB | 0 | kVAr |  |  | X | X
AC measurement | 521 |  | 300522 | 04 |  | Mains reactive power L2 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 521 |  | 300522 | 04 |  | Bus A reactive power L2 | INT16s | AB | 0 | kVAr | X
AC measurement | 522 |  | 300523 | 04 |  | S1 reactive power L3 | INT16s | AB | 0 | kVAr | [5 empty] | X
AC measurement | 522 |  | 300523 | 04 |  | Generator reactive power L3 | INT16s | AB | 0 | kVAr |  |  | X | X
AC measurement | 522 |  | 300523 | 04 |  | Mains reactive power L3 | INT16s | AB | 0 | kVAr |  | X
AC measurement | 522 |  | 300523 | 04 |  | Bus A reactive power L3 | INT16s | AB | 0 | kVAr | X
AC measurement | 523 |  | 300524 | 04 |  | Generator reactive power | INT16s | AB | 0 | kVAr |  |  | X | X
AC measurement | 523 |  | 300524 | 04 |  | Mains reactive power | INT16s | AB | 0 | kVAr |  | X
AC measurement | 523 |  | 300524 | 04 |  | S1 reactive power | INT16s | AB | 0 | kVAr | [5 empty] | X
AC measurement | 523 |  | 300524 | 04 |  | Bus A reactive power | INT16s | AB | 0 | kVAr | X
AC measurement | 524 |  | 300525 | 04 |  | S1 apparent power L1 | INT16s | AB | 0 | kVA | [5 empty] | X
AC measurement | 524 |  | 300525 | 04 |  | Generator apparent power L1 | INT16s | AB | 0 | kVA |  |  | X | X
AC measurement | 524 |  | 300525 | 04 |  | Mains apparent power L1 | INT16s | AB | 0 | kVA |  | X
AC measurement | 524 |  | 300525 | 04 |  | Bus A apparent power L1 | INT16s | AB | 0 | kVA | X
AC measurement | 525 |  | 300526 | 04 |  | S1 apparent power L2 | INT16s | AB | 0 | kVA | [5 empty] | X
AC measurement | 525 |  | 300526 | 04 |  | Generator apparent power L2 | INT16s | AB | 0 | kVA |  |  | X | X
AC measurement | 525 |  | 300526 | 04 |  | Mains apparent power L2 | INT16s | AB | 0 | kVA |  | X
AC measurement | 525 |  | 300526 | 04 |  | Bus A apparent power L2 | INT16s | AB | 0 | kVA | X
AC measurement | 526 |  | 300527 | 04 |  | S1 apparent power L3 | INT16s | AB | 0 | kVA | [5 empty] | X
AC measurement | 526 |  | 300527 | 04 |  | Mains apparent power L3 | INT16s | AB | 0 | kVA |  | X
AC measurement | 526 |  | 300527 | 04 |  | Generator apparent power L3 | INT16s | AB | 0 | kVA |  |  | X | X
AC measurement | 526 |  | 300527 | 04 |  | Bus A apparent power L3 | INT16s | AB | 0 | kVA | X
AC measurement | 527 |  | 300528 | 04 |  | S1 apparent power | INT16s | AB | 0 | kVA | [5 empty] | X
AC measurement | 527 |  | 300528 | 04 |  | Generator apparent power | INT16s | AB | 0 | kVA |  |  | X | X
AC measurement | 527 |  | 300528 | 04 |  | Mains apparent power | INT16s | AB | 0 | kVA |  | X
AC measurement | 527 |  | 300528 | 04 |  | Bus A apparent power | INT16s | AB | 0 | kVA | X
Counter | 528 |  | 300529 | 04 |  | S1 Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh | [5 empty] | X
Counter | 528 |  | 300529 | 04 |  | Generator Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 528 |  | 300529 | 04 |  | Mains Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  | X
Counter | 528 |  | 300529 | 04 |  | Bus A Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X
Counter | 530 |  | 300531 | 04 |  | S1 Export, active energy counter, day | INT32s | ABCD | 0 | kWh | [5 empty] | X
Counter | 530 |  | 300531 | 04 |  | Generator Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 530 |  | 300531 | 04 |  | Mains Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 530 |  | 300531 | 04 |  | Bus A Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 532 |  | 300533 | 04 |  | S1 Export, active energy counter, week | INT32s | ABCD | 0 | kWh | [5 empty] | X
Counter | 532 |  | 300533 | 04 |  | Generator Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 532 |  | 300533 | 04 |  | Mains Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 532 |  | 300533 | 04 |  | Bus A Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 534 |  | 300535 | 04 |  | S1 Export, active energy counter, month | INT32s | ABCD | 0 | kWh | [5 empty] | X
Counter | 534 |  | 300535 | 04 |  | Generator Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 534 |  | 300535 | 04 |  | Mains Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 534 |  | 300535 | 04 |  | Bus A Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 536 |  | 300537 | 04 |  | S1 Export, active energy counter, total | INT32s | ABCD | 0 | kWh | [5 empty] | X
Counter | 536 |  | 300537 | 04 |  | Generator Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 536 |  | 300537 | 04 |  | Mains Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 536 |  | 300537 | 04 |  | Bus A Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
AC measurement | 538 |  | 300539 | 04 |  | S1 PF | INT16s | AB | 2 | PF | [5 empty] | X
AC measurement | 538 |  | 300539 | 04 |  | Generator PF | INT16s | AB | 2 | PF |  |  | X | X
AC measurement | 538 |  | 300539 | 04 |  | Mains PF | INT16s | AB | 2 | PF |  | X
AC measurement | 538 |  | 300539 | 04 |  | Bus A PF | INT16s | AB | 2 | PF | X
AC measurement | 539 |  | 300540 | 04 |  | S2 voltage L1-L2 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 539 |  | 300540 | 04 |  | Bus B voltage L1-L2 | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 540 |  | 300541 | 04 |  | S2 voltage L2-L3 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 540 |  | 300541 | 04 |  | Bus B voltage L2-L3 | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 541 |  | 300542 | 04 |  | S2 voltage L3-L1 | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 541 |  | 300542 | 04 |  | Bus B voltage L3-L1 | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 542 |  | 300543 | 04 |  | S2 voltage L1-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 542 |  | 300543 | 04 |  | Bus B voltage L1-N | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 543 |  | 300544 | 04 |  | S2 voltage L2-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 543 |  | 300544 | 04 |  | Bus B voltage L2-N | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 544 |  | 300545 | 04 |  | S2 voltage L3-N | INT16s | AB | 0 | V | [5 empty] | X
AC measurement | 544 |  | 300545 | 04 |  | Bus B voltage L3-N | INT16s | AB | 0 | V | X | X | X | X
AC measurement | 545 |  | 300546 | 04 |  | S2 frequency L1 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 545 |  | 300546 | 04 |  | Bus B frequency L1 | INT16s | AB | 2 | Hz | X | X | X | X
AC measurement | 546 |  | 300547 | 04 |  | S2 frequency L2 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 546 |  | 300547 | 04 |  | Bus B frequency L2 | INT16s | AB | 2 | Hz | X | X | X | X
AC measurement | 547 |  | 300548 | 04 |  | S2 frequency L3 | INT16s | AB | 2 | Hz | [5 empty] | X
AC measurement | 547 |  | 300548 | 04 |  | Bus B frequency L3 | INT16s | AB | 2 | Hz | X | X | X | X
AC measurement | 548 |  | 300549 | 04 |  | S2 voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 548 |  | 300549 | 04 |  | Bus B voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X | X | X
AC measurement | 549 |  | 300550 | 04 |  | S2 voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 549 |  | 300550 | 04 |  | Bus B voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X | X | X
AC measurement | 550 |  | 300551 | 04 |  | S2 voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 550 |  | 300551 | 04 |  | Bus B voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X | X | X
AC measurement | 551 |  | 300552 | 04 |  | U S1 L1 - U S2 L1 phase angle | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U GEN L1 phase angle | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U Mains L1 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 551 |  | 300552 | 04 |  | U BB A L1 - U BB B L1 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 552 |  | 300553 | 04 |  | U S1 L2 - U S2 L2 phase angle | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U GEN L2 phase angle | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U Mains L2 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 552 |  | 300553 | 04 |  | U BB A L2 - U BB B L2 phase angle | INT16s | AB | 1 | Deg | X
AC measurement | 553 |  | 300554 | 04 |  | U S1 L3 - U S2 L3 phase angle | INT16s | AB | 1 | Deg | [5 empty] | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U GEN L3 phase angle | INT16s | AB | 1 | Deg |  |  | X | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U Mains L3 phase angle | INT16s | AB | 1 | Deg |  | X
AC measurement | 553 |  | 300554 | 04 |  | U BB A L3 - U BB B L3 phase angle | INT16s | AB | 1 | Deg | X
Counter | 554 |  | 300555 | 04 |  | Absolute running hours | INT32s | ABCD | 0 |  |  |  | X | X | X
Counter | 556 |  | 300557 | 04 |  | Relative running hours | INT32s | ABCD | 0 |  |  |  | X | X | X
Counter | 558 |  | 300559 | 04 |  | No. of alarms | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 559 |  | 300560 | 04 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 560 |  | 300561 | 04 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 561 |  | 300562 | 04 |  | Running minute counter, shutdown override | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 562 |  | 300563 | 04 |  | Running hour counter, shutdown override | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 563 |  | 300564 | 04 |  | No. of CB1 operations | INT16s | AB | 0 | [6 empty] | X
Counter | 563 |  | 300564 | 04 |  | No. of GB operations | INT16s | AB | 0 |  |  |  | X | X
Counter | 563 |  | 300564 | 04 |  | No. Of TB operations | INT16s | AB | 0 |  |  | X
Counter | 563 |  | 300564 | 04 |  | No. of BTB operations | INT16s | AB | 0 |  | X
Counter | 564 |  | 300565 | 04 |  | No. of CB2 operations | INT16s | AB | 0 | [6 empty] | X
Counter | 564 |  | 300565 | 04 |  | No. of MB operations | INT16s | AB | 0 |  |  | X | X | X
Counter | 566 |  | 300567 | 04 |  | Start attempts | INT16s | AB | 0 |  |  |  | X | X | X
DC measurement | 567 |  | 300568 | 04 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X | X | X | X | X
Counter | 569 |  | 300570 | 04 |  | Service timer 1 running hours | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 570 |  | 300571 | 04 |  | Service timer 1 running days | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 571 |  | 300572 | 04 |  | Service timer 2 running hours | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 572 |  | 300573 | 04 |  | Service timer 2 running days | INT16s | AB | 0 |  |  |  | X | X | X
AC measurement | 573 |  | 300574 | 04 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X | X
AC measurement | 574 |  | 300575 | 04 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X | X
DC measurement | 576 |  | 300577 | 04 |  | RPM (revolutions per minute) | INT16s | AB | 0 | rpm |  |  | X | X | X
Counter | 577 |  | 300578 | 04 |  | Running hours load profile | INT32s | ABCD | 0 |  |  |  | X | X | X
DC measurement | 583 |  | 300584 | 04 |  | Multi-input 20 | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 584 |  | 300585 | 04 |  | Multi-input 21 | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 585 |  | 300586 | 04 |  | Multi-input 22 | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 587 |  | 300588 | 04 |  | Multi-input 23 | INT16s | AB | 0 |  | X | X | X | X | X | X
AC measurement | 591 |  | 300592 | 04 |  | Busbar power, Multi-input 21 | INT16s | AB | 0 | kW |  | X
AC measurement | 591 |  | 300592 | 04 |  | Bus A power, Multi-input 21 | INT16s | AB | 0 | kW | X
AC measurement | 592 |  | 300593 | 04 |  | Mains power: Multi-input 20 or 4th CT input | INT16s | AB | 0 | kW |  | X | X
EIC measurement | 593 |  | 300594 | 04 |  | Engine Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 594 |  | 300595 | 04 |  | Engine Coolant Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 595 |  | 300596 | 04 |  | Engine Oil Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 596 |  | 300597 | 04 |  | Number of Actual Faults | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 597 |  | 300598 | 04 |  | Engine Oil Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 598 |  | 300599 | 04 |  | Fuel temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 599 |  | 300600 | 04 |  | Intake manifold #1 pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 600 |  | 300601 | 04 |  | Air inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 601 |  | 300602 | 04 |  | Coolant level | INT16s | AB | 1 | perc |  |  | X | X | X
EIC measurement | 602 |  | 300603 | 04 |  | Fuel rate | INT16s | AB | 1 | L/h |  |  | X | X | X
EIC measurement | 603 |  | 300604 | 04 |  | Charge air pressure | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 604 |  | 300605 | 04 |  | Intake manifold #1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 605 |  | 300606 | 04 |  | Drivers demand engine - percent torque | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 606 |  | 300607 | 04 |  | Actual engine - percent torque | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 607 |  | 300608 | 04 |  | Accelerator pedal position | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 608 |  | 300609 | 04 |  | Percent load at current speed | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 609 |  | 300610 | 04 |  | Air inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 610 |  | 300611 | 04 |  | Exhaust gas temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 611 |  | 300612 | 04 |  | Engine hours | INT16s | AB | 0 | h |  |  | X | X | X
EIC measurement | 612 |  | 300613 | 04 |  | Engine oil filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 613 |  | 300614 | 04 |  | Keyswitch battery potential | INT16s | AB | 1 | V |  |  | X | X | X
EIC measurement | 614 |  | 300615 | 04 |  | Fuel delivery pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 615 |  | 300616 | 04 |  | Engine oil level | INT16s | AB | 1 | perc |  |  | X | X | X
EIC measurement | 616 |  | 300617 | 04 |  | Crankcase pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 617 |  | 300618 | 04 |  | Coolant pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 618 |  | 300619 | 04 |  | Water in fuel 1 (1 = Yes, 0 = No) | INT16s | AB | 0 | 2 bits |  |  | X | X | X
EIC measurement | 619 |  | 300620 | 04 |  | Blowby flow | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 620 |  | 300621 | 04 |  | Fuel rail pressure | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 621 |  | 300622 | 04 |  | Timing rail pressure | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 622 |  | 300623 | 04 |  | Aftercooler water inlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 623 |  | 300624 | 04 |  | Turbo oil temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 624 |  | 300625 | 04 |  | Particulate trap inlet pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 625 |  | 300626 | 04 |  | Air filter differential pressure | INT16s | AB | 3 | bar/psi |  |  | X | X | X
EIC measurement | 626 |  | 300627 | 04 |  | Coolant filter differential pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 627 |  | 300628 | 04 |  | Atmospheric pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 628 |  | 300629 | 04 |  | Ambient air temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 629 |  | 300630 | 04 |  | Exhaust temperature - right | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 630 |  | 300631 | 04 |  | Exhaust temperature - left | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 631 |  | 300632 | 04 |  | Winding 1 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 632 |  | 300633 | 04 |  | Winding 2 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 633 |  | 300634 | 04 |  | Winding 3 temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 634 |  | 300635 | 04 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 635 |  | 300636 | 04 |  | Auxiliary_Analog_Info | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 636 |  | 300637 | 04 |  | Engine turbocharger 1 compressor outlet temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 637 |  | 300638 | 04 |  | Engine intercooler temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 638 |  | 300639 | 04 |  | Engine trip fuel | INT16s | AB | 0 | L |  |  | X | X | X
EIC measurement | 639 |  | 300640 | 04 |  | Engine total fuel used | INT16s | AB | 1 | kL |  |  | X | X | X
EIC measurement | 640 |  | 300641 | 04 |  | Trip fuel, gaseous | INT16s | AB | 0 | kg |  |  | X | X | X
EIC measurement | 641 |  | 300642 | 04 |  | Total fuel used, gaseous | INT16s | AB | 1 | ton |  |  | X | X | X
Control command state | 642 |  | 300643 | 04 |  | Control command address 0 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 643 |  | 300644 | 04 |  | Control command address 1 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 644 |  | 300645 | 04 |  | Control command address 2 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 645 |  | 300646 | 04 |  | Control command address 3 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 646 |  | 300647 | 04 |  | Control command address 4 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 647 |  | 300648 | 04 |  | Control command address 5 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 648 |  | 300649 | 04 |  | Control command address 6 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 649 |  | 300650 | 04 |  | Control command address 7 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 650 |  | 300651 | 04 |  | Control command address 8 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 651 |  | 300652 | 04 |  | Control command address 9 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 652 |  | 300653 | 04 |  | Control command address 10 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 653 |  | 300654 | 04 |  | Control command address 11 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 654 |  | 300655 | 04 |  | Control command address 12 | INT16s | AB | 0 |  | X | X | X | X | X | X
Control command state | 655 |  | 300656 | 04 |  | Control command address 13 | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 660 |  | 300661 | 04 |  | CIO 308 no. 1. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 661 |  | 300662 | 04 |  | CIO 308 no. 1. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 662 |  | 300663 | 04 |  | CIO 308 no. 1. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 663 |  | 300664 | 04 |  | CIO 308 no. 1. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 664 |  | 300665 | 04 |  | CIO 308 no. 1. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 665 |  | 300666 | 04 |  | CIO 308 no. 1. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 666 |  | 300667 | 04 |  | CIO 308 no. 1. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 667 |  | 300668 | 04 |  | CIO 308 no. 1. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 668 |  | 300669 | 04 |  | CIO 308 no. 2. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 669 |  | 300670 | 04 |  | CIO 308 no. 2. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 670 |  | 300671 | 04 |  | CIO 308 no. 2. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 671 |  | 300672 | 04 |  | CIO 308 no. 2. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 672 |  | 300673 | 04 |  | CIO 308 no. 2. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 673 |  | 300674 | 04 |  | CIO 308 no. 2. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 674 |  | 300675 | 04 |  | CIO 308 no. 2. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 675 |  | 300676 | 04 |  | CIO 308 no. 2. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 676 |  | 300677 | 04 |  | CIO 308 no. 3. Input 8 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 677 |  | 300678 | 04 |  | CIO 308 no. 3. Input 11 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 678 |  | 300679 | 04 |  | CIO 308 no. 3. Input 14 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 679 |  | 300680 | 04 |  | CIO 308 no. 3. Input 17 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 680 |  | 300681 | 04 |  | CIO 308 no. 3. Input 20 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 681 |  | 300682 | 04 |  | CIO 308 no. 3. Input 23 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 682 |  | 300683 | 04 |  | CIO 308 no. 3. Input 26 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 683 |  | 300684 | 04 |  | CIO 308 no. 3. Input 29 [Config] | INT16s | AB | 0 |  | X | X | X | X | X | X
AC measurement | 689 |  | 300690 | 04 |  | Power derate value | INT16s | AB | 1 | perc |  |  | X | X
Plant logic state | 690 |  | 300691 | 04 |  | Power derate function active: 0: No derate. 1: P derate 1. 2: P derate 2. 3: Pderate3. 4: EIC derate | INT16s | AB | 0 |  |  |  | X | X
Alarm | 691 |  | 300692 | 04 |  | M-Logic extended timer alarm 1 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X | X | X
Alarm | 692 |  | 300693 | 04 |  | M-Logic extended timer alarm 2 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X | X | X
Alarm | 693 |  | 300694 | 04 |  | M-Logic extended timer alarm 3 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X | X | X
Alarm | 694 |  | 300695 | 04 |  | M-Logic extended timer alarm 4 value | INT16s | AB | 0 | min/day/hrs | X | X | X | X | X | X
EIC measurement | 696 |  | 300697 | 04 |  | Lowest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 697 |  | 300698 | 04 |  | Highest Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 698 |  | 300699 | 04 |  | Average Cylinder Exhaust temperature | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 699 |  | 300700 | 04 |  | Cylinder Exhaust temperature: Max or Min most deviated from Average | INT16s | AB | 0 |  |  |  | X | X | X
AC measurement | 700 |  | 300701 | 04 |  | Actual nominal power (Includes derate etc.) | INT16s | AB | 0 |  | X | X | X | X
Plant logic state | 701 |  | 300702 | 04 |  | Mains power transducer used or Mains power 4th CT used | INT16s | AB | 0 |  |  | X | X
Counter | 702 |  | 300703 | 04 |  | Fan A running hours | INT32s | ABCD | 0 |  |  |  | X | X
Counter | 704 |  | 300705 | 04 |  | Fan B running hours | INT32s | ABCD | 0 |  |  |  | X | X
Counter | 706 |  | 300707 | 04 |  | Fan C running hours | INT32s | ABCD | 0 |  |  |  | X | X
Counter | 708 |  | 300709 | 04 |  | Fan D running hours | INT32s | ABCD | 0 |  |  |  | X | X
AC measurement | 750 |  | 300751 | 04 |  | 4th current input: I neutral (true RMS) | INT16s | AB | 0 | A | X | X | X | X
AC measurement | 751 |  | 300752 | 04 |  | 4th current input: I ground (3rd harmonic filter) | INT16s | AB | 0 | A | X | X | X | X
AC measurement | 752 |  | 300753 | 04 |  | 4th current input: Apparent power | INT16s | AB | 0 | kVA | X | X | X | X
AC measurement | 753 |  | 300754 | 04 |  | 4th current input: Active power | INT16s | AB | 0 | kW | X | X | X | X
AC measurement | 754 |  | 300755 | 04 |  | 4th current input: Reactive power | INT16s | AB | 0 | kvar | X | X | X | X
AC measurement | 755 |  | 300756 | 04 |  | 4th current input: Cos-phi | INT16s | AB | 2 | cosPhi | X | X | X | X
AC measurement | 756 |  | 300757 | 04 |  | 4th current input: Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X | X | X
AC measurement | 757 |  | 300758 | 04 |  | 4th current input: Power factor | INT16s | AB | 2 | PF | X | X | X | X
Plant logic state | 758 |  | 300759 | 04 |  | Mains Q transducer used or Mains Q 4th CT used | INT16s | AB | 0 |  |  | X | X
AC measurement | 759 |  | 300760 | 04 |  | Mains Q, Multi-input 20 or 4th CT | INT16s | AB | 0 | kW |  | X | X
Counter | 760 |  | 300761 | 04 |  | Absolute running minutes | INT16s | AB | 0 | min |  |  | X | X | X
PM Plant logic state | 763 |  | 300764 | 04 |  | Power management: Active application | INT16s | AB | 0 |  | X | X | X | X | X | X
AC measurement | 764 |  | 300765 | 04 |  | 4th current input: I busbar (true RMS) | INT16s | AB | 0 | A | X | X | X | X
AC measurement | 765 |  | 300766 | 04 |  | Active Power Load | INT32s | ABCD | 0 | kW | X | X | X | X | X | X
AC measurement | 767 |  | 300768 | 04 |  | Reactive Power Load | INT32s | ABCD | 0 | kW | X | X | X | X | X | X
Counter | 770 |  | 300771 | 04 |  | Controller name letter 1 + 2. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 771 |  | 300772 | 04 |  | Controller name letter 3 + 4. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 772 |  | 300773 | 04 |  | Controller name letter 5 + 6. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 773 |  | 300774 | 04 |  | Controller name letter 7 + 7. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 774 |  | 300775 | 04 |  | Controller name letter 9 + 10. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 775 |  | 300776 | 04 |  | Controller name letter 11 + 12. Read as HEX and convert to ASCII. | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 776 |  | 300777 | 04 |  | Multi-input 20 configuration | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 777 |  | 300778 | 04 |  | Multi-input 21 configuration | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 778 |  | 300779 | 04 |  | Multi-input 22 configuration | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 779 |  | 300780 | 04 |  | Multi-input 23 configuration | INT16s | AB | 0 |  | X | X | X | X | X | X
Counter | 790 |  | 300791 | 04 |  | Generator Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 790 |  | 300791 | 04 |  | Mains Export reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 790 |  | 300791 | 04 |  | Bus A Export reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 792 |  | 300793 | 04 |  | Generator Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 792 |  | 300793 | 04 |  | Mains Export reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 792 |  | 300793 | 04 |  | Bus A Export reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 794 |  | 300795 | 04 |  | Generator Export reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 794 |  | 300795 | 04 |  | Mains Export reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 794 |  | 300795 | 04 |  | Bus A Export reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 796 |  | 300797 | 04 |  | Generator Import active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 796 |  | 300797 | 04 |  | Mains Import active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 796 |  | 300797 | 04 |  | Bus A Import active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 798 |  | 300799 | 04 |  | Generator Import active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 798 |  | 300799 | 04 |  | Mains Import active energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 798 |  | 300799 | 04 |  | Bus A Import active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 800 |  | 300801 | 04 |  | Generator Import active energy counter, week | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 800 |  | 300801 | 04 |  | Mains Import active energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 800 |  | 300801 | 04 |  | Bus A Import active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 802 |  | 300803 | 04 |  | Generator Import active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 802 |  | 300803 | 04 |  | Mains Import active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 802 |  | 300803 | 04 |  | Bus A Import active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 804 |  | 300805 | 04 |  | Generator Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 804 |  | 300805 | 04 |  | Mains Import reactive energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 804 |  | 300805 | 04 |  | Bus A Import reactive energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 806 |  | 300807 | 04 |  | Generator Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 806 |  | 300807 | 04 |  | Mains Import reactive energy counter, month | INT32s | ABCD | 0 | kWh |  | X
Counter | 806 |  | 300807 | 04 |  | Bus A Import reactive energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 808 |  | 300809 | 04 |  | Generator Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 808 |  | 300809 | 04 |  | Mains Import reactive energy counter, week | INT32s | ABCD | 0 | kWh |  | X
Counter | 808 |  | 300809 | 04 |  | Bus A Import reactive energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 810 |  | 300811 | 04 |  | Generator Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh |  |  | X | X
Counter | 810 |  | 300811 | 04 |  | Mains Import reactive energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 810 |  | 300811 | 04 |  | Bus A Import reactive energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 812 |  | 300813 | 04 |  | Pulse counter 01 | INT32s | ABCD | 0 |  | X | X | X | X | X | X
Counter | 814 |  | 300815 | 04 |  | Pulse counter 02 | INT32s | ABCD | 0 |  | X | X | X | X | X | X
AC measurement | 816 |  | 300817 | 04 |  | Demand of peak current 1 | INT16s | AB | 0 |  |  | X | X | X
AC measurement | 817 |  | 300818 | 04 |  | Demand of peak current 2 | INT16s | AB | 0 |  |  | X | X | X
AC measurement | 818 |  | 300819 | 04 |  | Demand of peak current 3 | INT16s | AB | 0 |  |  | X | X | X
AC measurement | 819 |  | 300820 | 04 |  | Demand of avg. peak current 1 | INT16s | AB | 0 |  |  | X | X | X
AC measurement | 820 |  | 300821 | 04 |  | Demand of avg. peak current 2 | INT16s | AB | 0 |  |  | X | X | X
AC measurement | 821 |  | 300822 | 04 |  | Demand of avg. peak current 3 | INT16s | AB | 0 |  |  | X | X | X
Counter | 822 |  | 300823 | 04 |  | Start attempts standard | INT16s | AB | 0 |  |  |  | X | X | X
Counter | 823 |  | 300824 | 04 |  | Start attempts double starter | INT16s | AB | 0 |  |  |  | X | X | X
AC measurement | 827 |  | 300828 | 04 |  | AVR ref current | INT16s | AB | 0 |  |  |  | X
AC measurement | 828 |  | 300829 | 04 |  | CosPhi ref current sign | INT16s | AB | 0 |  |  |  | X
AC measurement | 829 |  | 300830 | 04 |  | CosPhi ref current abs value | INT16s | AB | 0 |  |  |  | X
EIC measurement | 831 |  | 300832 | 04 |  | GOV output | INT16s | AB | 0 |  |  |  | X
EIC measurement | 832 |  | 300833 | 04 |  | AVR output | INT16s | AB | 0 |  |  |  | X
AC measurement | 833 |  | 300834 | 04 |  | P ref actual | INT16s | AB | 0 |  |  |  | X
AC measurement | 834 |  | 300835 | 04 |  | AVR ref current ramped | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 840 |  | 300841 | 04 |  | Battery Potential / Power Input 1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 841 |  | 300842 | 04 |  | Engine Turbocharger 2 Boost Pressure | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 842 |  | 300843 | 04 |  | Engine Intake Manifold 3 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 843 |  | 300844 | 04 |  | Engine Intake Manifold 4 Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 844 |  | 300845 | 04 |  | Engine Fuel 1 Injector Metering Rail 1 Pressure | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 845 |  | 300846 | 04 |  | Engine Pre-filter Oil Pressure | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 846 |  | 300847 | 04 |  | Water in fuel 2 (1 = Yes, 0 = No) | INT16s | AB | 0 | 2 bits |  |  | X | X | X
EIC measurement | 850 |  | 300851 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 1 | g/h |  |  | X | X | X
EIC measurement | 851 |  | 300852 | 04 |  | Aftertreatment 2 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 852 |  | 300853 | 04 |  | Aftertreatment 2 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 853 |  | 300854 | 04 |  | Engine Oil-Filter Outlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 854 |  | 300855 | 04 |  | Engine Operating State | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 855 |  | 300856 | 04 |  | Source Address of Controlling Device | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 856 |  | 300857 | 04 |  | Engine Rated Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 857 |  | 300858 | 04 |  | Engine Speed At Idle, Point 1 | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 858 |  | 300859 | 04 |  | MTU only: Fuel Consumption g/KWh | INT16s | AB | 0 | g/kWh |  |  | X | X | X
EIC measurement | 859 |  | 300860 | 04 |  | MTU only: Engine Status of Start procedure | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 860 |  | 300861 | 04 |  | UREA Level (Scania and Isuzu) | INT16s | AB | 1 | perc |  |  | X | X | X
EIC measurement | 861 |  | 300862 | 04 |  | Severity status of the operator inducement system | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 862 |  | 300863 | 04 |  | Temperature of engine combustion byproducts leaving the diesel particulate filter exhaust in exhaust bank 1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 863 |  | 300864 | 04 |  | Time to activate next regeneration for diesel particulate filter | INT16s | AB | 1 | h |  |  | X | X | X
EIC measurement | 864 |  | 300865 | 04 |  | Temperature of combustion air after it exits from the Charge Air Cooler 1 but before any mixing of recirculated exhaust gas. | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 865 |  | 300866 | 04 |  | Aftertreatment 1 Diesel Particulate Filter 1 Soot Load Percent | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 866 |  | 300867 | 04 |  | Battery Charger 1 Output Voltage | INT16s | AB | 0 | V |  |  | X | X | X
EIC measurement | 867 |  | 300868 | 04 |  | Battery Charger 1 Output Current | INT16s | AB | 0 | A |  |  | X | X | X
EIC state | 868 | 0 | 300869 | 04 |  | DPF lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 868 | 1 | 300869 | 04 |  | DPF lamp ON solid | BOOL | [5 empty] | X | X | X
EIC state | 868 | 2 | 300869 | 04 |  | DPF lamp ON blink | BOOL | [5 empty] | X | X | X
EIC state | 868 | 3 | 300869 | 04 |  | DPF Active Regeneration not activated | BOOL | [5 empty] | X | X | X
EIC state | 868 | 4 | 300869 | 04 |  | DPF Active Regeneration activated | BOOL | [5 empty] | X | X | X
EIC state | 868 | 5 | 300869 | 04 |  | DPF Active Regeneration needed | BOOL | [5 empty] | X | X | X
EIC state | 868 | 6 | 300869 | 04 |  | DPF Regeneration not needed | BOOL | [5 empty] | X | X | X
EIC state | 868 | 7 | 300869 | 04 |  | DPF Regeneration needed Lowest | BOOL | [5 empty] | X | X | X
EIC state | 868 | 8 | 300869 | 04 |  | DPF Regeneration needed Moderate | BOOL | [5 empty] | X | X | X
EIC state | 868 | 9 | 300869 | 04 |  | DPF Regeneration needed Highest | BOOL | [5 empty] | X | X | X
EIC state | 868 | 10 | 300869 | 04 |  | DPF Regeneration Not Inhibit | BOOL | [5 empty] | X | X | X
EIC state | 868 | 11 | 300869 | 04 |  | DPF Regeneration Inhibit | BOOL | [5 empty] | X | X | X
EIC state | 868 | 12 | 300869 | 04 |  | Exhaust system high temperature OFF | BOOL | [5 empty] | X | X | X
EIC state | 868 | 13 | 300869 | 04 |  | Exhaust system high temperature ON | BOOL | [5 empty] | X | X | X
EIC state | 868 | 14 | 300869 | 04 |  | After run status | BOOL | [5 empty] | X | X | X
EIC state | 869 | 0 | 300870 | 04 |  | MTU limit lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 869 | 1 | 300870 | 04 |  | MTU limit lamp ON solid | BOOL | [5 empty] | X | X | X
EIC state | 869 | 2 | 300870 | 04 |  | MTU limit lamp ON blink 1Hz | BOOL | [5 empty] | X | X | X
EIC state | 869 | 3 | 300870 | 04 |  | DEF level low lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 869 | 4 | 300870 | 04 |  | DEF level low lamp ON solid | BOOL | [5 empty] | X | X | X
EIC state | 869 | 5 | 300870 | 04 |  | DEF level low lamp ON blink | BOOL | [5 empty] | X | X | X
EIC state | 869 | 6 | 300870 | 04 |  | Volvo Penta Scr Inducement not ACTIVE | BOOL | [5 empty] | X | X | X
EIC state | 869 | 7 | 300870 | 04 |  | Volvo Penta Scr Inducement WARNING | BOOL | [5 empty] | X | X | X
EIC state | 869 | 8 | 300870 | 04 |  | Volvo Penta Scr Derate ACTIVE | BOOL | [5 empty] | X | X | X
EIC state | 869 | 9 | 300870 | 04 |  | Volvo Penta Pre severe Derate WARNING | BOOL | [5 empty] | X | X | X
EIC state | 869 | 10 | 300870 | 04 |  | Volvo Penta Severe Derate | BOOL | [5 empty] | X | X | X
EIC state | 869 | 11 | 300870 | 04 |  | Volvo Penta Temperature Override Derate | BOOL | [5 empty] | X | X | X
EIC state | 869 | 12 | 300870 | 04 |  | Volvo Penta Scr Inducement Reason OK | BOOL | [5 empty] | X | X | X
EIC state | 869 | 13 | 300870 | 04 |  | Volvo Penta Reagent Tank low | BOOL | [5 empty] | X | X | X
EIC state | 869 | 14 | 300870 | 04 |  | Volvo Penta Incorrect Reagent Quality | BOOL | [5 empty] | X | X | X
EIC state | 869 | 15 | 300870 | 04 |  | Volvo Penta Absence of Reagent Dosing | BOOL | [5 empty] | X | X | X
EIC state | 870 | 0 | 300871 | 04 |  | MTU limit lamp ON blink 2Hz | BOOL | [5 empty] | X | X | X
EIC state | 870 | 1 | 300871 | 04 |  | MTU TIER4 lamp ON blink 2Hz | BOOL | [5 empty] | X | X | X
EIC state | 870 | 2 | 300871 | 04 |  | MTU buzzer lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 870 | 3 | 300871 | 04 |  | MTU buzzer lamp ON solid | BOOL | [5 empty] | X | X | X
EIC state | 870 | 4 | 300871 | 04 |  | MTU buzzer lamp ON blink 1Hz | BOOL | [5 empty] | X | X | X
EIC state | 870 | 5 | 300871 | 04 |  | MTU buzzer lamp ON blink 2Hz | BOOL | [5 empty] | X | X | X
EIC state | 870 | 6 | 300871 | 04 |  | Alarm Yellow lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 870 | 7 | 300871 | 04 |  | Alarm Yellow lamp ON | BOOL | [5 empty] | X | X | X
EIC state | 870 | 8 | 300871 | 04 |  | Alarm Red lamp OFF | BOOL | [5 empty] | X | X | X
EIC state | 870 | 9 | 300871 | 04 |  | Alarm Red lamp ON | BOOL | [5 empty] | X | X | X
EIC state | 870 | 10 | 300871 | 04 |  | Engine protect system SHUTDOWN | BOOL | [5 empty] | X | X | X
EIC state | 870 | 11 | 300871 | 04 |  | Engine over-speed test | BOOL | [5 empty] | X | X | X
EIC state | 870 | 12 | 300871 | 04 |  | Engine Alarm acknowledge | BOOL | [5 empty] | X | X | X
EIC state | 870 | 13 | 300871 | 04 |  | Manual purge ECU | BOOL | [5 empty] | X | X | X
EIC state | 870 | 14 | 300871 | 04 |  | Manual purge EIDSS | BOOL | [5 empty] | X | X | X
EIC state | 870 | 15 | 300871 | 04 |  | Force purge | BOOL | [5 empty] | X | X | X
EIC measurement | 871 |  | 300872 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Average Consumption | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 872 |  | 300873 | 04 |  | Volvo Penta Time left to torque reduction | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 873 |  | 300874 | 04 |  | Volvo Penta Time left to severe torque reduction | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 874 |  | 300875 | 04 |  | Volvo Penta SCR inducement severity | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 875 |  | 300876 | 04 |  | Volvo Penta SCR inducement reason | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 876 |  | 300877 | 04 |  | Engine Operating Derate Request | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 877 |  | 300878 | 04 |  | Engine Demand - Percent Torque | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 878 |  | 300879 | 04 |  | Engine Throttle Actuator 1 Control Command | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 879 |  | 300880 | 04 |  | Long-term Fuel Trim | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 880 |  | 300881 | 04 |  | Short-term Fuel Trim | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 881 |  | 300882 | 04 |  | Engine Exhaust Gas Oxygen Sensor Closed Loop Operation | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 882 |  | 300883 | 04 |  | Engine Desired Ignition Timing #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 883 |  | 300884 | 04 |  | Engine Actual Ignition Timing | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 884 |  | 300885 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 1 | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 885 |  | 300886 | 04 |  | Aftertreatment 1 Intake Percent Oxygen 2 | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 886 |  | 300887 | 04 |  | Engine Starter Mode | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 887 |  | 300888 | 04 |  | Actual Maximum Available Engine-Percent Torque | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 888 |  | 300889 | 04 |  | Engine Coolant Preheated State | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 889 |  | 300890 | 04 |  | Engine Safety and Protection Override Status | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 890 |  | 300891 | 04 |  | Engine Cylinder Cut-off | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 891 |  | 300892 | 04 |  | MTU Engine Running State | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 892 |  | 300893 | 04 |  | External Stop State | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 893 |  | 300894 | 04 |  | MTU Requested Absolute Torque | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 894 |  | 300895 | 04 |  | Source of Current Speed Demand | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 895 |  | 300896 | 04 |  | Engine Demanded Operating Speed (Speed Demand Effective) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 896 |  | 300897 | 04 |  | Feedback of Speed Demand CAN | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 897 |  | 300898 | 04 |  | Feedback of Speed Demand Analogue Input | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 898 |  | 300899 | 04 |  | Speed Demand Fail Mode | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 899 |  | 300900 | 04 |  | Inducement Timer | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 900 |  | 300901 | 04 |  | Mean Trip Fuel consumption | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 901 |  | 300902 | 04 |  | Nominal power | INT16s | AB | 0 | kWm |  |  | X | X | X
EIC measurement | 902 |  | 300903 | 04 |  | Engine Trip Fuel (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X | X
EIC measurement | 904 |  | 300905 | 04 |  | Engine Total Fuel Used (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X | X
EIC measurement | 906 |  | 300907 | 04 |  | Mean Trip Fuel consumption (not scaled) | INT32s | ABCD | 0 | L |  |  | X | X | X
EIC measurement | 908 |  | 300909 | 04 |  | Engine power | INT16s | AB | 0 | kW |  |  | X | X | X
EIC measurement | 909 |  | 300910 | 04 |  | Engine Hours (not scaled) | INT32s | ABCD | 0 | h |  |  | X | X | X
EIC measurement | 911 |  | 300912 | 04 |  | Engine intake Manifold #1 Absolute pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 912 |  | 300913 | 04 |  | Air Filter Differential pressure 2 | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 913 |  | 300914 | 04 |  | Fuel Supply Pump Inlet Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 914 |  | 300915 | 04 |  | Fuel Filter (suction side) Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 915 |  | 300916 | 04 |  | Engine Fuel Filter Differential Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
DAVR measurement | 916 |  | 300917 | 04 |  | DAVR Generator voltage L1L2 | INT16s | AB | 0 | V |  |  | X | X
DAVR measurement | 917 |  | 300918 | 04 |  | DAVR Generator frequency L1 | INT16s | AB | 0 | Hz |  |  | X | X
DAVR measurement | 918 |  | 300919 | 04 |  | DAVR Generator current L1 | INT16s | AB | 0 | A |  |  | X | X
DAVR measurement | 919 |  | 300920 | 04 |  | DAVR Generator excitation field current | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 921 |  | 300922 | 04 |  | DAVR Generator total reactive power | INT16s | AB | 0 | kvar |  |  | X | X
DAVR measurement | 922 |  | 300923 | 04 |  | DAVR Generator overall power factor | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 923 |  | 300924 | 04 |  | DAVR Generator overall power factor lagging | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 925 |  | 300926 | 04 |  | DAVR Generator total active power | INT16s | AB | 0 | kW |  |  | X | X
DAVR measurement | 927 |  | 300928 | 04 |  | DAVR Generator total apparent power | INT16s | AB | 0 | kVA |  |  | X | X
DAVR measurement | 928 |  | 300929 | 04 |  | DAVR Pt100 #1 | INT16s | AB | 0 | Deg C/F |  |  | X | X
DAVR measurement | 929 |  | 300930 | 04 |  | DAVR Pt100 #2 | INT16s | AB | 0 | Deg C/F |  |  | X | X
DAVR measurement | 930 |  | 300931 | 04 |  | DAVR Pt100 #3 | INT16s | AB | 0 | Deg C/F |  |  | X | X
DAVR measurement | 931 |  | 300932 | 04 |  | DAVR Trip alarm | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 932 |  | 300933 | 04 |  | Speed demand switch | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 933 |  | 300934 | 04 |  | Pressure: Lube Oil Limit LO | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 934 |  | 300935 | 04 |  | Pressure: Lube Oil Limit LOLO | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 935 |  | 300936 | 04 |  | Pressure: Fuel | INT16s | AB | 0 | bar/psi |  |  | X | X | X
EIC measurement | 936 |  | 300937 | 04 |  | Temperature: Coolant Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 937 |  | 300938 | 04 |  | Temperature: Coolant Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 938 |  | 300939 | 04 |  | Temperature: Coolant Intercooler | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 939 |  | 300940 | 04 |  | ECU temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 940 |  | 300941 | 04 |  | Actual Droop | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 941 |  | 300942 | 04 |  | Injection Quantity Act.DBR | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 942 |  | 300943 | 04 |  | Engine Speed Camshaft | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 943 |  | 300944 | 04 |  | Temperature: Lube Oil Limit HI | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 944 |  | 300945 | 04 |  | Temperature: Lube Oil Limit HIHI | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 945 |  | 300946 | 04 |  | Feedback Speed Demand analog | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 946 |  | 300947 | 04 |  | Stop signal activated | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 947 |  | 300948 | 04 |  | Exhaust Port Temperature 01 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 948 |  | 300949 | 04 |  | Exhaust Port Temperature 02 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 949 |  | 300950 | 04 |  | Exhaust Port Temperature 03 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 950 |  | 300951 | 04 |  | Exhaust Port Temperature 04 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 951 |  | 300952 | 04 |  | Exhaust Port Temperature 05 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 952 |  | 300953 | 04 |  | Exhaust Port Temperature 06 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 953 |  | 300954 | 04 |  | Exhaust Port Temperature 07 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 954 |  | 300955 | 04 |  | Exhaust Port Temperature 08 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 955 |  | 300956 | 04 |  | Exhaust Port Temperature 09 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 956 |  | 300957 | 04 |  | Exhaust Port Temperature 10 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 957 |  | 300958 | 04 |  | Exhaust Port Temperature 11 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 958 |  | 300959 | 04 |  | Exhaust Port Temperature 12 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 959 |  | 300960 | 04 |  | Exhaust Port Temperature 13 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 960 |  | 300961 | 04 |  | Exhaust Port Temperature 14 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 961 |  | 300962 | 04 |  | Exhaust Port Temperature 15 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 962 |  | 300963 | 04 |  | Exhaust Port Temperature 16 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 963 |  | 300964 | 04 |  | Exhaust Port Temperature 17 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 964 |  | 300965 | 04 |  | Exhaust Port Temperature 18 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 965 |  | 300966 | 04 |  | Exhaust Port Temperature 19 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 966 |  | 300967 | 04 |  | Exhaust Port Temperature 20 EPT1 | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 967 |  | 300968 | 04 |  | Engine Filtered Fuel Delivery Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 968 |  | 300969 | 04 |  | Engine Coolant Temperature 2 | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 969 |  | 300970 | 04 |  | Engine Coolant Temperature 3 | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 970 |  | 300971 | 04 |  | Engine Coolant Pump Outlet Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 971 |  | 300972 | 04 |  | Engine Auxiliary Coolant Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 972 |  | 300973 | 04 |  | Engine Turbocharger 1 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 973 |  | 300974 | 04 |  | Engine Turbocharger 2 Turbine Intake Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 974 |  | 300975 | 04 |  | Engine Auxiliary Coolant Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 975 |  | 300976 | 04 |  | Ambient Conditions 2 Specific Humidity | INT16s | AB | 1 | g/kg |  |  | X | X | X
EIC measurement | 976 |  | 300977 | 04 |  | Engine Turbocharger 2 Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 977 |  | 300978 | 04 |  | Engine Turbocharger 3 Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 978 |  | 300979 | 04 |  | Trip Engine Running Time | INT16s | AB | 0 | h |  |  | X | X | X
EIC measurement | 979 |  | 300980 | 04 |  | Trip Idle Time | INT16s | AB | 0 | h |  |  | X | X | X
EIC measurement | 980 |  | 300981 | 04 |  | Estimated Percent Fan Speed | INT16s | AB | 1 | perc |  |  | X | X | X
EIC measurement | 981 |  | 300982 | 04 |  | Engine Turbocharger 1 Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 982 |  | 300983 | 04 |  | Nominal Friction - Percent Torque | INT16s | AB | 0 | perc |  |  | X | X | X
EIC measurement | 983 |  | 300984 | 04 |  | Engine's Desired Operating Speed | INT16s | AB | 0 | rpm |  |  | X | X | X
EIC measurement | 984 |  | 300985 | 04 |  | Temperature of pre-combustion air found in intake manifold of engine air supply system | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 985 |  | 300986 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Level | INT16s | AB | 1 | perc |  |  | X | X | X
EIC measurement | 986 |  | 300987 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Tank Temperature | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 987 |  | 300988 | 04 |  | Aftertreatment 1 Intake NOx | INT16s | AB | 1 | ppm |  |  | X | X | X
EIC measurement | 988 |  | 300989 | 04 |  | Aftertreatment 1 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X | X | X
EIC measurement | 989 |  | 300990 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | g/h |  |  | X | X | X
EIC measurement | 990 |  | 300991 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Doser Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 991 |  | 300992 | 04 |  | Aftertreatment 1 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
EIC measurement | 992 |  | 300993 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Dosing Requested Quantity | INT16s | AB | 0 | g/h |  |  | X | X | X
EIC measurement | 993 |  | 300994 | 04 |  | Aftertreatment 1 SCR Catalyst Intake Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 994 |  | 300995 | 04 |  | Aftertreatment 1 SCR Catalyst Outlet Gas Temperature | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 995 |  | 300996 | 04 |  | Aftertreatment 2 Intake NOx | INT16s | AB | 1 | ppm |  |  | X | X | X
EIC measurement | 996 |  | 300997 | 04 |  | Aftertreatment 2 Outlet NOx | INT16s | AB | 1 | ppm |  |  | X | X | X
EIC measurement | 997 |  | 300998 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Actual Dosing Quantity | INT16s | AB | 1 | Deg C/F |  |  | X | X | X
EIC measurement | 998 |  | 300999 | 04 |  | Aftertreatment 2 Diesel Exhaust Fluid Dosing Absolute Pressure | INT16s | AB | 2 | bar/psi |  |  | X | X | X
EIC measurement | 999 |  | 301000 | 04 |  | Aftertreatment 2 SCR Dosing Air Assist Valve | INT16s | AB | 0 | Deg C/F |  |  | X | X | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | G -P> 1 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | M -P> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | BA -P> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | G -P> 2 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | M -P> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | BA -P> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 2 | 301001 | 04 | 1070 | G -P> 3 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 2 | 301001 | 04 | 1070 | M -P> 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 2 | 301001 | 04 | 1070 | BA -P> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | G I> 1 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | M I> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | BA I> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | G I> 2 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | M I> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | BA I> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | G I> 3 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | M I> 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | BA I> 3 | BOOL |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | G I> 4 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | M I> 4 | BOOL |  |  |  |  | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | BA I> 4 | BOOL |  |  |  | X
AC alarm | 1000 | 7 | 301001 | 04 | 1087 | G I> inv. | BOOL | [5 empty] | X | X
AC alarm | 1000 | 8 | 301001 | 04 | 1110 | G Iv> | BOOL | [5 empty] | X | X
AC alarm | 1000 | 8 | 301001 | 04 | 1110 | M Iv> | BOOL |  |  |  |  | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | G I>> 1 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | M I>> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | BA I>> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | G I>> 2 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | M I>> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | BA I>> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | G U> 1 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | M U> 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | BA U> 1 | BOOL |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | M U> 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | G U> 2 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | BA U> 2 | BOOL |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | G U< 1 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | M U< 1 | BOOL |  |  |  |  | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | BA U< 1 | BOOL |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | G U< 2 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | M U< 2 | BOOL |  |  |  |  | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | BA U< 2 | BOOL |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | G U< 3 | BOOL | [5 empty] | X | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | M U< 3 | BOOL |  |  |  |  | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | BA U< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | G f> 1 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | M f> 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | BA f> 1 | BOOL |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | G f> 2 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | M f> 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | BA f> 2 | BOOL |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | G f> 3 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | M f> 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | BA f> 3 | BOOL |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | G f< 1 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | M f< 1 | BOOL |  |  |  |  | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | BA f< 1 | BOOL |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | G f< 2 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | M f< 2 | BOOL |  |  |  |  | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | BA f< 2 | BOOL |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | G f< 3 | BOOL | [5 empty] | X | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | M f< 3 | BOOL |  |  |  |  | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | BA f< 3 | BOOL |  |  |  | X
AC alarm | 1001 | 6 | 301002 | 04 | 1270 | BB U> 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 7 | 301002 | 04 | 1280 | BB U> 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 8 | 301002 | 04 | 1290 | BB U> 3 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 9 | 301002 | 04 | 1300 | BB U< 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 10 | 301002 | 04 | 1310 | BB U< 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 11 | 301002 | 04 | 1320 | BB U< 3 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 12 | 301002 | 04 | 1330 | BB U< 4 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 13 | 301002 | 04 | 1350 | BB f> 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 14 | 301002 | 04 | 1360 | BB f> 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1001 | 15 | 301002 | 04 | 1370 | BB f> 3 | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 0 | 301003 | 04 | 1380 | BB f< 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 1 | 301003 | 04 | 1390 | BB f< 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 2 | 301003 | 04 | 1400 | BB f< 3 | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 3 | 301003 | 04 | 1410 | BB f< 4 | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 4 | 301003 | 04 | 1420 | df/dt (ROCOF) | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 5 | 301003 | 04 | 1430 | Vector jump | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 6 | 301003 | 04 | 1440 | BB pos. seq. volt. low | BOOL |  |  |  | X | X | X | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | G P> 1 | BOOL | [5 empty] | X | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | M P> 1 | BOOL |  |  |  |  | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | BA P> 1 | BOOL |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | G P> 2 | BOOL | [5 empty] | X | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | M P> 2 | BOOL |  |  |  |  | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | BA P> 2 | BOOL |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | G P> 3 | BOOL | [5 empty] | X | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | M P> 3 | BOOL |  |  |  |  | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | BA P> 3 | BOOL |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | G P> 4 | BOOL | [5 empty] | X | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | M P> 4 | BOOL |  |  |  |  | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | BA P> 4 | BOOL |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | G P> 5 | BOOL | [5 empty] | X | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | M P> 5 | BOOL |  |  |  |  | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | BA P> 5 | BOOL |  |  |  | X
AC alarm | 1002 | 12 | 301003 | 04 | 1500 | Unbalance curr. 1 | BOOL |  |  |  |  | X | X
AC alarm | 1002 | 13 | 301003 | 04 | 1510 | Unbalance volt. | BOOL |  |  |  |  | X | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | G -Q> | BOOL | [5 empty] | X | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | M -Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 14 | 301003 | 04 | 1520 | BA -Q> | BOOL |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | G Q> | BOOL | [5 empty] | X | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | M Q> | BOOL |  |  |  |  | X
AC alarm | 1002 | 15 | 301003 | 04 | 1530 | BA Q> | BOOL |  |  |  | X
AC alarm | 1003 | 0 | 301004 | 04 | 1540 | Gen. neg. seq. I | BOOL | [5 empty] | X | X
AC alarm | 1003 | 0 | 301004 | 04 | 1540 | Mains neg. seq. I | BOOL |  |  |  |  | X
AC alarm | 1003 | 1 | 301004 | 04 | 1550 | Generator neg. seq. U | BOOL | [5 empty] | X | X
AC alarm | 1003 | 1 | 301004 | 04 | 1550 | Mains neg. seq. U | BOOL |  |  |  |  | X
AC alarm | 1003 | 1 | 301004 | 04 | 1550 | Bus A neg. seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 04 | 1570 | Gen. zero seq. I | BOOL | [5 empty] | X | X
AC alarm | 1003 | 2 | 301004 | 04 | 1570 | Mains zero seq. I | BOOL |  |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 04 | 1570 | Bus A zero seq. I | BOOL |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 04 | 1580 | Zero seq. U | BOOL | [5 empty] | X | X
AC alarm | 1003 | 3 | 301004 | 04 | 1580 | Mains zero seq. U | BOOL |  |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 04 | 1580 | Bus A zero seq. U | BOOL |  |  |  | X
AC alarm | 1003 | 4 | 301004 | 04 | 1600 | Directional overcurrent 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1003 | 5 | 301004 | 04 | 1610 | Directional overcurrent 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1003 | 6 | 301004 | 04 | 1620 | BB unbalance U | BOOL |  |  |  | X | X | X | X
AC alarm | 1004 | 6 | 301005 | 04 | 1960 | U and Q< 1 | BOOL |  |  |  |  | X | X | X
AC alarm | 1004 | 7 | 301005 | 04 | 1970 | U and Q< 2 | BOOL |  |  |  |  | X | X | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | GB ext. trip | BOOL | [5 empty] | X | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | TB ext. trip | BOOL |  |  |  |  | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | BTB ext. trip | BOOL |  |  |  | X
AC alarm | 1004 | 9 | 301005 | 04 | 1983 | MB ext. trip | BOOL |  |  |  |  | X | X | X
AC alarm | 1004 | 14 | 301005 | 04 | 1760 | G P dep. Q< | BOOL | [5 empty] | X | X
AC alarm | 1004 | 15 | 301005 | 04 | 1790 | G P dep. Q> | BOOL | [5 empty] | X | X
Alarm | 1005 | 0 | 301006 | 04 | 2120 | Synchronising window | BOOL |  |  |  | X | X | X | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure GB | BOOL | [5 empty] | X | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure TB | BOOL |  |  |  |  | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure BTB | BOOL |  |  |  | X
Alarm | 1005 | 2 | 301006 | 04 | 2140 | Synchronising failure MB | BOOL |  |  |  |  | X | X | X
AC alarm | 1005 | 3 | 301006 | 04 | 2150 | Phase seq. failure A | BOOL |  |  |  | X | X | X | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | GB open failure | BOOL | [5 empty] | X | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | TB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | BTB open failure | BOOL |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | GB close failure | BOOL | [5 empty] | X | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | TB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | BTB close failure | BOOL |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | GB pos. failure | BOOL | [5 empty] | X | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | TB pos. failure | BOOL |  |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | BTB pos. failure | BOOL |  |  |  | X
Alarm | 1005 | 7 | 301006 | 04 | 2200 | MB open failure | BOOL |  |  |  |  | X | X | X
Alarm | 1005 | 8 | 301006 | 04 | 2210 | MB close failure | BOOL |  |  |  |  | X | X | X
Alarm | 1005 | 9 | 301006 | 04 | 2220 | MB pos. failure | BOOL |  |  |  |  | X | X | X
Alarm | 1005 | 10 | 301006 | 04 | 2270 | Close before excitation failure | BOOL | [5 empty] | X | X
AC alarm | 1005 | 11 | 301006 | 04 | 2155 | Phase seq. failure B | BOOL |  |  |  | X | X | X | X
Alarm | 1006 | 0 | 301007 | 04 | 2560 | GOVERNOR regulation fail. | BOOL | [5 empty] | X | X
Alarm | 1006 | 1 | 301007 | 04 | 2630 | Deload error | BOOL | [5 empty] | X | X
Alarm | 1006 | 2 | 301007 | 04 | 2680 | AVR regulation fail. | BOOL | [5 empty] | X | X
Alarm | 1007 | 0 | 301008 | 04 | 3000 | Digital alarm input 39 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 1 | 301008 | 04 | 3010 | Digital alarm input 40 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 2 | 301008 | 04 | 3020 | Digital alarm input 41 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 3 | 301008 | 04 | 3030 | Digital alarm input 42 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 4 | 301008 | 04 | 3040 | Digital alarm input 43 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 5 | 301008 | 04 | 3050 | Digital alarm input 44 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 6 | 301008 | 04 | 3060 | Digital alarm input 45 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 7 | 301008 | 04 | 3070 | Digital alarm input 46 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 8 | 301008 | 04 | 3080 | Digital alarm input 47 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 9 | 301008 | 04 | 3090 | Digital alarm input 48 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 10 | 301008 | 04 | 3100 | Digital alarm input 49 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1007 | 11 | 301008 | 04 | 3110 | Digital alarm input 50 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1010 | 12 | 301011 | 04 | 3490 | Digital alarm input 4 (Emergency stop) | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 7 | 301012 | 04 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 8 | 301012 | 04 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 9 | 301012 | 04 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 10 | 301012 | 04 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 11 | 301012 | 04 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 12 | 301012 | 04 | 3620 | M-Logic extended alarm 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 13 | 301012 | 04 | 3630 | M-Logic extended alarm 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 14 | 301012 | 04 | 3640 | M-Logic extended alarm 3 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1011 | 15 | 301012 | 04 | 3650 | M-Logic extended alarm 4 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 0 | 301014 | 04 | 4120 | Multi input terminal 20.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 1 | 301014 | 04 | 4130 | Multi input terminal 20.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 2 | 301014 | 04 | 4140 | W. fail. 20 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 3 | 301014 | 04 | 4150 | Multi input terminal 21.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 4 | 301014 | 04 | 4160 | Multi input terminal 21.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 5 | 301014 | 04 | 4170 | W. fail. 21 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 6 | 301014 | 04 | 4180 | Multi input terminal 22.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 7 | 301014 | 04 | 4190 | Multi input terminal 22.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 8 | 301014 | 04 | 4200 | W. fail. 22 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1013 | 9 | 301014 | 04 | 4510 | Overspeed 1 | BOOL | [5 empty] | X | X | X
Alarm | 1013 | 10 | 301014 | 04 | 4520 | Overspeed 2 | BOOL | [5 empty] | X | X | X
Alarm | 1013 | 11 | 301014 | 04 | 4530 | Crank failure | BOOL | [5 empty] | X | X | X
Alarm | 1013 | 12 | 301014 | 04 | 4540 | Running feedback failure | BOOL | [5 empty] | X | X | X
Alarm | 1013 | 13 | 301014 | 04 | 4550 | MPU wire failure | BOOL | [5 empty] | X | X | X
Alarm | 1013 | 14 | 301014 | 04 | 4560 | Hz/V failure | BOOL | [5 empty] | X | X
Alarm | 1013 | 15 | 301014 | 04 | 4570 | Start failure | BOOL | [5 empty] | X | X | X
Alarm | 1014 | 0 | 301015 | 04 | 4580 | Stop failure | BOOL | [5 empty] | X | X | X
Alarm | 1014 | 1 | 301015 | 04 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1014 | 2 | 301015 | 04 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1014 | 5 | 301015 | 04 | 4590 | Underspeed 1 | BOOL | [5 empty] | X | X | X
Alarm | 1014 | 6 | 301015 | 04 | 4210 | Multi input terminal 23.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1014 | 7 | 301015 | 04 | 4220 | Multi input terminal 23.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1014 | 8 | 301015 | 04 | 4230 | W. fail. 23 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1015 | 0 | 301016 | 04 | 6110 | Service timer 1 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 1 | 301016 | 04 | 6120 | Service timer 2 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 2 | 301016 | 04 | 6270 | Stop coil wire break | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 4 | 301016 | 04 | 6330 | Engine heater 1 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 5 | 301016 | 04 | 6410 | Battery test | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 6 | 301016 | 04 | 6440 | Battery asymmetry 1 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 7 | 301016 | 04 | 6450 | Battery asymmetry 2 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 8 | 301016 | 04 | 6470 | Max. ventilation 1 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 9 | 301016 | 04 | 6480 | Max. ventilation 2 | BOOL | [5 empty] | X | X | X
Alarm | 1015 | 10 | 301016 | 04 | 6500 | Block switchboard error | BOOL | [5 empty] | X | X
Alarm | 1015 | 11 | 301016 | 04 | 6510 | Stop switchboard error | BOOL | [5 empty] | X | X
Alarm | 1015 | 12 | 301016 | 04 | 6540 | Unit not in auto | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1015 | 13 | 301016 | 04 | 6550 | Fuel pump logic | BOOL | [5 empty] | X | X | X
Relay state | 1016 | 0 | 301017 | 04 | 5000 | Relay 5 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 1 | 301017 | 04 | 5000 | Relay 6 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 2 | 301017 | 04 | 5000 | Relay 9 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 3 | 301017 | 04 | 5000 | Relay 10 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 4 | 301017 | 04 | 5000 | Relay 11 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 5 | 301017 | 04 | 5000 | Relay 12 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 6 | 301017 | 04 | 5000 | Relay 13 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 7 | 301017 | 04 | 5000 | Relay 14 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 8 | 301017 | 04 | 5080 | Relay 15 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 9 | 301017 | 04 | 8090 | Relay 16 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 10 | 301017 | 04 | 5100 | Relay 17 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1016 | 11 | 301017 | 04 | 5110 | Relay 18 | BOOL |  |  |  | X | X | X | X | X | X
Relay state | 1017 | 12 | 301018 | 04 |  | Run. coil relay | BOOL | [5 empty] | X | X | X
Relay state | 1017 | 13 | 301018 | 04 |  | Start prepare | BOOL | [5 empty] | X | X | X
Relay state | 1017 | 14 | 301018 | 04 |  | Start relay | BOOL | [5 empty] | X | X | X
Relay state | 1017 | 15 | 301018 | 04 |  | Stop coil relay | BOOL | [5 empty] | X | X | X
Plant logic state | 1018 | 0 | 301019 | 04 |  | Mains failure (Single DG) | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 0 | 301019 | 04 |  | Mains failure | BOOL |  |  |  |  | X
Plant logic state | 1018 | 1 | 301019 | 04 |  | MB position ON (Single DG) | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 1 | 301019 | 04 |  | MB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 2 | 301019 | 04 |  | DG ramp down | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 3 | 301019 | 04 |  | Start GOV/AVR regulation | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | GB position ON | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | TB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | BTB position ON | BOOL |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | GB synchronising | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | TB synchronising | BOOL |  |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | BTB synchronising | BOOL |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 04 |  | Engine running | BOOL | [5 empty] | X | X | X
Plant logic state | 1018 | 7 | 301019 | 04 | 6173 | Running detected, timer expired | BOOL | [5 empty] | X | X | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | DG Hz/V OK, timer expired | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | BB Hz/V OK, timer expired | BOOL |  |  |  | X | X
Plant logic state | 1018 | 9 | 301019 | 04 | 6410 | Battery test ongoing | BOOL | [5 empty] | X | X | X
Plant logic state | 1018 | 10 | 301019 | 04 |  | Shutdown override active | BOOL | [5 empty] | X | X | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | GB position OFF | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | TB position OFF | BOOL |  |  |  |  | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | BTB position OFF | BOOL |  |  |  | X
Plant logic state | 1018 | 12 | 301019 | 04 |  | MB position OFF | BOOL |  |  |  |  | X | X | X
Plant logic state | 1018 | 13 | 301019 | 04 |  | BB Hz/V OK | BOOL |  |  |  | X | X | X | X
Plant logic state | 1018 | 14 | 301019 | 04 |  | Single DG, MB synchronising | BOOL | [5 empty] | X | X
Plant logic state | 1018 | 14 | 301019 | 04 |  | Mains, MB synchronising | BOOL |  |  |  |  | X
Modes | 1018 | 15 | 301019 | 04 |  | Dry mode | BOOL | [5 empty] | X | X
Modes | 1019 | 0 | 301020 | 04 |  | BLOCK mode | BOOL |  |  |  | X | X | X | X | X | X
Modes | 1019 | 1 | 301020 | 04 |  | No Regulation mode | BOOL | [5 empty] | X | X | X
Modes | 1019 | 2 | 301020 | 04 |  | MANUAL mode | BOOL |  |  |  | X | X | X | X | X
Modes | 1019 | 3 | 301020 | 04 |  | AUTO mode | BOOL |  |  |  | X | X | X | X | X
Modes | 1019 | 4 | 301020 | 04 |  | TEST | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 5 | 301020 | 04 |  | Island | BOOL |  |  |  |  | X | X | X | X
Modes | 1019 | 6 | 301020 | 04 |  | AMF | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 7 | 301020 | 04 |  | Peak shaving | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 8 | 301020 | 04 |  | Fixed power | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 9 | 301020 | 04 |  | Mains power export | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 10 | 301020 | 04 |  | Load takeover | BOOL |  |  |  |  | X | X | X
Modes | 1019 | 11 | 301020 | 04 |  | Power management | BOOL | [5 empty] | X | X
Modes | 1019 | 15 | 301020 | 04 |  | AMF active | BOOL |  |  |  |  | X | X | X
EIC alarm | 1020 | 0 | 301021 | 04 | 7570 | Communication Error | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 1 | 301021 | 04 | 7580 | Warning / Yellow alarm | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 2 | 301021 | 04 | 7590 | Shutdown / Red alarm | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 3 | 301021 | 04 | 7600 | Over-speed | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 4 | 301021 | 04 | 7610 | Coolant water temperature 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 5 | 301021 | 04 | 7620 | Coolant water temperature 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 6 | 301021 | 04 | 7630 | Oil pressure 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 7 | 301021 | 04 | 7640 | Oil pressure 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 8 | 301021 | 04 | 7650 | Oil temperature 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 9 | 301021 | 04 | 7660 | Oil temperature 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 10 | 301021 | 04 | 7670 | Coolant water level 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 11 | 301021 | 04 | 7680 | Coolant water level 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 12 | 301021 | 04 | 7690 | Cylinder exhaust difference 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1020 | 13 | 301021 | 04 | 7700 | Cylinder exhaust difference 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1021 | 0 | 301022 | 04 |  | ECU alarm bit 49 | BOOL | [5 empty] | X | X | X
EIC alarm | 1021 | 1 | 301022 | 04 |  | ECU alarm bit 50 | BOOL | [5 empty] | X | X | X
EIC alarm | 1021 | 12 | 301022 | 04 |  | Protection lamp | BOOL | [5 empty] | X | X | X
EIC alarm | 1021 | 13 | 301022 | 04 |  | Malfunction lamp | BOOL | [5 empty] | X | X | X
EIC alarm | 1021 | 14 | 301022 | 04 |  | Yellow lamp | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 0 | 301023 | 04 |  | ECU alarm bit 33 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 1 | 301023 | 04 |  | ECU alarm bit 34 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 2 | 301023 | 04 |  | ECU alarm bit 35 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 3 | 301023 | 04 |  | ECU alarm bit 36 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 4 | 301023 | 04 |  | ECU alarm bit 37 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 5 | 301023 | 04 |  | ECU alarm bit 38 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 6 | 301023 | 04 |  | ECU alarm bit 39 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 7 | 301023 | 04 |  | ECU alarm bit 40 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 8 | 301023 | 04 |  | ECU alarm bit 41 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 9 | 301023 | 04 |  | ECU alarm bit 42 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 10 | 301023 | 04 |  | ECU alarm bit 43 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 11 | 301023 | 04 |  | ECU alarm bit 44 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 12 | 301023 | 04 |  | ECU alarm bit 45 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 13 | 301023 | 04 |  | ECU alarm bit 46 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 14 | 301023 | 04 |  | ECU alarm bit 47 | BOOL | [5 empty] | X | X | X
EIC alarm | 1022 | 15 | 301023 | 04 |  | ECU alarm bit 48 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 0 | 301024 | 04 |  | ECU alarm bit 17 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 1 | 301024 | 04 |  | ECU alarm bit 18 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 2 | 301024 | 04 |  | ECU alarm bit 19 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 3 | 301024 | 04 |  | ECU alarm bit 20 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 4 | 301024 | 04 |  | ECU alarm bit 21 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 5 | 301024 | 04 |  | ECU alarm bit 22 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 6 | 301024 | 04 |  | ECU alarm bit 23 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 7 | 301024 | 04 |  | ECU alarm bit 24 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 8 | 301024 | 04 |  | ECU alarm bit 25 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 9 | 301024 | 04 |  | ECU alarm bit 26 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 10 | 301024 | 04 |  | ECU alarm bit 27 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 11 | 301024 | 04 |  | ECU alarm bit 28 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 12 | 301024 | 04 |  | ECU alarm bit 29 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 13 | 301024 | 04 |  | ECU alarm bit 30 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 14 | 301024 | 04 |  | ECU alarm bit 31 | BOOL | [5 empty] | X | X | X
EIC alarm | 1023 | 15 | 301024 | 04 |  | ECU alarm bit 32 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 0 | 301025 | 04 |  | ECU alarm bit 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 1 | 301025 | 04 |  | ECU alarm bit 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 2 | 301025 | 04 |  | ECU alarm bit 3 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 3 | 301025 | 04 |  | ECU alarm bit 4 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 4 | 301025 | 04 |  | ECU alarm bit 5 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 5 | 301025 | 04 |  | ECU alarm bit 6 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 6 | 301025 | 04 |  | ECU alarm bit 7 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 7 | 301025 | 04 |  | ECU alarm bit 8 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 8 | 301025 | 04 |  | ECU alarm bit 9 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 9 | 301025 | 04 |  | ECU alarm bit 10 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 10 | 301025 | 04 |  | ECU alarm bit 11 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 11 | 301025 | 04 |  | ECU alarm bit 12 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 12 | 301025 | 04 |  | ECU alarm bit 13 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 13 | 301025 | 04 |  | ECU alarm bit 14 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 14 | 301025 | 04 |  | ECU alarm bit 15 | BOOL | [5 empty] | X | X | X
EIC alarm | 1024 | 15 | 301025 | 04 |  | ECU alarm bit 16 | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 0 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Overreving | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 1 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Speed sensor 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 2 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Speed sensor 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 3 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Water temperature sensor | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 4 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Charge air temperature sensor | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 5 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Charge air pressure sensor | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 6 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil temperature sensor | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 7 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure sensor | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 8 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Fault in cor. | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 9 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Throttle pedal | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 10 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Emergency stop o.r | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 11 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 12 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Wrong parameter | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 13 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Battery voltage | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 14 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Oil pressure protection | BOOL | [5 empty] | X | X | X
EIC alarm | 1026 | 15 | 301027 | 04 |  | Scania EMS 2 KWP2000 - Emergency stop cor | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 0 | 301028 | 04 |  | Scania EMS 2 KWP2000 - CAN-circuit defect | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 1 | 301028 | 04 |  | Scania EMS 2 KWP2000 - CAN message DLN1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 2 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Wrong CAN version | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 3 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 1 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 4 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 2 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 5 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 3 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 6 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 4 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 7 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 5 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 8 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 6 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 9 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 7 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 10 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Un. inj. cyl. 8 | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 11 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Extra analogue input | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 12 | 301028 | 04 |  | Scania EMS 2 KWP2000 - System shutdown | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 13 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Coolant l. protection | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 14 | 301028 | 04 |  | Scania EMS 2 KWP2000 - hardware watchdog | BOOL | [5 empty] | X | X | X
EIC alarm | 1027 | 15 | 301028 | 04 |  | Scania EMS 2 KWP2000 - Fault in RAM | BOOL | [5 empty] | X | X | X
EIC alarm | 1028 | 0 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Seal | BOOL | [5 empty] | X | X | X
EIC alarm | 1028 | 1 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Coolant shut off | BOOL | [5 empty] | X | X | X
EIC alarm | 1028 | 2 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Over heat protection | BOOL | [5 empty] | X | X | X
EIC alarm | 1028 | 3 | 301029 | 04 |  | Scania EMS 2 KWP2000 - Fault in TPU | BOOL | [5 empty] | X | X | X
PM alarm | 1031 | 1 | 301032 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 2 | 301032 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 3 | 301032 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 4 | 301032 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 5 | 301032 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 6 | 301032 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 7 | 301032 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 8 | 301032 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 9 | 301032 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 10 | 301032 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 11 | 301032 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 12 | 301032 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 13 | 301032 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 14 | 301032 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1031 | 15 | 301032 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 0 | 301033 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 2 | 301033 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 3 | 301033 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 4 | 301033 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 5 | 301033 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 6 | 301033 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 7 | 301033 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 8 | 301033 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 9 | 301033 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 10 | 301033 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 11 | 301033 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 12 | 301033 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 13 | 301033 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 14 | 301033 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1032 | 15 | 301033 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1033 | 0 | 301034 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1033 | 1 | 301034 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
Alarm | 1033 | 2 | 301034 | 04 | 7520 | Communication error ext. | BOOL |  |  |  | X | X | X | X | X | X
PM alarm | 1034 | 1 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 2 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 3 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 4 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 5 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 6 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 7 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 8 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 9 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 10 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 11 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 12 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 13 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 14 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1034 | 15 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1035 | 0 | 301036 | 04 |  | Ext. Modbus comm. error, CAN ID 16 | BOOL |  |  |  | X | X | X
Alarm | 1036 | 0 | 301037 | 04 | 12000 | Ext. Analogue in. 1.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 1 | 301037 | 04 | 12010 | Ext. Analogue in. 1.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 3 | 301037 | 04 | 12030 | Ext. Analogue in. 2.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 4 | 301037 | 04 | 12040 | Ext. Analogue in. 2.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 6 | 301037 | 04 | 12060 | Ext. Analogue in. 3.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 7 | 301037 | 04 | 12070 | Ext. Analogue in. 3.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 9 | 301037 | 04 | 12090 | Ext. Analogue in. 4.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 10 | 301037 | 04 | 12100 | Ext. Analogue in. 4.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 12 | 301037 | 04 | 12120 | Ext. Analogue in. 5.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 13 | 301037 | 04 | 12130 | Ext. Analogue in. 5.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1036 | 15 | 301037 | 04 | 12150 | Ext. Analogue in. 6.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1037 | 0 | 301038 | 04 | 12160 | Ext. Analogue in. 6.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1037 | 2 | 301038 | 04 | 12180 | Ext. Analogue in. 7.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1037 | 3 | 301038 | 04 | 12190 | Ext. Analogue in. 7.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1037 | 5 | 301038 | 04 | 12210 | Ext. Analogue in. 8.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1037 | 6 | 301038 | 04 | 12220 | Ext. Analogue in. 8.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 0 | 301039 | 04 | 12540 | External digital input 1/CIO 116-1 digital input 10 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 1 | 301039 | 04 | 12550 | External digital input 2/CIO 116-1 digital input 11 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 2 | 301039 | 04 | 12560 | External digital input 3/CIO 116-1 digital input 12 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 3 | 301039 | 04 | 12570 | External digital input 4/CIO 116-1 digital input 13 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 4 | 301039 | 04 | 12580 | External digital input 5/CIO 116-1 digital input 14 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 5 | 301039 | 04 | 12590 | External digital input 6/CIO 116-1 digital input 15 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 6 | 301039 | 04 | 12600 | External digital input 7/CIO 116-1 digital input 16 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 7 | 301039 | 04 | 12610 | External digital input 8/CIO 116-1 digital input 17 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 8 | 301039 | 04 | 12620 | External digital input 9/CIO 116-1 digital input 19 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 9 | 301039 | 04 | 12630 | External digital input 10/CIO 116-1 digital input 20 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 10 | 301039 | 04 | 12640 | External digital input 11/CIO 116-1 digital input 21 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 11 | 301039 | 04 | 12650 | External digital input 12/CIO 116-1 digital input 22 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 12 | 301039 | 04 | 12660 | External digital input 13/CIO 116-1 digital input 23 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 13 | 301039 | 04 | 12670 | External digital input 14/CIO 116-1 digital input 24 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 14 | 301039 | 04 | 12680 | External digital input 15/CIO 116-1 digital input 25 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1038 | 15 | 301039 | 04 | 12690 | External digital input 16/CIO 116 no.1 digital input 26 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 0 | 301040 | 04 | 12790 | External digital output 1/CIO 208-1 digital output 9 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 1 | 301040 | 04 | 12800 | External digital output 2/CIO 208-1 digital output 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 2 | 301040 | 04 | 12810 | External digital output 3/CIO 208-1 digital output 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 3 | 301040 | 04 | 12820 | External digital output 4/CIO 208-1 digital output 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 4 | 301040 | 04 | 12830 | External digital output 5/CIO 208-1 digital output 18 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 5 | 301040 | 04 | 12840 | External digital output 6/CIO 208-1 digital output 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 6 | 301040 | 04 | 12850 | External digital output 7/CIO 208-1 digital output 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 7 | 301040 | 04 | 12860 | External digital output 8/CIO 208-1 digital output 27 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 8 | 301040 | 04 | 12870 | External digital output 9/CIO 208-2 digital output 9 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 9 | 301040 | 04 | 12880 | External digital output 10/CIO 208-2 digital output 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 10 | 301040 | 04 | 12890 | External digital output 11/CIO 208-2 digital output 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 11 | 301040 | 04 | 12900 | External digital output 12/CIO 208-2 digital output 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 12 | 301040 | 04 | 12910 | External digital output 13/CIO 208-2 digital output 18 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 13 | 301040 | 04 | 12920 | External digital output 14/CIO 208-2 digital output 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 14 | 301040 | 04 | 12930 | External digital output 15/CIO 208-2 digital output 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1039 | 15 | 301040 | 04 | 12940 | External digital output 16/CIO 208-2 digital output 27 | BOOL |  |  |  | X | X | X | X | X | X
PM alarm | 1040 | 0 | 301041 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 1 | 301041 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 2 | 301041 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 3 | 301041 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 4 | 301041 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 5 | 301041 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 6 | 301041 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 7 | 301041 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 8 | 301041 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 9 | 301041 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 10 | 301041 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 11 | 301041 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 12 | 301041 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 13 | 301041 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 14 | 301041 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1040 | 15 | 301041 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 0 | 301042 | 04 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 1 | 301042 | 04 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 2 | 301042 | 04 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 3 | 301042 | 04 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 4 | 301042 | 04 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 5 | 301042 | 04 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 6 | 301042 | 04 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 7 | 301042 | 04 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 8 | 301042 | 04 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 9 | 301042 | 04 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 10 | 301042 | 04 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 11 | 301042 | 04 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 12 | 301042 | 04 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 13 | 301042 | 04 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 14 | 301042 | 04 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1041 | 15 | 301042 | 04 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 0 | 301043 | 04 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 1 | 301043 | 04 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 2 | 301043 | 04 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 3 | 301043 | 04 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 4 | 301043 | 04 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 5 | 301043 | 04 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 6 | 301043 | 04 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1042 | 7 | 301043 | 04 |  | CAN 1 missing ID 40 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 0 | 301044 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 1 | 301044 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 2 | 301044 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 3 | 301044 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 4 | 301044 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 5 | 301044 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 6 | 301044 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 7 | 301044 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 8 | 301044 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 9 | 301044 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 10 | 301044 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 11 | 301044 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 12 | 301044 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 13 | 301044 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 14 | 301044 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X | X
PM alarm | 1043 | 15 | 301044 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 0 | 301045 | 04 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 1 | 301045 | 04 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 2 | 301045 | 04 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 3 | 301045 | 04 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 4 | 301045 | 04 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 5 | 301045 | 04 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 6 | 301045 | 04 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 7 | 301045 | 04 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 8 | 301045 | 04 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 9 | 301045 | 04 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 10 | 301045 | 04 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 11 | 301045 | 04 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 12 | 301045 | 04 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 13 | 301045 | 04 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 14 | 301045 | 04 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1044 | 15 | 301045 | 04 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 0 | 301046 | 04 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 1 | 301046 | 04 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 2 | 301046 | 04 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 3 | 301046 | 04 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 4 | 301046 | 04 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 5 | 301046 | 04 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 6 | 301046 | 04 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1045 | 7 | 301046 | 04 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X | X | X
Plant logic state | 1050 | 0 | 301051 | 04 |  | Ready to autostart | BOOL | [5 empty] | X | X | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | Mains U > 30% of U nominal | BOOL |  |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | GEN U > 30% of U nominal | BOOL | [5 empty] | X | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | BA U > 30% of U nominal | BOOL |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 04 |  | BB U > 30% of U nominal | BOOL |  |  |  | X | X | X | X
Plant logic state | 1050 | 3 | 301051 | 04 |  | Power derate state/active | BOOL | [5 empty] | X | X
Plant logic state | 1050 | 4 | 301051 | 04 |  | ATS BTB position ON | BOOL | [8 empty] | X
Plant logic state | 1050 | 5 | 301051 | 04 |  | ATS BTB position OFF | BOOL | [8 empty] | X
Plant logic state | 1050 | 6 | 301051 | 04 |  | ATS BTB synchronising | BOOL | [8 empty] | X
Plant logic state | 1050 | 14 | 301051 | 04 |  | This unit using analogue LS instead of PMS | BOOL | [5 empty] | X
Plant logic state | 1050 | 15 | 301051 | 04 |  | Any unit using analogue LS instead of PMS | BOOL | [5 empty] | X
M-Logic state | 1051 |  | 301052 | 04 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1052 |  | 301053 | 04 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X | X | X | X | X
Alarm | 1053 | 0 | 301054 | 04 | 6590 | Fan A Failure | BOOL | [5 empty] | X | X
Alarm | 1053 | 1 | 301054 | 04 | 6600 | Fan B Failure | BOOL | [5 empty] | X | X
Alarm | 1053 | 2 | 301054 | 04 | 6610 | Fan C Failure | BOOL | [5 empty] | X | X
Alarm | 1053 | 3 | 301054 | 04 | 6620 | Fan D Failure | BOOL | [5 empty] | X | X
Alarm | 1053 | 4 | 301054 | 04 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 5 | 301054 | 04 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 6 | 301054 | 04 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 7 | 301054 | 04 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 8 | 301054 | 04 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 9 | 301054 | 04 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 10 | 301054 | 04 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 11 | 301054 | 04 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 12 | 301054 | 04 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 13 | 301054 | 04 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 14 | 301054 | 04 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1053 | 15 | 301054 | 04 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
AC alarm | 1054 | 0 | 301055 | 04 |  | In> inverse | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 1 | 301055 | 04 |  | Ie> inverse | BOOL |  |  |  | X | X | X | X
Alarm | 1054 | 3 | 301055 | 04 | 6352 | External Engine Stop | BOOL | [5 empty] | X | X | X
AC alarm | 1054 | 4 | 301055 | 04 | 1710 | Unbalance curr. 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 5 | 301055 | 04 | 7480 | Avg U BB > 1 | BOOL |  |  |  |  | X | X | X
AC alarm | 1054 | 6 | 301055 | 04 | 7490 | Avg U BB > 2 | BOOL |  |  |  |  | X | X | X
AC alarm | 1054 | 7 | 301055 | 04 | 7440 | 4th CT -P> 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 8 | 301055 | 04 | 7450 | 4th CT -P> 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 9 | 301055 | 04 | 7460 | 4th CT P> 1 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 10 | 301055 | 04 | 7470 | 4th CT P> 2 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 11 | 301055 | 04 | 1920 | BB f> 4 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 12 | 301055 | 04 | 1930 | BB f< 5 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 13 | 301055 | 04 | 1940 | BB U> 4 | BOOL |  |  |  | X | X | X | X
AC alarm | 1054 | 14 | 301055 | 04 | 1950 | BB U< 5 | BOOL |  |  |  | X | X | X | X
DAVR Alarm | 1056 | 0 | 301057 | 04 | 7830 | Digital AVR Communication Error | BOOL | [5 empty] | X | X
DAVR Alarm | 1056 | 1 | 301057 | 04 | 7761 | Digital AVR Warning | BOOL | [5 empty] | X | X
DAVR Alarm | 1056 | 2 | 301057 | 04 | 7763 | Digital AVR Trip | BOOL | [5 empty] | X | X
Alarm | 1056 | 13 | 301057 | 04 | 18000 | SDU status OK error | BOOL | [7 empty] | X
Alarm | 1056 | 14 | 301057 | 04 | 18010 | SDU warning | BOOL | [7 empty] | X
Alarm | 1056 | 15 | 301057 | 04 | 18020 | SDU comm I/F error | BOOL | [7 empty] | X
Alarm | 1057 | 0 | 301058 | 04 |  | Fail class: Block start | BOOL | [7 empty] | X
Alarm | 1057 | 0 | 301058 | 04 |  | Fail class: Block start + breaker on | BOOL |  |  |  | X | X | X | X
Alarm | 1057 | 1 | 301058 | 04 |  | Fail class: Warning | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip GB | BOOL | [5 empty] | X | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip BTB | BOOL |  |  |  | X | X
Alarm | 1057 | 3 | 301058 | 04 |  | Fail class: Trip GB + stop with cooling down | BOOL | [5 empty] | X | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Shutdown | BOOL | [7 empty] | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Trip GB + stop without cooling down | BOOL | [5 empty] | X | X
Alarm | 1057 | 5 | 301058 | 04 |  | Fail class: Trip MB | BOOL |  |  |  |  | X | X | X
Alarm | 1057 | 6 | 301058 | 04 |  | Fail class: Safety stop | BOOL | [5 empty] | X | X
Alarm | 1057 | 7 | 301058 | 04 |  | Fail class: If MB present Trip MB else Trip GB | BOOL | [5 empty] | X | X
Alarm | 1057 | 7 | 301058 | 04 |  | Fail class: If MB present Trip MB else Trip TB | BOOL |  |  |  |  | X
Alarm | 1057 | 8 | 301058 | 04 |  | Fail class: Controlled stop (deload + cooldown) | BOOL | [5 empty] | X | X
Alarm | 1057 | 9 | 301058 | 04 |  | Fail class: PV shutdown (Hybrid only) | BOOL | [6 empty] | X
M-Logic state | 1058 |  | 301059 | 04 |  | Virtual events 33-48 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1059 |  | 301060 | 04 |  | Virtual events 49-64 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1060 |  | 301061 | 04 |  | Virtual events 65-80 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1061 |  | 301062 | 04 |  | Virtual events 81-96 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1062 |  | 301063 | 04 |  | Flipflop output 1-16 | INT16s | AB | 0 |  | X | X | X | X | X | X
Alarm | 1063 | 0 | 301064 | 04 |  | Avg L-L AC RMS voltage High 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 1 | 301064 | 04 |  | Avg L-L AC RMS voltage High 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 2 | 301064 | 04 |  | Avg L-L AC RMS voltage Low 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 3 | 301064 | 04 |  | Avg L-L AC RMS voltage Low 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 4 | 301064 | 04 |  | Avg L-N AC RMS voltage High 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 5 | 301064 | 04 |  | Avg L-N AC RMS voltage High 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 6 | 301064 | 04 |  | Avg L-N AC RMS voltage Low 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 7 | 301064 | 04 |  | Avg L-N AC RMS voltage Low 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 8 | 301064 | 04 |  | Average AC frequency High 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 9 | 301064 | 04 |  | Average AC frequency High 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 10 | 301064 | 04 |  | Average AC frequency Low 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 11 | 301064 | 04 |  | Average AC frequency Low 2 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 12 | 301064 | 04 |  | Average AC RMS current High 1 | BOOL |  |  |  | X | X | X | X
Alarm | 1063 | 13 | 301064 | 04 |  | Average AC RMS current High 2 | BOOL |  |  |  | X | X | X | X
EIC state | 1068 | 0 | 301069 | 04 |  | M-Logic command: Reset trip fuel | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 1 | 301069 | 04 |  | M-Logic command: MTU Alternate droop setting | BOOL | [5 empty] | X | X | X
Plant logic state | 1068 | 2 | 301069 | 04 |  | Nominal frequency 50/60Hz | BOOL |  |  |  | X | X | X | X
Plant logic state | 1068 | 3 | 301069 | 04 |  | Idle run active | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 5 | 301069 | 04 |  | Engine start | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 6 | 301069 | 04 |  | Engine stop | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 7 | 301069 | 04 |  | Disable Engine Cylinder Cutoff2 | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 8 | 301069 | 04 |  | M-Logic command: Engine overspeed test | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 9 | 301069 | 04 |  | M-Logic command: Intermittent Oil Priming | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 10 | 301069 | 04 |  | Engine preheat active | BOOL | [5 empty] | X | X | X
EIC state | 1068 | 11 | 301069 | 04 |  | CVT transmission enabled | BOOL | [5 empty] | X | X | X
Alarm | 1074 | 0 | 301075 | 04 | 4750 | Delta analogue 7 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1074 | 1 | 301075 | 04 | 4760 | Delta analogue 7 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1074 | 2 | 301075 | 04 | 4770 | Delta analogue 8 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1074 | 3 | 301075 | 04 | 4780 | Delta analogue 8 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1074 | 4 | 301075 | 04 | 4790 | Delta analogue 9 - fail 1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1074 | 5 | 301075 | 04 | 4800 | Delta analogue 9 - fail 2 | BOOL |  |  |  | X | X | X | X | X | X
EIC state | 1076 |  | 301077 | 04 |  | JCB: Dosing Module Status | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1077 |  | 301078 | 04 |  | JCB: Actual Reducing Agent Quantity | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1078 |  | 301079 | 04 |  | JCB: Aftertreatment Lamp | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1079 |  | 301080 | 04 |  | JCB: Refresh Status Byte | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1080 |  | 301081 | 04 |  | JCB: SCR Monitor | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1081 |  | 301082 | 04 |  | JCB: Successful Running Refreshes | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1082 |  | 301083 | 04 |  | JCB: Successful Stationary Refreshes | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1083 |  | 301084 | 04 |  | JCB: Engine Rating | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1085 |  | 301086 | 04 |  | Emergency Shutdown Indication | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1086 |  | 301087 | 04 |  | Humidity Derate Percentage | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1087 |  | 301088 | 04 |  | Volvo Penta: Number of EIO Activations | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1088 |  | 301089 | 04 |  | Volvo Penta: Accumulated EIO time | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1089 |  | 301090 | 04 |  | Volvo Penta: Time left of EIO Operation | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1092 |  | 301093 | 04 |  | HATZ: Remaining Service Hours | INT16s | AB | 0 |  |  |  | X | X | X
EIC state | 1093 | 0 | 301094 | 04 |  | HATZ: Engine Running | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 1 | 301094 | 04 |  | HATZ: Service Delay | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 2 | 301094 | 04 |  | HATZ: Pre-glow Active | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 3 | 301094 | 04 |  | HATZ: Oil Pressure Missing | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 4 | 301094 | 04 |  | HATZ: Engine Diagnostic Lamp | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 5 | 301094 | 04 |  | HATZ: Engine Over temperature | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 6 | 301094 | 04 |  | HATZ: Air Filter Switch | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 7 | 301094 | 04 |  | HATZ: DPF Regeneration Not Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 8 | 301094 | 04 |  | HATZ: DPF Regeneration Inhibit Park Brake Not Set | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 9 | 301094 | 04 |  | HATZ: DPF Regeneration Not Inhibit Out Of Neutral | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 10 | 301094 | 04 |  | HATZ: DPF Regeneration Inhibit Out Of Neutral | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 11 | 301094 | 04 |  | HATZ: Parking Brake Switch | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 12 | 301094 | 04 |  | HATZ: Brake Switch | BOOL | [5 empty] | X | X | X
EIC state | 1093 | 13 | 301094 | 04 |  | HATZ: Transmission Neutral Switch | BOOL | [5 empty] | X | X | X
EIC measurement | 1094 |  | 301095 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1095 |  | 301096 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1096 |  | 301097 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1097 |  | 301098 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1098 |  | 301099 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1099 |  | 301100 | 04 |  | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature (SPN 4765) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1100 |  | 301101 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1101 |  | 301102 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1102 |  | 301103 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1103 |  | 301104 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1104 |  | 301105 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1105 |  | 301106 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1106 |  | 301107 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1107 |  | 301108 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1108 |  | 301109 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1109 |  | 301110 | 04 |  | See DRH manual | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1110 |  | 301111 | 04 |  | Isuzu: Escape Mode Enable Flag | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1111 |  | 301112 | 04 |  | Isuzu: Inducement Level | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1112 |  | 301113 | 04 |  | Isuzu: UREA Tank Level | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1113 |  | 301114 | 04 |  | Isuzu: UREA Tank Level Indicator | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1114 |  | 301115 | 04 |  | Isuzu: Level Indicator (Amber) Action | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1115 |  | 301116 | 04 |  | Isuzu: DPF Amber Lamp Mode | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1116 |  | 301117 | 04 |  | Isuzu: Exhaust system lamp | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1117 |  | 301118 | 04 |  | Isuzu: DPF Green Lamp Mode | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1118 |  | 301119 | 04 |  | Isuzu: NO POWER Lamp | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1119 |  | 301120 | 04 |  | Isuzu: Output Limitation | INT16s | AB | 0 |  |  |  | X | X | X
M-Logic state | 1128 |  | 301129 | 04 |  | Virtual toggle status 1-16 | INT16s | AB | 0 |  | X | X | X | X | X | X
M-Logic state | 1129 |  | 301130 | 04 |  | Virtual toggle status 17-32 | INT16s | AB | 0 |  | X | X | X | X | X | X
Alarm | 1130 | 0 | 301131 | 04 |  | CIO 308-2 Analogue input 8.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 1 | 301131 | 04 |  | CIO 308-2 Analogue input 8.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 2 | 301131 | 04 |  | CIO 308-2 Analogue input 11.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 3 | 301131 | 04 |  | CIO 308-2 Analogue input 11.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 4 | 301131 | 04 |  | CIO 308-2 Analogue input 14.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 5 | 301131 | 04 |  | CIO 308-2 Analogue input 14.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 6 | 301131 | 04 |  | CIO 308-2 Analogue input 17.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 7 | 301131 | 04 |  | CIO 308-2 Analogue input 17.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 8 | 301131 | 04 |  | CIO 308-2 Analogue input 20.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 9 | 301131 | 04 |  | CIO 308-2 Analogue input 20.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 10 | 301131 | 04 |  | CIO 308-2 Analogue input 23.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 11 | 301131 | 04 |  | CIO 308-2 Analogue input 23.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 12 | 301131 | 04 |  | CIO 308-2 Analogue input 26.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 13 | 301131 | 04 |  | CIO 308-2 Analogue input 26.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 14 | 301131 | 04 |  | CIO 308-2 Analogue input 29.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1130 | 15 | 301131 | 04 |  | CIO 308-2 Analogue input 29.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 0 | 301132 | 04 |  | CIO 308-3 Analogue input 8.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 1 | 301132 | 04 |  | CIO 308-3 Analogue input 8.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 2 | 301132 | 04 |  | CIO 308-3 Analogue input 11.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 3 | 301132 | 04 |  | CIO 308-3 Analogue input 11.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 4 | 301132 | 04 |  | CIO 308-3 Analogue input 14.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 5 | 301132 | 04 |  | CIO 308-3 Analogue input 14.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 6 | 301132 | 04 |  | CIO 308-3 Analogue input 17.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 7 | 301132 | 04 |  | CIO 308-3 Analogue input 17.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 8 | 301132 | 04 |  | CIO 308-3 Analogue input 20.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 9 | 301132 | 04 |  | CIO 308-3 Analogue input 20.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 10 | 301132 | 04 |  | CIO 308-3 Analogue input 23.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 11 | 301132 | 04 |  | CIO 308-3 Analogue input 23.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 12 | 301132 | 04 |  | CIO 308-3 Analogue input 26.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 13 | 301132 | 04 |  | CIO 308-3 Analogue input 26.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 14 | 301132 | 04 |  | CIO 308-3 Analogue input 29.1 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1131 | 15 | 301132 | 04 |  | CIO 308-3 Analogue input 29.2 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 0 | 301133 | 04 |  | CIO 116-2 digital input 10 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 1 | 301133 | 04 |  | CIO 116-2 digital input 11 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 2 | 301133 | 04 |  | CIO 116-2 digital input 12 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 3 | 301133 | 04 |  | CIO 116-2 digital input 13 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 4 | 301133 | 04 |  | CIO 116-2 digital input 14 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 5 | 301133 | 04 |  | CIO 116-2 digital input 15 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 6 | 301133 | 04 |  | CIO 116-2 digital input 16 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 7 | 301133 | 04 |  | CIO 116-2 digital input 17 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 8 | 301133 | 04 |  | CIO 116-2 digital input 18 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 9 | 301133 | 04 |  | CIO 116-2 digital input 20 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 10 | 301133 | 04 |  | CIO 116-2 digital input 21 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 11 | 301133 | 04 |  | CIO 116-2 digital input 22 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 12 | 301133 | 04 |  | CIO 116-2 digital input 23 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 13 | 301133 | 04 |  | CIO 116-2 digital input 24 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 14 | 301133 | 04 |  | CIO 116-2 digital input 25 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1132 | 15 | 301133 | 04 |  | CIO 116-2 digital input 26 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 0 | 301134 | 04 |  | CIO 116-3 digital input 10 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 1 | 301134 | 04 |  | CIO 116-3 digital input 11 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 2 | 301134 | 04 |  | CIO 116-3 digital input 12 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 3 | 301134 | 04 |  | CIO 116-3 digital input 13 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 4 | 301134 | 04 |  | CIO 116-3 digital input 14 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 5 | 301134 | 04 |  | CIO 116-3 digital input 15 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 6 | 301134 | 04 |  | CIO 116-3 digital input 16 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 7 | 301134 | 04 |  | CIO 116-3 digital input 17 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 8 | 301134 | 04 |  | CIO 116-3 digital input 19 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 9 | 301134 | 04 |  | CIO 116-3 digital input 20 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 10 | 301134 | 04 |  | CIO 116-3 digital input 21 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 11 | 301134 | 04 |  | CIO 116-3 digital input 22 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 12 | 301134 | 04 |  | CIO 116-3 digital input 23 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 13 | 301134 | 04 |  | CIO 116-3 digital input 24 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 14 | 301134 | 04 |  | CIO 116-3 digital input 25 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1133 | 15 | 301134 | 04 |  | CIO 116-3 digital input 26 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 0 | 301137 | 04 |  | CIO 208-3 digital output 9 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 1 | 301137 | 04 |  | CIO 208-3 digital output 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 2 | 301137 | 04 |  | CIO 208-3 digital output 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 3 | 301137 | 04 |  | CIO 208-3 digital output 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 4 | 301137 | 04 |  | CIO 208-3 digital output 18 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 5 | 301137 | 04 |  | CIO 208-3 digital output 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 6 | 301137 | 04 |  | CIO 208-3 digital output 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1136 | 7 | 301137 | 04 |  | CIO 208-3 digital output 27 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 0 | 301139 | 04 |  | CIO 116 no. 1. Input 10 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 1 | 301139 | 04 |  | CIO 116 no. 1. Input 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 2 | 301139 | 04 |  | CIO 116 no. 1. Input 12 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 3 | 301139 | 04 |  | CIO 116 no. 1. Input 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 4 | 301139 | 04 |  | CIO 116 no. 1. Input 14 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 5 | 301139 | 04 |  | CIO 116 no. 1. Input 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 6 | 301139 | 04 |  | CIO 116 no. 1. Input 16 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 7 | 301139 | 04 |  | CIO 116 no. 1. Input 17 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 8 | 301139 | 04 |  | CIO 116 no. 1. Input 19 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 9 | 301139 | 04 |  | CIO 116 no. 1. Input 20 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 10 | 301139 | 04 |  | CIO 116 no. 1. Input 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 11 | 301139 | 04 |  | CIO 116 no. 1. Input 22 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 12 | 301139 | 04 |  | CIO 116 no. 1. Input 23 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 13 | 301139 | 04 |  | CIO 116 no. 1. Input 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 14 | 301139 | 04 |  | CIO 116 no. 1. Input 25 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1138 | 15 | 301139 | 04 |  | CIO 116 no. 1. Input 26 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 0 | 301140 | 04 |  | CIO 116 no. 2. Input 10 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 1 | 301140 | 04 |  | CIO 116 no. 2. Input 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 2 | 301140 | 04 |  | CIO 116 no. 2. Input 12 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 3 | 301140 | 04 |  | CIO 116 no. 2. Input 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 4 | 301140 | 04 |  | CIO 116 no. 2. Input 14 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 5 | 301140 | 04 |  | CIO 116 no. 2. Input 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 6 | 301140 | 04 |  | CIO 116 no. 2. Input 16 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 7 | 301140 | 04 |  | CIO 116 no. 2. Input 17 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 8 | 301140 | 04 |  | CIO 116 no. 2. Input 19 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 9 | 301140 | 04 |  | CIO 116 no. 2. Input 20 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 10 | 301140 | 04 |  | CIO 116 no. 2. Input 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 11 | 301140 | 04 |  | CIO 116 no. 2. Input 22 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 12 | 301140 | 04 |  | CIO 116 no. 2. Input 23 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 13 | 301140 | 04 |  | CIO 116 no. 2. Input 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 14 | 301140 | 04 |  | CIO 116 no. 2. Input 25 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1139 | 15 | 301140 | 04 |  | CIO 116 no. 2. Input 26 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 0 | 301141 | 04 |  | CIO 116 no. 3. Input 10 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 1 | 301141 | 04 |  | CIO 116 no. 3. Input 11 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 2 | 301141 | 04 |  | CIO 116 no. 3. Input 12 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 3 | 301141 | 04 |  | CIO 116 no. 3. Input 13 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 4 | 301141 | 04 |  | CIO 116 no. 3. Input 14 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 5 | 301141 | 04 |  | CIO 116 no. 3. Input 15 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 6 | 301141 | 04 |  | CIO 116 no. 3. Input 16 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 7 | 301141 | 04 |  | CIO 116 no. 3. Input 17 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 8 | 301141 | 04 |  | CIO 116 no. 3. Input 19 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 9 | 301141 | 04 |  | CIO 116 no. 3. Input 20 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 10 | 301141 | 04 |  | CIO 116 no. 3. Input 21 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 11 | 301141 | 04 |  | CIO 116 no. 3. Input 22 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 12 | 301141 | 04 |  | CIO 116 no. 3. Input 23 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 13 | 301141 | 04 |  | CIO 116 no. 3. Input 24 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 14 | 301141 | 04 |  | CIO 116 no. 3. Input 25 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1140 | 15 | 301141 | 04 |  | CIO 116 no. 3. Input 26 | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 0 | 301142 | 04 |  | CIO 116 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 1 | 301142 | 04 |  | CIO 116 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 2 | 301142 | 04 |  | CIO 116 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 3 | 301142 | 04 |  | CIO 208 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 4 | 301142 | 04 |  | CIO 208 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 5 | 301142 | 04 |  | CIO 208 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 6 | 301142 | 04 |  | CIO 308 no. 1 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 7 | 301142 | 04 |  | CIO 308 no. 2 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital output state | 1141 | 8 | 301142 | 04 |  | CIO 308 no. 3 conf. status out | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 0 | 301143 | 04 |  | Digital input 39 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 1 | 301143 | 04 |  | Digital input 40 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 2 | 301143 | 04 |  | Digital input 41 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 3 | 301143 | 04 |  | Digital input 42 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 4 | 301143 | 04 |  | Digital input 43 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 5 | 301143 | 04 |  | Digital input 44 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 6 | 301143 | 04 |  | Digital input 45 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 7 | 301143 | 04 |  | Digital input 46 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 9 | 301143 | 04 |  | Emergency stop input 4 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 10 | 301143 | 04 |  | Dplus input 7 | BOOL | [5 empty] | X | X | X
Digital input state | 1142 | 11 | 301143 | 04 |  | Digital input 47 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 12 | 301143 | 04 |  | Digital input 48 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 13 | 301143 | 04 |  | Digital input 49 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1142 | 14 | 301143 | 04 |  | Digital input 50 | BOOL |  |  |  | X | X | X | X | X | X
Digital input state | 1145 | 15 | 301146 | 04 |  | CIO 308 no. 2. Input 29 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 0 | 301151 | 04 |  | M-Logic Output evaluation Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 1 | 301151 | 04 |  | M-Logic Output evaluation Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 2 | 301151 | 04 |  | M-Logic Output evaluation Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 3 | 301151 | 04 |  | M-Logic Output evaluation Line 4 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 4 | 301151 | 04 |  | M-Logic Output evaluation Line 5 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 5 | 301151 | 04 |  | M-Logic Output evaluation Line 6 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 6 | 301151 | 04 |  | M-Logic Output evaluation Line 7 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 7 | 301151 | 04 |  | M-Logic Output evaluation Line 8 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 8 | 301151 | 04 |  | M-Logic Output evaluation Line 9 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 9 | 301151 | 04 |  | M-Logic Output evaluation Line 10 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 10 | 301151 | 04 |  | M-Logic Output evaluation Line 11 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 11 | 301151 | 04 |  | M-Logic Output evaluation Line 12 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 12 | 301151 | 04 |  | M-Logic Output evaluation Line 13 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 13 | 301151 | 04 |  | M-Logic Output evaluation Line 14 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 14 | 301151 | 04 |  | M-Logic Output evaluation Line 15 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1150 | 15 | 301151 | 04 |  | M-Logic Output evaluation Line 16 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 0 | 301152 | 04 |  | M-Logic Output evaluation Line 17 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 1 | 301152 | 04 |  | M-Logic Output evaluation Line 18 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 2 | 301152 | 04 |  | M-Logic Output evaluation Line 19 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 3 | 301152 | 04 |  | M-Logic Output evaluation Line 20 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 4 | 301152 | 04 |  | M-Logic Output evaluation Line 21 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 5 | 301152 | 04 |  | M-Logic Output evaluation Line 22 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 6 | 301152 | 04 |  | M-Logic Output evaluation Line 23 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 7 | 301152 | 04 |  | M-Logic Output evaluation Line 24 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 8 | 301152 | 04 |  | M-Logic Output evaluation Line 25 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 9 | 301152 | 04 |  | M-Logic Output evaluation Line 26 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 10 | 301152 | 04 |  | M-Logic Output evaluation Line 27 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 11 | 301152 | 04 |  | M-Logic Output evaluation Line 28 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 12 | 301152 | 04 |  | M-Logic Output evaluation Line 29 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 13 | 301152 | 04 |  | M-Logic Output evaluation Line 30 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 14 | 301152 | 04 |  | M-Logic Output evaluation Line 31 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1151 | 15 | 301152 | 04 |  | M-Logic Output evaluation Line 32 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 0 | 301153 | 04 |  | M-Logic Output evaluation Line 33 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 1 | 301153 | 04 |  | M-Logic Output evaluation Line 34 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 2 | 301153 | 04 |  | M-Logic Output evaluation Line 35 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 3 | 301153 | 04 |  | M-Logic Output evaluation Line 36 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 4 | 301153 | 04 |  | M-Logic Output evaluation Line 37 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 5 | 301153 | 04 |  | M-Logic Output evaluation Line 38 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 6 | 301153 | 04 |  | M-Logic Output evaluation Line 39 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 7 | 301153 | 04 |  | M-Logic Output evaluation Line 40 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 8 | 301153 | 04 |  | M-Logic Output evaluation Line 41 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 9 | 301153 | 04 |  | M-Logic Output evaluation Line 42 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 10 | 301153 | 04 |  | M-Logic Output evaluation Line 43 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 11 | 301153 | 04 |  | M-Logic Output evaluation Line 44 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 12 | 301153 | 04 |  | M-Logic Output evaluation Line 45 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 13 | 301153 | 04 |  | M-Logic Output evaluation Line 46 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 14 | 301153 | 04 |  | M-Logic Output evaluation Line 47 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1152 | 15 | 301153 | 04 |  | M-Logic Output evaluation Line 48 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 0 | 301154 | 04 |  | M-Logic Output evaluation Line 49 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 1 | 301154 | 04 |  | M-Logic Output evaluation Line 50 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 2 | 301154 | 04 |  | M-Logic Output evaluation Line 51 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 3 | 301154 | 04 |  | M-Logic Output evaluation Line 52 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 4 | 301154 | 04 |  | M-Logic Output evaluation Line 53 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 5 | 301154 | 04 |  | M-Logic Output evaluation Line 54 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 6 | 301154 | 04 |  | M-Logic Output evaluation Line 55 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 7 | 301154 | 04 |  | M-Logic Output evaluation Line 56 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 8 | 301154 | 04 |  | M-Logic Output evaluation Line 57 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 9 | 301154 | 04 |  | M-Logic Output evaluation Line 58 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 10 | 301154 | 04 |  | M-Logic Output evaluation Line 59 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 11 | 301154 | 04 |  | M-Logic Output evaluation Line 60 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 12 | 301154 | 04 |  | M-Logic Output evaluation Line 61 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 13 | 301154 | 04 |  | M-Logic Output evaluation Line 62 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 14 | 301154 | 04 |  | M-Logic Output evaluation Line 63 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1153 | 15 | 301154 | 04 |  | M-Logic Output evaluation Line 64 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 0 | 301155 | 04 |  | M-Logic Output evaluation Line 65 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 1 | 301155 | 04 |  | M-Logic Output evaluation Line 66 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 2 | 301155 | 04 |  | M-Logic Output evaluation Line 67 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 3 | 301155 | 04 |  | M-Logic Output evaluation Line 68 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 4 | 301155 | 04 |  | M-Logic Output evaluation Line 69 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 5 | 301155 | 04 |  | M-Logic Output evaluation Line 70 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 6 | 301155 | 04 |  | M-Logic Output evaluation Line 71 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 7 | 301155 | 04 |  | M-Logic Output evaluation Line 72 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 8 | 301155 | 04 |  | M-Logic Output evaluation Line 73 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 9 | 301155 | 04 |  | M-Logic Output evaluation Line 74 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 10 | 301155 | 04 |  | M-Logic Output evaluation Line 75 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 11 | 301155 | 04 |  | M-Logic Output evaluation Line 76 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 12 | 301155 | 04 |  | M-Logic Output evaluation Line 77 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 13 | 301155 | 04 |  | M-Logic Output evaluation Line 78 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 14 | 301155 | 04 |  | M-Logic Output evaluation Line 79 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1154 | 15 | 301155 | 04 |  | M-Logic Output evaluation Line 80 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 8 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 9 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 10 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 1 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 11 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 12 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 13 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 2 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 14 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1155 | 15 | 301156 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 0 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 3 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 1 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 2 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 3 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 4 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 4 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 5 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 6 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 5 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 7 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 8 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 9 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 6 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 10 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 11 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 12 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 7 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 13 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 14 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1156 | 15 | 301157 | 04 |  | M-Logic Output evaluation AOP2_1 LED 8 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 0 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 1 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 2 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 9 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 3 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 4 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 5 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 10 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 6 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 7 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 8 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 11 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 9 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 10 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 11 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 12 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 12 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 13 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 14 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 13 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1157 | 15 | 301158 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 0 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 1 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 14 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 2 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 3 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 4 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 15 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 5 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 6 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 7 | 301159 | 04 |  | M-Logic Output evaluation AOP2_1 LED 16 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 8 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 9 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 10 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 1 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 11 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 12 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 13 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 2 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 14 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1158 | 15 | 301159 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 0 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 3 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 1 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 2 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 3 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 4 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 4 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 5 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 6 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 5 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 7 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 8 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 9 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 6 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 10 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 11 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 12 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 7 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 13 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 14 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1159 | 15 | 301160 | 04 |  | M-Logic Output evaluation AOP2_2 LED 8 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 0 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 1 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 2 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 9 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 3 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 4 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 5 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 10 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 6 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 7 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 8 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 11 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 9 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 10 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 11 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 12 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 12 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 13 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 14 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 13 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1160 | 15 | 301161 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 0 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 1 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 14 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 2 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 3 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 4 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 15 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 5 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 6 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1161 | 7 | 301162 | 04 |  | M-Logic Output evaluation AOP2_2 LED 16 Line 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 0 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 1 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 2 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 3 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 4 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 4 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 5 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 5 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 6 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 6 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 7 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 7 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_1 Button 8 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 8 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 9 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 10 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 11 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 4 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 12 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 5 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 13 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 6 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 14 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 7 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1171 | 15 | 301172 | 04 |  | M-Logic Output Evaluation AOP2_2 Button 8 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 8 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 9 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 10 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_1 Buzzer 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 11 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 12 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1173 | 13 | 301174 | 04 |  | M-Logic Output Evaluation AOP2_2 Buzzer 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 7 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 8 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 9 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_1 Relay 3 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 10 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 1 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 11 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 2 | BOOL |  |  |  | X | X | X | X | X | X
M-Logic state | 1174 | 12 | 301175 | 04 |  | M-Logic Output Evaluation AOP2_2 Relay 3 | BOOL |  |  |  | X | X | X | X | X | X
DAVR measurement | 1214 |  | 301215 | 04 |  | DVC 550 Pt100 #1 | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 1215 |  | 301216 | 04 |  | DVC 550 Pt100 #2 | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 1216 |  | 301217 | 04 |  | DVC 550 Pt100 #3 | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 1217 |  | 301218 | 04 |  | DVC 550 Pt100 #4 | INT16s | AB | 0 |  |  |  | X | X
DAVR measurement | 1218 |  | 301219 | 04 |  | DVC 550 Pt100 #5 | INT16s | AB | 0 |  |  |  | X | X
EIC measurement | 1220 | 0 | 301221 | 04 |  | FPT Stage V: Fuel in Oil Detection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 1 | 301221 | 04 |  | FPT Stage V: Water in Fuel Detection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 2 | 301221 | 04 |  | FPT Stage V: Engine Protection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 3 | 301221 | 04 |  | FPT Stage V: Turbo Charger Protection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 4 | 301221 | 04 |  | FPT Stage V: Scr Injector Overheat Protection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 5 | 301221 | 04 |  | FPT Stage V: Urea Thawing Mode Active | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 6 | 301221 | 04 |  | FPT Stage V: Engine Over Speed Warning | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 7 | 301221 | 04 |  | FPT Stage V: Exhaust Over Heat Condition | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 8 | 301221 | 04 |  | FPT Stage V: Clogged DPF | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 9 | 301221 | 04 |  | FPT Stage V: Smoke Limitation | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 10 | 301221 | 04 |  | FPT Stage V: Engine Oil Over Temperature | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 11 | 301221 | 04 |  | FPT Stage V: Nh3 Slip Detection | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 12 | 301221 | 04 |  | FPT Stage V: Bad Urea Quality | BOOL | [5 empty] | X | X | X
EIC measurement | 1220 | 13 | 301221 | 04 |  | FPT Stage V: Low Catalyst Efficiency | BOOL | [5 empty] | X | X | X
EIC measurement | 1221 |  | 301222 | 04 |  | FPT Stage V: DEF Technical Failure | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1222 |  | 301223 | 04 |  | FPT Stage V: DEF Quality | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1223 |  | 301224 | 04 |  | FPT Stage V: DEF Level | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1224 |  | 301225 | 04 |  | FPT Stage V: Fuel Filter Heater Status | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1225 |  | 301226 | 04 |  | FPT Stage V: Low Idle Increase Desired | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1226 |  | 301227 | 04 |  | Scania: DPF regeneration countdown timer | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1227 |  | 301228 | 04 |  | Scania: Urea level inducement state | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1228 |  | 301229 | 04 |  | Scania: Emission-OBD inducement state | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1229 |  | 301230 | 04 |  | Scania: Emission-OBD inducement failure reason | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1230 |  | 301231 | 04 |  | John Deere STAGE V: Engine Diesel Particulate Filter Regeneration State | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1231 |  | 301232 | 04 |  | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1232 |  | 301233 | 04 |  | Aftertreatment Diesel Particulate Filter Status | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1233 |  | 301234 | 04 |  | Aftertreatment 1 Diesel Exhaust Fluid Concentration | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1234 |  | 301235 | 04 |  | Engine Requested Fuel Valve 1 Position | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1235 |  | 301236 | 04 |  | Engine Oil Priming State (SPN 3551) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1236 |  | 301237 | 04 |  | Fuel Pump Primer Status (SPN 4083) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1237 |  | 301238 | 04 |  | Sensor supply voltage 1 (SPN 3509) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1238 |  | 301239 | 04 |  | Sensor supply voltage 2 (SPN 3510) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1239 |  | 301240 | 04 |  | Accelerator Pedal Position 2 (SPN 29) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1240 |  | 301241 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Temporary System Lockout (SPN 3714) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1241 |  | 301242 | 04 |  | Diesel Particulate Filter Active Regeneration Inhibited Due to Permanent System Lockout (SPN 3715) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1242 |  | 301243 | 04 |  | Aftertreatment Ambient Air Temperature (SPN 7441) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1243 |  | 301244 | 04 |  | Aftertreatment Thermal Management Status (SPN 7332) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1244 |  | 301245 | 04 |  | Aftertreatment Engine Speed Increase request (SPN 7502) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1245 |  | 301246 | 04 |  | Aftertreatment Engine Load Request (SPN 7503) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1246 |  | 301247 | 04 |  | Feedback Engine Fueling State (SPN 5794) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1247 |  | 301248 | 04 |  | Engine Fueling Inhibit Allowed (SPN 5795) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1248 |  | 301249 | 04 |  | Engine controlled shutdown request (SPN 3606) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1249 |  | 301250 | 04 |  | Engine oil pre-heated state (SPN 3552) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1250 |  | 301251 | 04 |  | Engine ventilation state (SPN 3554) | INT16s | AB | 0 |  |  |  | X | X | X
EIC measurement | 1251 |  | 301252 | 04 |  | Rail pressure (Jichai) | INT16s | AB | 0 |  |  |  | X | X | X
M-Logic state | 1252 |  | 301253 | 04 |  | Oneshot output 1-16 | INT16s | AB | 0 |  | X | X | X | X | X | X
AC measurement | 1267 |  | 301268 | 04 |  | Remaining cyclic time (ATS) | INT16s | AB | 0 | Min | [5 empty] | X
AC measurement | 1268 |  | 301269 | 04 |  | Source to run in cyclic mode (ATS) | INT16s | AB | 0 | [6 empty] | X
Alarm | 1269 | 0 | 301270 | 04 |  | Elevator pre-delay timer is running. | BOOL | [8 empty] | X
Alarm | 1269 | 1 | 301270 | 04 |  | Elevator post-delay timer is running. | BOOL | [8 empty] | X
Alarm | 1269 | 2 | 301270 | 04 |  | Load energized from source 1 | BOOL | [8 empty] | X
Alarm | 1269 | 3 | 301270 | 04 |  | Load energized from source 1 | BOOL | [8 empty] | X
Alarm | 1269 | 4 | 301270 | 04 |  | Load bus 1 (between CB1 and BTB) energized | BOOL | [8 empty] | X
Alarm | 1269 | 5 | 301270 | 04 |  | Load bus 2 (between CB2 and BTB) energized | BOOL | [8 empty] | X
Alarm | 1269 | 6 | 301270 | 04 |  | Gen-gen wait for start mode enabled | BOOL | [8 empty] | X
Alarm | 1269 | 7 | 301270 | 04 |  | Gen-gen wait for start mode enabled and started | BOOL | [8 empty] | X
AC measurement | 1320 |  | 301321 | 04 |  | Hybrid only: PV power reference | INT16s | AB | 0 | kW |  |  |  | X
AC measurement | 1321 |  | 301322 | 04 |  | Hybrid only: PV reactive power reference | INT16s | AB | 0 | kW |  |  |  | X
AC measurement | 1322 |  | 301323 | 04 |  | Hybrid only: PV power actual | INT16s | AB | 0 | kW |  |  |  | X
AC measurement | 1323 |  | 301324 | 04 |  | Hybrid only: PV reactive power actual | INT16s | AB | 0 | kW |  |  |  | X
AC measurement | 1324 |  | 301325 | 04 |  | Hybrid only: PV nominal power actual | INT16s | AB | 0 | kW |  |  |  | X
Plant logic state | 1325 |  | 301326 | 04 |  | Hybrid only: PV breaker status | INT16s | AB | 0 |  |  |  |  | X
Alarm | 1326 | 0 | 301327 | 04 |  | Hybrid only: PV running status | BOOL | [6 empty] | X
Plant logic state | 1327 |  | 301328 | 04 |  | Hybrid only: Number of PV related alarms present. Plus 1 for any amount of active alarms with PV shutdown fail class. | INT16s | AB | 0 |  |  |  |  | X
Counter | 1330 |  | 301331 | 04 |  | Hybrid only: PV Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1332 |  | 301333 | 04 |  | Hybrid only: PV Export, active energy counter, year | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1334 |  | 301335 | 04 |  | Hybrid only: PV Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1336 |  | 301337 | 04 |  | Hybrid only: PV Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1338 |  | 301339 | 04 |  | Hybrid only: PV Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1340 |  | 301341 | 04 |  | Hybrid only: PV Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  |  | X
Counter | 1342 |  | 301343 | 04 |  | Hybrid only: PV Export, reactive energy counter, year | INT32s | ABCD | 0 | kvarh |  |  |  | X
Counter | 1344 |  | 301345 | 04 |  | Hybrid only: PV Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  |  |  | X
Counter | 1346 |  | 301347 | 04 |  | Hybrid only: PV Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  |  |  | X
Counter | 1348 |  | 301349 | 04 |  | Hybrid only: PV Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  |  |  | X
Counter | 1350 |  | 301351 | 04 |  | Hybrid only: PV curtailed energy counter, total | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1352 |  | 301353 | 04 |  | Hybrid only: PV curtailed energy counter, year | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1354 |  | 301355 | 04 |  | Hybrid only: PV curtailed energy counter, month | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1356 |  | 301357 | 04 |  | Hybrid only: PV curtailed energy counter, week | INT32s | ABCD | 0 | kWh |  |  |  | X
Counter | 1358 |  | 301359 | 04 |  | Hybrid only: PV curtailed energy counter, day | INT32s | ABCD | 0 | kWh |  |  |  | X
Alarm | 1360 | 0 | 301361 | 04 | 3660 | M-Logic alarm 10 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1360 | 1 | 301361 | 04 | 3670 | M-Logic alarm 11 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1360 | 2 | 301361 | 04 | 3680 | M-Logic alarm 12 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1360 | 3 | 301361 | 04 | 3690 | M-Logic alarm 13 | BOOL |  |  |  | X | X | X | X | X | X
Alarm | 1360 | 4 | 301361 | 04 | 3700 | M-Logic alarm 14 | BOOL |  |  |  | X | X | X | X | X | X
EIC alarm | 1370 |  | 301371 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1371 |  | 301372 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1372 |  | 301373 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1373 |  | 301374 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1374 |  | 301375 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1375 |  | 301376 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1376 |  | 301377 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1377 |  | 301378 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1378 |  | 301379 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1379 |  | 301380 | 04 |  | Active diagnostic codes (DM1/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1380 |  | 301381 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1381 |  | 301382 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1382 |  | 301383 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1383 |  | 301384 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1384 |  | 301385 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1385 |  | 301386 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1386 |  | 301387 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1387 |  | 301388 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1388 |  | 301389 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1389 |  | 301390 | 04 |  | Active diagnostic codes (DM1/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1402 |  | 301403 | 04 |  | Active fail mode identifier (DM1/FMI): #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1403 |  | 301404 | 04 |  | Active fail mode identifier (DM1/FMI): #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1404 |  | 301405 | 04 |  | Active fail mode identifier (DM1/FMI): #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1405 |  | 301406 | 04 |  | Active fail mode identifier (DM1/FMI): #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1406 |  | 301407 | 04 |  | Active fail mode identifier (DM1/FMI): #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1407 |  | 301408 | 04 |  | Active fail mode identifier (DM1/FMI): #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1408 |  | 301409 | 04 |  | Active fail mode identifier (DM1/FMI): #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1409 |  | 301410 | 04 |  | Active fail mode identifier (DM1/FMI): #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1410 |  | 301411 | 04 |  | Active fail mode identifier (DM1/FMI): #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1411 |  | 301412 | 04 |  | Active fail mode identifier (DM1/FMI): #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1418 |  | 301419 | 04 |  | Active occurrence counter (DM1/OC): #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1419 |  | 301420 | 04 |  | Active occurrence counter (DM1/OC): #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1420 |  | 301421 | 04 |  | Active occurrence counter (DM1/OC): #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1421 |  | 301422 | 04 |  | Active occurrence counter (DM1/OC): #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1422 |  | 301423 | 04 |  | Active occurrence counter (DM1/OC): #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1423 |  | 301424 | 04 |  | Active occurrence counter (DM1/OC): #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1424 |  | 301425 | 04 |  | Active occurrence counter (DM1/OC): #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1425 |  | 301426 | 04 |  | Active occurrence counter (DM1/OC): #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1426 |  | 301427 | 04 |  | Active occurrence counter (DM1/OC): #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1427 |  | 301428 | 04 |  | Active occurrence counter (DM1/OC): #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1434 |  | 301435 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1435 |  | 301436 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1436 |  | 301437 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1437 |  | 301438 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1438 |  | 301439 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1439 |  | 301440 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1440 |  | 301441 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1441 |  | 301442 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1442 |  | 301443 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1443 |  | 301444 | 04 |  | Active diagnostic codes (DM2/SPN): LOW-WORD #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1444 |  | 301445 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1445 |  | 301446 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1446 |  | 301447 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1447 |  | 301448 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1448 |  | 301449 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1449 |  | 301450 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1450 |  | 301451 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1451 |  | 301452 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1452 |  | 301453 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1453 |  | 301454 | 04 |  | Active diagnostic codes (DM2/SPN): HIGH-WORD #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1466 |  | 301467 | 04 |  | Active fail mode identifier (DM2/FMI): #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1467 |  | 301468 | 04 |  | Active fail mode identifier (DM2/FMI): #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1468 |  | 301469 | 04 |  | Active fail mode identifier (DM2/FMI): #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1469 |  | 301470 | 04 |  | Active fail mode identifier (DM2/FMI): #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1470 |  | 301471 | 04 |  | Active fail mode identifier (DM2/FMI): #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1471 |  | 301472 | 04 |  | Active fail mode identifier (DM2/FMI): #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1472 |  | 301473 | 04 |  | Active fail mode identifier (DM2/FMI): #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1473 |  | 301474 | 04 |  | Active fail mode identifier (DM2/FMI): #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1474 |  | 301475 | 04 |  | Active fail mode identifier (DM2/FMI): #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1475 |  | 301476 | 04 |  | Active fail mode identifier (DM2/FMI): #10 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1482 |  | 301483 | 04 |  | Active occurrence counter (DM2/OC): #1 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1483 |  | 301484 | 04 |  | Active occurrence counter (DM2/OC): #2 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1484 |  | 301485 | 04 |  | Active occurrence counter (DM2/OC): #3 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1485 |  | 301486 | 04 |  | Active occurrence counter (DM2/OC): #4 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1486 |  | 301487 | 04 |  | Active occurrence counter (DM2/OC): #5 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1487 |  | 301488 | 04 |  | Active occurrence counter (DM2/OC): #6 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1488 |  | 301489 | 04 |  | Active occurrence counter (DM2/OC): #7 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1489 |  | 301490 | 04 |  | Active occurrence counter (DM2/OC): #8 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1490 |  | 301491 | 04 |  | Active occurrence counter (DM2/OC): #9 | INT16s | AB | 0 |  |  |  | X | X | X
EIC alarm | 1491 |  | 301492 | 04 |  | Active occurrence counter (DM2/OC): #10 | INT16s | AB | 0 |  |  |  | X | X | X
PM AC measurement | 1500 |  | 301501 | 04 |  | Total power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1501 |  | 301502 | 04 |  | Available power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1502 |  | 301503 | 04 |  | Total nominal power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1503 |  | 301504 | 04 |  | Total genset power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1504 |  | 301505 | 04 |  | Total reactive power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1505 |  | 301506 | 04 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1506 |  | 301507 | 04 |  | Plant type | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1507 |  | 301508 | 04 |  | Load-dependent stop, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1508 |  | 301509 | 04 |  | Load-dependent start, active set-point | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1510 |  | 301511 | 04 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1511 |  | 301512 | 04 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1512 |  | 301513 | 04 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1513 |  | 301514 | 04 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1514 |  | 301515 | 04 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1515 |  | 301516 | 04 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1516 |  | 301517 | 04 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1517 |  | 301518 | 04 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1518 |  | 301519 | 04 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1519 |  | 301520 | 04 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1520 |  | 301521 | 04 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1521 |  | 301522 | 04 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1522 |  | 301523 | 04 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1523 |  | 301524 | 04 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1524 |  | 301525 | 04 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1525 |  | 301526 | 04 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1526 |  | 301527 | 04 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1527 |  | 301528 | 04 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1528 |  | 301529 | 04 |  | Active Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1529 |  | 301530 | 04 |  | Active Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1530 |  | 301531 | 04 |  | Active Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1531 |  | 301532 | 04 |  | Active Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1532 |  | 301533 | 04 |  | Active Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1533 |  | 301534 | 04 |  | Active Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1534 |  | 301535 | 04 |  | Active Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1535 |  | 301536 | 04 |  | Active Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1536 |  | 301537 | 04 |  | Active Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1537 |  | 301538 | 04 |  | Active Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1538 |  | 301539 | 04 |  | Active Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1539 |  | 301540 | 04 |  | Active Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1540 |  | 301541 | 04 |  | Active Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1541 |  | 301542 | 04 |  | Active Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1542 |  | 301543 | 04 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1543 |  | 301544 | 04 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1544 |  | 301545 | 04 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1545 |  | 301546 | 04 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1546 |  | 301547 | 04 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1547 |  | 301548 | 04 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1548 |  | 301549 | 04 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1549 |  | 301550 | 04 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1550 |  | 301551 | 04 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1551 |  | 301552 | 04 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1552 |  | 301553 | 04 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1553 |  | 301554 | 04 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1554 |  | 301555 | 04 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1555 |  | 301556 | 04 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1556 |  | 301557 | 04 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1557 |  | 301558 | 04 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1558 |  | 301559 | 04 |  | Priority of genset | INT16s | AB | 0 |  |  |  | X
PM AC measurement | 1560 |  | 301561 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1561 |  | 301562 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1562 |  | 301563 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1563 |  | 301564 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1565 |  | 301566 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1566 |  | 301567 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1567 |  | 301568 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1568 |  | 301569 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1569 |  | 301570 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1570 |  | 301571 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1571 |  | 301572 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1572 |  | 301573 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1573 |  | 301574 | 04 |  | Active Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1574 |  | 301575 | 04 |  | Active Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1575 |  | 301576 | 04 |  | Active Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1576 |  | 301577 | 04 |  | Active Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1577 |  | 301578 | 04 |  | Active Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1578 |  | 301579 | 04 |  | Active Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1579 |  | 301580 | 04 |  | Active Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1580 |  | 301581 | 04 |  | Active Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1581 |  | 301582 | 04 |  | Active Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1582 |  | 301583 | 04 |  | Active Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1583 |  | 301584 | 04 |  | Active Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1584 |  | 301585 | 04 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1585 |  | 301586 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1586 |  | 301587 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1587 |  | 301588 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1588 |  | 301589 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1589 |  | 301590 | 04 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1590 |  | 301591 | 04 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1591 |  | 301592 | 04 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1592 |  | 301593 | 04 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1593 |  | 301594 | 04 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1594 |  | 301595 | 04 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1595 |  | 301596 | 04 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1596 |  | 301597 | 04 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1597 |  | 301598 | 04 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1598 |  | 301599 | 04 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1599 |  | 301600 | 04 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1600 |  | 301601 | 04 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1601 |  | 301602 | 04 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1602 |  | 301603 | 04 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1603 |  | 301604 | 04 |  | Active Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1604 |  | 301605 | 04 |  | Active Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1605 |  | 301606 | 04 |  | Active Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1606 |  | 301607 | 04 |  | Active Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1607 |  | 301608 | 04 |  | Active Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1608 |  | 301609 | 04 |  | Active Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1609 |  | 301610 | 04 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1610 |  | 301611 | 04 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1611 |  | 301612 | 04 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1612 |  | 301613 | 04 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1613 |  | 301614 | 04 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1614 |  | 301615 | 04 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1615 |  | 301616 | 04 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1616 |  | 301617 | 04 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1617 |  | 301618 | 04 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1618 |  | 301619 | 04 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1619 |  | 301620 | 04 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1620 |  | 301621 | 04 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1621 |  | 301622 | 04 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1622 |  | 301623 | 04 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1623 |  | 301624 | 04 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1624 |  | 301625 | 04 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1625 |  | 301626 | 04 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1626 |  | 301627 | 04 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1627 |  | 301628 | 04 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1628 |  | 301629 | 04 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1629 |  | 301630 | 04 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1630 |  | 301631 | 04 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1631 |  | 301632 | 04 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1632 |  | 301633 | 04 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1633 |  | 301634 | 04 |  | Bus power mains 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1634 |  | 301635 | 04 |  | Bus power mains 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1635 |  | 301636 | 04 |  | Bus power mains 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1636 |  | 301637 | 04 |  | Bus power mains 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1637 |  | 301638 | 04 |  | Bus power mains 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1638 |  | 301639 | 04 |  | Bus power mains 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1639 |  | 301640 | 04 |  | Bus power mains 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1640 |  | 301641 | 04 |  | Bus power mains 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1641 |  | 301642 | 04 |  | Bus power mains 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1642 |  | 301643 | 04 |  | Bus power mains 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1643 |  | 301644 | 04 |  | Bus power mains 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1644 |  | 301645 | 04 |  | Bus power mains 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1645 |  | 301646 | 04 |  | Bus power mains 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1646 |  | 301647 | 04 |  | Bus power mains 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1647 |  | 301648 | 04 |  | Bus power mains 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1648 |  | 301649 | 04 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X | X
PM Plant logic state | 1649 | 0 | 301650 | 04 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 1 | 301650 | 04 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 2 | 301650 | 04 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 3 | 301650 | 04 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 4 | 301650 | 04 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 5 | 301650 | 04 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 6 | 301650 | 04 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 7 | 301650 | 04 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 8 | 301650 | 04 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 9 | 301650 | 04 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 10 | 301650 | 04 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 11 | 301650 | 04 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 12 | 301650 | 04 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 13 | 301650 | 04 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 14 | 301650 | 04 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1649 | 15 | 301650 | 04 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 0 | 301651 | 04 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 1 | 301651 | 04 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 2 | 301651 | 04 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 3 | 301651 | 04 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 4 | 301651 | 04 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 5 | 301651 | 04 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 6 | 301651 | 04 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 7 | 301651 | 04 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 8 | 301651 | 04 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 9 | 301651 | 04 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 10 | 301651 | 04 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 11 | 301651 | 04 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 12 | 301651 | 04 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 13 | 301651 | 04 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 14 | 301651 | 04 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1650 | 15 | 301651 | 04 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 0 | 301652 | 04 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 1 | 301652 | 04 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 2 | 301652 | 04 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 3 | 301652 | 04 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 4 | 301652 | 04 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 5 | 301652 | 04 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 6 | 301652 | 04 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1651 | 7 | 301652 | 04 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 0 | 301653 | 04 |  | ID 33 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 1 | 301653 | 04 |  | ID 34 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 2 | 301653 | 04 |  | ID 35 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 3 | 301653 | 04 |  | ID 36 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 4 | 301653 | 04 |  | ID 37 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 5 | 301653 | 04 |  | ID 38 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 6 | 301653 | 04 |  | ID 39 BTB controlled | BOOL |  |  |  | X | X | X
PM Plant logic state | 1652 | 7 | 301653 | 04 |  | ID 40 BTB controlled | BOOL |  |  |  | X | X | X
PM AC measurement | 1653 |  | 301654 | 04 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1654 |  | 301655 | 04 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1655 |  | 301656 | 04 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1656 |  | 301657 | 04 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1657 |  | 301658 | 04 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1658 |  | 301659 | 04 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1659 |  | 301660 | 04 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1660 |  | 301661 | 04 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1661 |  | 301662 | 04 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1662 |  | 301663 | 04 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1663 |  | 301664 | 04 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1664 |  | 301665 | 04 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1665 |  | 301666 | 04 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1666 |  | 301667 | 04 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1667 |  | 301668 | 04 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1668 |  | 301669 | 04 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1696 |  | 301697 | 04 |  | Total PV active power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1697 |  | 301698 | 04 |  | Total PV reactive power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1698 |  | 301699 | 04 |  | Total Battery active power | INT16s | AB | 0 |  | X | X | X
PM AC measurement | 1699 |  | 301700 | 04 |  | Total Battery reactive power | INT16s | AB | 0 |  | X | X | X
PM Plant logic state | 1700 | 0 | 301701 | 04 |  | TB available | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 1 | 301701 | 04 |  | Mains unit available | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 2 | 301701 | 04 |  | Any MB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 3 | 301701 | 04 |  | All MB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 4 | 301701 | 04 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 5 | 301701 | 04 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 6 | 301701 | 04 |  | Any GB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 7 | 301701 | 04 |  | All GB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 8 | 301701 | 04 |  | Any TB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 9 | 301701 | 04 |  | All TB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 10 | 301701 | 04 |  | Any BTB pos. ON | BOOL |  |  |  | X | X | X
PM Plant logic state | 1700 | 11 | 301701 | 04 |  | Any BTB pos. OFF | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 0 | 301702 | 04 |  | GB pos. ON ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 1 | 301702 | 04 |  | GB pos. ON ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 2 | 301702 | 04 |  | GB pos. ON ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 3 | 301702 | 04 |  | GB pos. ON ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 4 | 301702 | 04 |  | GB pos. ON ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 5 | 301702 | 04 |  | GB pos. ON ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 6 | 301702 | 04 |  | GB pos. ON ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 7 | 301702 | 04 |  | GB pos. ON ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 8 | 301702 | 04 |  | GB pos. ON ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 9 | 301702 | 04 |  | GB pos. ON ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 10 | 301702 | 04 |  | GB pos. ON ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 11 | 301702 | 04 |  | GB pos. ON ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 12 | 301702 | 04 |  | GB pos. ON ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 13 | 301702 | 04 |  | GB pos. ON ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 14 | 301702 | 04 |  | GB pos. ON ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1701 | 15 | 301702 | 04 |  | GB pos. ON ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 0 | 301703 | 04 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 1 | 301703 | 04 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 2 | 301703 | 04 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 3 | 301703 | 04 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 4 | 301703 | 04 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 5 | 301703 | 04 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 6 | 301703 | 04 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 7 | 301703 | 04 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 8 | 301703 | 04 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 9 | 301703 | 04 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 10 | 301703 | 04 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 11 | 301703 | 04 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 12 | 301703 | 04 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 13 | 301703 | 04 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 14 | 301703 | 04 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1702 | 15 | 301703 | 04 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 0 | 301704 | 04 |  | GEN Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 1 | 301704 | 04 |  | GEN Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 2 | 301704 | 04 |  | GEN Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 3 | 301704 | 04 |  | GEN Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 4 | 301704 | 04 |  | GEN Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 5 | 301704 | 04 |  | GEN Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 6 | 301704 | 04 |  | GEN Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 7 | 301704 | 04 |  | GEN Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 8 | 301704 | 04 |  | GEN Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 9 | 301704 | 04 |  | GEN Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 10 | 301704 | 04 |  | GEN Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 11 | 301704 | 04 |  | GEN Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 12 | 301704 | 04 |  | GEN Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 13 | 301704 | 04 |  | GEN Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 14 | 301704 | 04 |  | GEN Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1703 | 15 | 301704 | 04 |  | GEN Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 0 | 301705 | 04 |  | Mains OK, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 1 | 301705 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 2 | 301705 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 3 | 301705 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1704 | 4 | 301705 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 0 | 301706 | 04 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 1 | 301706 | 04 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 2 | 301706 | 04 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 3 | 301706 | 04 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 4 | 301706 | 04 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 5 | 301706 | 04 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 6 | 301706 | 04 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 7 | 301706 | 04 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 8 | 301706 | 04 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 9 | 301706 | 04 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 10 | 301706 | 04 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 11 | 301706 | 04 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 12 | 301706 | 04 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 13 | 301706 | 04 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 14 | 301706 | 04 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1705 | 15 | 301706 | 04 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 0 | 301707 | 04 |  | Mains not in MANUAL, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 1 | 301707 | 04 |  | Mains not in MANUAL, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 2 | 301707 | 04 |  | Mains not in MANUAL, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 3 | 301707 | 04 |  | Mains not in MANUAL, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1706 | 4 | 301707 | 04 |  | Mains not in MANUAL, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 0 | 301708 | 04 |  | Any alarms, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 1 | 301708 | 04 |  | Any alarms, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 2 | 301708 | 04 |  | Any alarms, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 3 | 301708 | 04 |  | Any alarms, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 4 | 301708 | 04 |  | Any alarms, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 5 | 301708 | 04 |  | Any alarms, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 6 | 301708 | 04 |  | Any alarms, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 7 | 301708 | 04 |  | Any alarms, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 8 | 301708 | 04 |  | Any alarms, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 9 | 301708 | 04 |  | Any alarms, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 10 | 301708 | 04 |  | Any alarms, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 11 | 301708 | 04 |  | Any alarms, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 12 | 301708 | 04 |  | Any alarms, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 13 | 301708 | 04 |  | Any alarms, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 14 | 301708 | 04 |  | Any alarms, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1707 | 15 | 301708 | 04 |  | Any alarms, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 0 | 301709 | 04 |  | Any alarms, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 1 | 301709 | 04 |  | Any alarms, mains 1A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 2 | 301709 | 04 |  | Any alarms, mains 1B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 3 | 301709 | 04 |  | Any alarms, mains 2A | BOOL |  |  |  | X | X | X
PM Plant logic state | 1708 | 4 | 301709 | 04 |  | Any alarms, mains 2B | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 0 | 301710 | 04 |  | Engine running, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 1 | 301710 | 04 |  | Engine running, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 2 | 301710 | 04 |  | Engine running, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 3 | 301710 | 04 |  | Engine running, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 4 | 301710 | 04 |  | Engine running, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 5 | 301710 | 04 |  | Engine running, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 6 | 301710 | 04 |  | Engine running, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 7 | 301710 | 04 |  | Engine running, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 8 | 301710 | 04 |  | Engine running, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 9 | 301710 | 04 |  | Engine running, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 10 | 301710 | 04 |  | Engine running, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 11 | 301710 | 04 |  | Engine running, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 12 | 301710 | 04 |  | Engine running, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 13 | 301710 | 04 |  | Engine running, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 14 | 301710 | 04 |  | Engine running, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1709 | 15 | 301710 | 04 |  | Engine running, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 0 | 301711 | 04 |  | MB pos. ON, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 1 | 301711 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 2 | 301711 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 3 | 301711 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 4 | 301711 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 5 | 301711 | 04 |  | MB pos. OFF, single mains | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 6 | 301711 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 7 | 301711 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 8 | 301711 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1710 | 9 | 301711 | 04 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 0 | 301712 | 04 |  | GB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 1 | 301712 | 04 |  | GB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 2 | 301712 | 04 |  | GB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 3 | 301712 | 04 |  | GB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 4 | 301712 | 04 |  | GB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 5 | 301712 | 04 |  | GB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 6 | 301712 | 04 |  | GB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 7 | 301712 | 04 |  | GB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 8 | 301712 | 04 |  | GB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 9 | 301712 | 04 |  | GB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 10 | 301712 | 04 |  | GB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 11 | 301712 | 04 |  | GB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 12 | 301712 | 04 |  | GB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 13 | 301712 | 04 |  | GB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 14 | 301712 | 04 |  | GB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1711 | 15 | 301712 | 04 |  | GB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 0 | 301713 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 1 | 301713 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 2 | 301713 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 3 | 301713 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 4 | 301713 | 04 |  | Mains OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 5 | 301713 | 04 |  | Mains OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 6 | 301713 | 04 |  | Mains OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 7 | 301713 | 04 |  | Mains OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 8 | 301713 | 04 |  | Mains OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 9 | 301713 | 04 |  | Mains OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 10 | 301713 | 04 |  | Mains OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 11 | 301713 | 04 |  | Mains OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 12 | 301713 | 04 |  | Mains OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 13 | 301713 | 04 |  | Mains OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 14 | 301713 | 04 |  | Mains OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1712 | 15 | 301713 | 04 |  | Mains OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 0 | 301714 | 04 |  | Mains not in MANUAL 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 1 | 301714 | 04 |  | Mains not in MANUAL 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 2 | 301714 | 04 |  | Mains not in MANUAL 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 3 | 301714 | 04 |  | Mains not in MANUAL 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 4 | 301714 | 04 |  | Mains not in MANUAL 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 5 | 301714 | 04 |  | Mains not in MANUAL 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 6 | 301714 | 04 |  | Mains not in MANUAL 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 7 | 301714 | 04 |  | Mains not in MANUAL 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 8 | 301714 | 04 |  | Mains not in MANUAL 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 9 | 301714 | 04 |  | Mains not in MANUAL 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 10 | 301714 | 04 |  | Mains not in MANUAL 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 11 | 301714 | 04 |  | Mains not in MANUAL 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 12 | 301714 | 04 |  | Mains not in MANUAL 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 13 | 301714 | 04 |  | Mains not in MANUAL 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 14 | 301714 | 04 |  | Mains not in MANUAL 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1713 | 15 | 301714 | 04 |  | Mains not in MANUAL 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 0 | 301715 | 04 |  | Any alarms, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 1 | 301715 | 04 |  | Any alarms, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 2 | 301715 | 04 |  | Any alarms, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 3 | 301715 | 04 |  | Any alarms, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 4 | 301715 | 04 |  | Any alarms, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 5 | 301715 | 04 |  | Any alarms, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 6 | 301715 | 04 |  | Any alarms, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 7 | 301715 | 04 |  | Any alarms, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 8 | 301715 | 04 |  | Any alarms, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 9 | 301715 | 04 |  | Any alarms, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 10 | 301715 | 04 |  | Any alarms, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 11 | 301715 | 04 |  | Any alarms, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 12 | 301715 | 04 |  | Any alarms, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 13 | 301715 | 04 |  | Any alarms, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 14 | 301715 | 04 |  | Any alarms, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1714 | 15 | 301715 | 04 |  | Any alarms, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 0 | 301716 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 1 | 301716 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 2 | 301716 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 3 | 301716 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 4 | 301716 | 04 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 5 | 301716 | 04 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 6 | 301716 | 04 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 7 | 301716 | 04 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 8 | 301716 | 04 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 9 | 301716 | 04 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 10 | 301716 | 04 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 11 | 301716 | 04 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 12 | 301716 | 04 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 13 | 301716 | 04 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 14 | 301716 | 04 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1715 | 15 | 301716 | 04 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 0 | 301717 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 1 | 301717 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 2 | 301717 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 3 | 301717 | 04 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 4 | 301717 | 04 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 5 | 301717 | 04 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 6 | 301717 | 04 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 7 | 301717 | 04 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 8 | 301717 | 04 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 9 | 301717 | 04 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 10 | 301717 | 04 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 11 | 301717 | 04 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 12 | 301717 | 04 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 13 | 301717 | 04 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 14 | 301717 | 04 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1716 | 15 | 301717 | 04 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 0 | 301718 | 04 |  | Mains failure, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 1 | 301718 | 04 |  | Mains failure, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 2 | 301718 | 04 |  | Mains failure, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 3 | 301718 | 04 |  | Mains failure, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 4 | 301718 | 04 |  | Mains failure, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 5 | 301718 | 04 |  | Mains failure, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 6 | 301718 | 04 |  | Mains failure, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 7 | 301718 | 04 |  | Mains failure, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 8 | 301718 | 04 |  | Mains failure, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 9 | 301718 | 04 |  | Mains failure, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 10 | 301718 | 04 |  | Mains failure, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 11 | 301718 | 04 |  | Mains failure, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 12 | 301718 | 04 |  | Mains failure, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 13 | 301718 | 04 |  | Mains failure, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 14 | 301718 | 04 |  | Mains failure, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1717 | 15 | 301718 | 04 |  | Mains failure, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 0 | 301719 | 04 |  | MB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 1 | 301719 | 04 |  | MB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 2 | 301719 | 04 |  | MB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 3 | 301719 | 04 |  | MB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 4 | 301719 | 04 |  | MB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 5 | 301719 | 04 |  | MB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 6 | 301719 | 04 |  | MB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 7 | 301719 | 04 |  | MB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 8 | 301719 | 04 |  | MB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 9 | 301719 | 04 |  | MB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 10 | 301719 | 04 |  | MB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 11 | 301719 | 04 |  | MB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 12 | 301719 | 04 |  | MB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 13 | 301719 | 04 |  | MB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 14 | 301719 | 04 |  | MB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1718 | 15 | 301719 | 04 |  | MB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 0 | 301720 | 04 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 1 | 301720 | 04 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 2 | 301720 | 04 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 3 | 301720 | 04 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 4 | 301720 | 04 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 5 | 301720 | 04 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 6 | 301720 | 04 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 7 | 301720 | 04 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 8 | 301720 | 04 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 9 | 301720 | 04 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 10 | 301720 | 04 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 11 | 301720 | 04 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 12 | 301720 | 04 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 13 | 301720 | 04 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 14 | 301720 | 04 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1719 | 15 | 301720 | 04 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 0 | 301721 | 04 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 1 | 301721 | 04 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 2 | 301721 | 04 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 3 | 301721 | 04 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 4 | 301721 | 04 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 5 | 301721 | 04 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 6 | 301721 | 04 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 7 | 301721 | 04 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 8 | 301721 | 04 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 9 | 301721 | 04 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 10 | 301721 | 04 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 11 | 301721 | 04 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 12 | 301721 | 04 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 13 | 301721 | 04 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 14 | 301721 | 04 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1720 | 15 | 301721 | 04 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 0 | 301722 | 04 |  | TB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 1 | 301722 | 04 |  | TB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 2 | 301722 | 04 |  | TB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 3 | 301722 | 04 |  | TB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 4 | 301722 | 04 |  | TB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 5 | 301722 | 04 |  | TB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 6 | 301722 | 04 |  | TB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 7 | 301722 | 04 |  | TB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 8 | 301722 | 04 |  | TB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 9 | 301722 | 04 |  | TB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 10 | 301722 | 04 |  | TB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 11 | 301722 | 04 |  | TB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 12 | 301722 | 04 |  | TB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 13 | 301722 | 04 |  | TB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 14 | 301722 | 04 |  | TB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1721 | 15 | 301722 | 04 |  | TB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 0 | 301723 | 04 |  | Any alarms, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 1 | 301723 | 04 |  | Any alarms, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 2 | 301723 | 04 |  | Any alarms, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 3 | 301723 | 04 |  | Any alarms, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 4 | 301723 | 04 |  | Any alarms, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 5 | 301723 | 04 |  | Any alarms, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 6 | 301723 | 04 |  | Any alarms, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1722 | 7 | 301723 | 04 |  | Any alarms, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 0 | 301726 | 04 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 1 | 301726 | 04 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 2 | 301726 | 04 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 3 | 301726 | 04 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 4 | 301726 | 04 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 5 | 301726 | 04 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 6 | 301726 | 04 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1725 | 7 | 301726 | 04 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 0 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 1 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 2 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 3 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 4 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 5 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 6 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 7 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 8 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 9 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 10 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 11 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 12 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 13 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 14 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X | X | X
PM alarm | 1727 | 15 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 0 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 1 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 2 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 3 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 4 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 5 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 6 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X | X | X
PM alarm | 1728 | 7 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 0 | 301733 | 04 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 1 | 301733 | 04 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 2 | 301733 | 04 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 3 | 301733 | 04 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 4 | 301733 | 04 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 5 | 301733 | 04 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 6 | 301733 | 04 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 7 | 301733 | 04 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 8 | 301733 | 04 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 9 | 301733 | 04 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 10 | 301733 | 04 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 11 | 301733 | 04 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 12 | 301733 | 04 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 13 | 301733 | 04 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 14 | 301733 | 04 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1732 | 15 | 301733 | 04 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 0 | 301734 | 04 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 1 | 301734 | 04 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 2 | 301734 | 04 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 3 | 301734 | 04 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 4 | 301734 | 04 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 5 | 301734 | 04 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 6 | 301734 | 04 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 7 | 301734 | 04 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 8 | 301734 | 04 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 9 | 301734 | 04 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 10 | 301734 | 04 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 11 | 301734 | 04 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 12 | 301734 | 04 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 13 | 301734 | 04 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 14 | 301734 | 04 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1733 | 15 | 301734 | 04 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 0 | 301735 | 04 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 1 | 301735 | 04 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 2 | 301735 | 04 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 3 | 301735 | 04 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 4 | 301735 | 04 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 5 | 301735 | 04 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 6 | 301735 | 04 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1734 | 7 | 301735 | 04 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 0 | 301736 | 04 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 1 | 301736 | 04 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 2 | 301736 | 04 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 3 | 301736 | 04 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 4 | 301736 | 04 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 5 | 301736 | 04 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 6 | 301736 | 04 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 7 | 301736 | 04 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 8 | 301736 | 04 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 9 | 301736 | 04 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 10 | 301736 | 04 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 11 | 301736 | 04 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 12 | 301736 | 04 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 13 | 301736 | 04 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 14 | 301736 | 04 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1735 | 15 | 301736 | 04 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 0 | 301737 | 04 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 1 | 301737 | 04 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 2 | 301737 | 04 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 3 | 301737 | 04 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 4 | 301737 | 04 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 5 | 301737 | 04 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 6 | 301737 | 04 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 7 | 301737 | 04 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 8 | 301737 | 04 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 9 | 301737 | 04 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 10 | 301737 | 04 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 11 | 301737 | 04 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 12 | 301737 | 04 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 13 | 301737 | 04 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 14 | 301737 | 04 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1736 | 15 | 301737 | 04 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 0 | 301738 | 04 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 1 | 301738 | 04 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 2 | 301738 | 04 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 3 | 301738 | 04 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 4 | 301738 | 04 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 5 | 301738 | 04 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 6 | 301738 | 04 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1737 | 7 | 301738 | 04 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 0 | 301739 | 04 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 1 | 301739 | 04 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 2 | 301739 | 04 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 3 | 301739 | 04 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 4 | 301739 | 04 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 5 | 301739 | 04 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 6 | 301739 | 04 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1738 | 7 | 301739 | 04 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 0 | 301740 | 04 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 1 | 301740 | 04 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 2 | 301740 | 04 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 3 | 301740 | 04 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 4 | 301740 | 04 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 5 | 301740 | 04 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 6 | 301740 | 04 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 7 | 301740 | 04 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 8 | 301740 | 04 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 9 | 301740 | 04 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 10 | 301740 | 04 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 11 | 301740 | 04 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 12 | 301740 | 04 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 13 | 301740 | 04 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 14 | 301740 | 04 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1739 | 15 | 301740 | 04 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 0 | 301741 | 04 |  | Hz/V present, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 1 | 301741 | 04 |  | Hz/V present, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 2 | 301741 | 04 |  | Hz/V present, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 3 | 301741 | 04 |  | Hz/V present, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 4 | 301741 | 04 |  | Hz/V present, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 5 | 301741 | 04 |  | Hz/V present, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 6 | 301741 | 04 |  | Hz/V present, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 7 | 301741 | 04 |  | Hz/V present, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 8 | 301741 | 04 |  | Hz/V present, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 9 | 301741 | 04 |  | Hz/V present, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 10 | 301741 | 04 |  | Hz/V present, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 11 | 301741 | 04 |  | Hz/V present, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 12 | 301741 | 04 |  | Hz/V present, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 13 | 301741 | 04 |  | Hz/V present, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 14 | 301741 | 04 |  | Hz/V present, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1740 | 15 | 301741 | 04 |  | Hz/V present, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 0 | 301742 | 04 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 1 | 301742 | 04 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 2 | 301742 | 04 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 3 | 301742 | 04 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 4 | 301742 | 04 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 5 | 301742 | 04 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 6 | 301742 | 04 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1741 | 7 | 301742 | 04 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 0 | 301750 | 04 |  | Dry Mode active on ID1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 1 | 301750 | 04 |  | Dry Mode active on ID2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 2 | 301750 | 04 |  | Dry Mode active on ID3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 3 | 301750 | 04 |  | Dry Mode active on ID4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 4 | 301750 | 04 |  | Dry Mode active on ID5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 5 | 301750 | 04 |  | Dry Mode active on ID6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 6 | 301750 | 04 |  | Dry Mode active on ID7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 7 | 301750 | 04 |  | Dry Mode active on ID8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 8 | 301750 | 04 |  | Dry Mode active on ID9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 9 | 301750 | 04 |  | Dry Mode active on ID10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 10 | 301750 | 04 |  | Dry Mode active on ID11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 11 | 301750 | 04 |  | Dry Mode active on ID12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 12 | 301750 | 04 |  | Dry Mode active on ID13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 13 | 301750 | 04 |  | Dry Mode active on ID14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 14 | 301750 | 04 |  | Dry Mode active on ID15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1749 | 15 | 301750 | 04 |  | Dry Mode active on ID16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 0 | 301751 | 04 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 1 | 301751 | 04 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 2 | 301751 | 04 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 3 | 301751 | 04 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 4 | 301751 | 04 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 5 | 301751 | 04 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 6 | 301751 | 04 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 7 | 301751 | 04 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 8 | 301751 | 04 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 9 | 301751 | 04 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 10 | 301751 | 04 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 11 | 301751 | 04 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 12 | 301751 | 04 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 13 | 301751 | 04 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 14 | 301751 | 04 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1750 | 15 | 301751 | 04 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 0 | 301752 | 04 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 1 | 301752 | 04 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 2 | 301752 | 04 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 3 | 301752 | 04 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 4 | 301752 | 04 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 5 | 301752 | 04 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 6 | 301752 | 04 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 7 | 301752 | 04 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 8 | 301752 | 04 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 9 | 301752 | 04 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 10 | 301752 | 04 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 11 | 301752 | 04 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 12 | 301752 | 04 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 13 | 301752 | 04 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 14 | 301752 | 04 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1751 | 15 | 301752 | 04 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 0 | 301753 | 04 |  | GB synchronising, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 1 | 301753 | 04 |  | GB synchronising, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 2 | 301753 | 04 |  | GB synchronising, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 3 | 301753 | 04 |  | GB synchronising, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 4 | 301753 | 04 |  | GB synchronising, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 5 | 301753 | 04 |  | GB synchronising, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 6 | 301753 | 04 |  | GB synchronising, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 7 | 301753 | 04 |  | GB synchronising, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 8 | 301753 | 04 |  | GB synchronising, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 9 | 301753 | 04 |  | GB synchronising, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 10 | 301753 | 04 |  | GB synchronising, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 11 | 301753 | 04 |  | GB synchronising, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 12 | 301753 | 04 |  | GB synchronising, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 13 | 301753 | 04 |  | GB synchronising, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 14 | 301753 | 04 |  | GB synchronising, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1752 | 15 | 301753 | 04 |  | GB synchronising, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 0 | 301754 | 04 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 1 | 301754 | 04 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 2 | 301754 | 04 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 3 | 301754 | 04 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 4 | 301754 | 04 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 5 | 301754 | 04 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 6 | 301754 | 04 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 7 | 301754 | 04 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 8 | 301754 | 04 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 9 | 301754 | 04 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 10 | 301754 | 04 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 11 | 301754 | 04 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 12 | 301754 | 04 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 13 | 301754 | 04 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 14 | 301754 | 04 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1753 | 15 | 301754 | 04 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 0 | 301755 | 04 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 1 | 301755 | 04 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 2 | 301755 | 04 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 3 | 301755 | 04 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 4 | 301755 | 04 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 5 | 301755 | 04 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 6 | 301755 | 04 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 7 | 301755 | 04 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 8 | 301755 | 04 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 9 | 301755 | 04 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 10 | 301755 | 04 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 11 | 301755 | 04 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 12 | 301755 | 04 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 13 | 301755 | 04 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 14 | 301755 | 04 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1754 | 15 | 301755 | 04 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 0 | 301756 | 04 |  | Running, ID 17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 1 | 301756 | 04 |  | Running, ID 18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 2 | 301756 | 04 |  | Running, ID 19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 3 | 301756 | 04 |  | Running, ID 20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 4 | 301756 | 04 |  | Running, ID 21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 5 | 301756 | 04 |  | Running, ID 22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 6 | 301756 | 04 |  | Running, ID 23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 7 | 301756 | 04 |  | Running, ID 24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 8 | 301756 | 04 |  | Running, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 9 | 301756 | 04 |  | Running, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 10 | 301756 | 04 |  | Running, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 11 | 301756 | 04 |  | Running, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 12 | 301756 | 04 |  | Running, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 13 | 301756 | 04 |  | Running, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 14 | 301756 | 04 |  | Running, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1755 | 15 | 301756 | 04 |  | Running, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 0 | 301757 | 04 |  | Dry Mode active on ID17 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 1 | 301757 | 04 |  | Dry Mode active on ID18 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 2 | 301757 | 04 |  | Dry Mode active on ID19 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 3 | 301757 | 04 |  | Dry Mode active on ID20 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 4 | 301757 | 04 |  | Dry Mode active on ID21 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 5 | 301757 | 04 |  | Dry Mode active on ID22 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 6 | 301757 | 04 |  | Dry Mode active on ID23 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 7 | 301757 | 04 |  | Dry Mode active on ID24 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 8 | 301757 | 04 |  | Dry Mode active on ID25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 9 | 301757 | 04 |  | Dry Mode active on ID26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 10 | 301757 | 04 |  | Dry Mode active on ID27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 11 | 301757 | 04 |  | Dry Mode active on ID28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 12 | 301757 | 04 |  | Dry Mode active on ID29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 13 | 301757 | 04 |  | Dry Mode active on ID30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 14 | 301757 | 04 |  | Dry Mode active on ID31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1756 | 15 | 301757 | 04 |  | Dry Mode active on ID32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 0 | 301758 | 04 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 1 | 301758 | 04 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 2 | 301758 | 04 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 3 | 301758 | 04 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 4 | 301758 | 04 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 5 | 301758 | 04 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 6 | 301758 | 04 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 7 | 301758 | 04 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 8 | 301758 | 04 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 9 | 301758 | 04 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 10 | 301758 | 04 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 11 | 301758 | 04 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 12 | 301758 | 04 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 13 | 301758 | 04 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 14 | 301758 | 04 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1757 | 15 | 301758 | 04 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 0 | 301759 | 04 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 1 | 301759 | 04 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 2 | 301759 | 04 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 3 | 301759 | 04 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 4 | 301759 | 04 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 5 | 301759 | 04 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 6 | 301759 | 04 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 7 | 301759 | 04 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 8 | 301759 | 04 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 9 | 301759 | 04 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 10 | 301759 | 04 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 11 | 301759 | 04 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 12 | 301759 | 04 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 13 | 301759 | 04 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 14 | 301759 | 04 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1758 | 15 | 301759 | 04 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 0 | 301760 | 04 |  | MB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 1 | 301760 | 04 |  | MB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 2 | 301760 | 04 |  | MB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 3 | 301760 | 04 |  | MB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 4 | 301760 | 04 |  | MB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 5 | 301760 | 04 |  | MB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 6 | 301760 | 04 |  | MB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 7 | 301760 | 04 |  | MB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 8 | 301760 | 04 |  | MB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 9 | 301760 | 04 |  | MB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 10 | 301760 | 04 |  | MB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 11 | 301760 | 04 |  | MB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 12 | 301760 | 04 |  | MB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 13 | 301760 | 04 |  | MB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 14 | 301760 | 04 |  | MB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1759 | 15 | 301760 | 04 |  | MB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 0 | 301761 | 04 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 1 | 301761 | 04 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 2 | 301761 | 04 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 3 | 301761 | 04 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 4 | 301761 | 04 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 5 | 301761 | 04 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 6 | 301761 | 04 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 7 | 301761 | 04 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 8 | 301761 | 04 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 9 | 301761 | 04 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 10 | 301761 | 04 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 11 | 301761 | 04 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 12 | 301761 | 04 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 13 | 301761 | 04 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 14 | 301761 | 04 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1760 | 15 | 301761 | 04 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 0 | 301762 | 04 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 1 | 301762 | 04 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 2 | 301762 | 04 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 3 | 301762 | 04 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 4 | 301762 | 04 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 5 | 301762 | 04 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 6 | 301762 | 04 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 7 | 301762 | 04 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 8 | 301762 | 04 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 9 | 301762 | 04 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 10 | 301762 | 04 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 11 | 301762 | 04 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 12 | 301762 | 04 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 13 | 301762 | 04 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 14 | 301762 | 04 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1761 | 15 | 301762 | 04 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 0 | 301763 | 04 |  | TB synchronising, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 1 | 301763 | 04 |  | TB synchronising, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 2 | 301763 | 04 |  | TB synchronising, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 3 | 301763 | 04 |  | TB synchronising, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 4 | 301763 | 04 |  | TB synchronising, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 5 | 301763 | 04 |  | TB synchronising, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 6 | 301763 | 04 |  | TB synchronising, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 7 | 301763 | 04 |  | TB synchronising, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 8 | 301763 | 04 |  | TB synchronising, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 9 | 301763 | 04 |  | TB synchronising, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 10 | 301763 | 04 |  | TB synchronising, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 11 | 301763 | 04 |  | TB synchronising, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 12 | 301763 | 04 |  | TB synchronising, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 13 | 301763 | 04 |  | TB synchronising, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 14 | 301763 | 04 |  | TB synchronising, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1762 | 15 | 301763 | 04 |  | TB synchronising, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 0 | 301764 | 04 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 1 | 301764 | 04 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 2 | 301764 | 04 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 3 | 301764 | 04 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 4 | 301764 | 04 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 5 | 301764 | 04 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 6 | 301764 | 04 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 7 | 301764 | 04 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 8 | 301764 | 04 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 9 | 301764 | 04 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 10 | 301764 | 04 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 11 | 301764 | 04 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 12 | 301764 | 04 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 13 | 301764 | 04 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 14 | 301764 | 04 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1763 | 15 | 301764 | 04 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 0 | 301765 | 04 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 1 | 301765 | 04 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 2 | 301765 | 04 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 3 | 301765 | 04 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 4 | 301765 | 04 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 5 | 301765 | 04 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 6 | 301765 | 04 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 7 | 301765 | 04 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 8 | 301765 | 04 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 9 | 301765 | 04 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 10 | 301765 | 04 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 11 | 301765 | 04 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 12 | 301765 | 04 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 13 | 301765 | 04 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 14 | 301765 | 04 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1764 | 15 | 301765 | 04 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 0 | 301766 | 04 |  | Mains OK, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 1 | 301766 | 04 |  | Mains OK, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 2 | 301766 | 04 |  | Mains OK, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 3 | 301766 | 04 |  | Mains OK, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 4 | 301766 | 04 |  | Mains OK, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 5 | 301766 | 04 |  | Mains OK, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 6 | 301766 | 04 |  | Mains OK, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 7 | 301766 | 04 |  | Mains OK, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 8 | 301766 | 04 |  | Mains OK, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 9 | 301766 | 04 |  | Mains OK, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 10 | 301766 | 04 |  | Mains OK, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 11 | 301766 | 04 |  | Mains OK, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 12 | 301766 | 04 |  | Mains OK, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 13 | 301766 | 04 |  | Mains OK, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 14 | 301766 | 04 |  | Mains OK, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1765 | 15 | 301766 | 04 |  | Mains OK, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 0 | 301767 | 04 |  | Mains not in semi 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 1 | 301767 | 04 |  | Mains not in semi 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 2 | 301767 | 04 |  | Mains not in semi 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 3 | 301767 | 04 |  | Mains not in semi 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 4 | 301767 | 04 |  | Mains not in semi 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 5 | 301767 | 04 |  | Mains not in semi 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 6 | 301767 | 04 |  | Mains not in semi 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 7 | 301767 | 04 |  | Mains not in semi 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 8 | 301767 | 04 |  | Mains not in semi 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 9 | 301767 | 04 |  | Mains not in semi 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 10 | 301767 | 04 |  | Mains not in semi 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 11 | 301767 | 04 |  | Mains not in semi 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 12 | 301767 | 04 |  | Mains not in semi 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 13 | 301767 | 04 |  | Mains not in semi 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 14 | 301767 | 04 |  | Mains not in semi 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1766 | 15 | 301767 | 04 |  | Mains not in semi 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 0 | 301768 | 04 |  | Mains failure, ID 1 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 1 | 301768 | 04 |  | Mains failure, ID 2 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 2 | 301768 | 04 |  | Mains failure, ID 3 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 3 | 301768 | 04 |  | Mains failure, ID 4 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 4 | 301768 | 04 |  | Mains failure, ID 5 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 5 | 301768 | 04 |  | Mains failure, ID 6 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 6 | 301768 | 04 |  | Mains failure, ID 7 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 7 | 301768 | 04 |  | Mains failure, ID 8 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 8 | 301768 | 04 |  | Mains failure, ID 9 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 9 | 301768 | 04 |  | Mains failure, ID 10 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 10 | 301768 | 04 |  | Mains failure, ID 11 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 11 | 301768 | 04 |  | Mains failure, ID 12 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 12 | 301768 | 04 |  | Mains failure, ID 13 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 13 | 301768 | 04 |  | Mains failure, ID 14 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 14 | 301768 | 04 |  | Mains failure, ID 15 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1767 | 15 | 301768 | 04 |  | Mains failure, ID 16 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 0 | 301770 | 04 |  | PV breaker OFF, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 1 | 301770 | 04 |  | PV breaker OFF, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 2 | 301770 | 04 |  | PV breaker OFF, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 3 | 301770 | 04 |  | PV breaker OFF, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 4 | 301770 | 04 |  | PV breaker OFF, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 5 | 301770 | 04 |  | PV breaker OFF, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 6 | 301770 | 04 |  | PV breaker OFF, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1769 | 7 | 301770 | 04 |  | PV breaker OFF, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 0 | 301771 | 04 |  | Breaker synchronising, PV ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 1 | 301771 | 04 |  | Breaker synchronising, PV ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 2 | 301771 | 04 |  | Breaker synchronising, PV ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 3 | 301771 | 04 |  | Breaker synchronising, PV ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 4 | 301771 | 04 |  | Breaker synchronising, PV ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 5 | 301771 | 04 |  | Breaker synchronising, PV ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 6 | 301771 | 04 |  | Breaker synchronising, PV ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1770 | 7 | 301771 | 04 |  | Breaker synchronising, PV ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 0 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 1 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 2 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 3 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 4 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 5 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 6 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 7 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 8 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 9 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 10 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 11 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 12 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 13 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 14 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1771 | 15 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 0 | 301773 | 04 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 1 | 301773 | 04 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 2 | 301773 | 04 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 3 | 301773 | 04 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 4 | 301773 | 04 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 5 | 301773 | 04 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 6 | 301773 | 04 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 7 | 301773 | 04 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 8 | 301773 | 04 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 9 | 301773 | 04 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 10 | 301773 | 04 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 11 | 301773 | 04 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 12 | 301773 | 04 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 13 | 301773 | 04 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 14 | 301773 | 04 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1772 | 15 | 301773 | 04 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 0 | 301774 | 04 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 1 | 301774 | 04 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 2 | 301774 | 04 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 3 | 301774 | 04 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 4 | 301774 | 04 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 5 | 301774 | 04 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 6 | 301774 | 04 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 7 | 301774 | 04 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 8 | 301774 | 04 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 9 | 301774 | 04 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 10 | 301774 | 04 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 11 | 301774 | 04 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 12 | 301774 | 04 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 13 | 301774 | 04 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 14 | 301774 | 04 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1773 | 15 | 301774 | 04 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 0 | 301775 | 04 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 1 | 301775 | 04 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 2 | 301775 | 04 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 3 | 301775 | 04 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 4 | 301775 | 04 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 5 | 301775 | 04 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 6 | 301775 | 04 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 7 | 301775 | 04 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 8 | 301775 | 04 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 9 | 301775 | 04 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 10 | 301775 | 04 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 11 | 301775 | 04 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 12 | 301775 | 04 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 13 | 301775 | 04 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 14 | 301775 | 04 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1774 | 15 | 301775 | 04 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 0 | 301776 | 04 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 1 | 301776 | 04 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 2 | 301776 | 04 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 3 | 301776 | 04 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 4 | 301776 | 04 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 5 | 301776 | 04 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 6 | 301776 | 04 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 7 | 301776 | 04 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 8 | 301776 | 04 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 9 | 301776 | 04 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 10 | 301776 | 04 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 11 | 301776 | 04 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 12 | 301776 | 04 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 13 | 301776 | 04 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 14 | 301776 | 04 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1775 | 15 | 301776 | 04 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 0 | 301777 | 04 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 1 | 301777 | 04 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 2 | 301777 | 04 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 3 | 301777 | 04 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 4 | 301777 | 04 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 5 | 301777 | 04 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 6 | 301777 | 04 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 7 | 301777 | 04 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 8 | 301777 | 04 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 9 | 301777 | 04 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 10 | 301777 | 04 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 11 | 301777 | 04 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 12 | 301777 | 04 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 13 | 301777 | 04 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 14 | 301777 | 04 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1776 | 15 | 301777 | 04 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 0 | 301778 | 04 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 1 | 301778 | 04 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 2 | 301778 | 04 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 3 | 301778 | 04 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 4 | 301778 | 04 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 5 | 301778 | 04 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 6 | 301778 | 04 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 7 | 301778 | 04 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 8 | 301778 | 04 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 9 | 301778 | 04 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 10 | 301778 | 04 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 11 | 301778 | 04 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 12 | 301778 | 04 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 13 | 301778 | 04 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 14 | 301778 | 04 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1777 | 15 | 301778 | 04 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 0 | 301779 | 04 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 1 | 301779 | 04 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 2 | 301779 | 04 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 3 | 301779 | 04 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 4 | 301779 | 04 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 5 | 301779 | 04 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 6 | 301779 | 04 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 7 | 301779 | 04 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 8 | 301779 | 04 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 9 | 301779 | 04 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 10 | 301779 | 04 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 11 | 301779 | 04 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 12 | 301779 | 04 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 13 | 301779 | 04 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 14 | 301779 | 04 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1778 | 15 | 301779 | 04 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 0 | 301780 | 04 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 1 | 301780 | 04 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 2 | 301780 | 04 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 3 | 301780 | 04 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 4 | 301780 | 04 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 5 | 301780 | 04 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 6 | 301780 | 04 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 7 | 301780 | 04 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 8 | 301780 | 04 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 9 | 301780 | 04 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 10 | 301780 | 04 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 11 | 301780 | 04 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 12 | 301780 | 04 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 13 | 301780 | 04 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 14 | 301780 | 04 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1779 | 15 | 301780 | 04 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 0 | 301781 | 04 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 1 | 301781 | 04 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 2 | 301781 | 04 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 3 | 301781 | 04 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 4 | 301781 | 04 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 5 | 301781 | 04 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 6 | 301781 | 04 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 7 | 301781 | 04 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 8 | 301781 | 04 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 9 | 301781 | 04 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 10 | 301781 | 04 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 11 | 301781 | 04 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 12 | 301781 | 04 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 13 | 301781 | 04 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 14 | 301781 | 04 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1780 | 15 | 301781 | 04 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 0 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 1 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 2 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 3 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 4 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 5 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 6 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 7 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 8 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 9 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 10 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 11 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 12 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 13 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 14 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1781 | 15 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 0 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 1 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 2 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 3 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 4 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 5 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 6 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 7 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 8 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 9 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 10 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 11 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 12 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 13 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 14 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1782 | 15 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 0 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 1 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 2 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 3 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 4 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 5 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 6 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 7 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 8 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 9 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 10 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 11 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 12 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 13 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 14 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1783 | 15 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 0 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 1 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 2 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 3 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 4 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 5 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 6 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 7 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 8 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 9 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 10 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 11 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 12 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 13 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 14 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1784 | 15 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 0 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 1 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 2 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 3 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 4 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 5 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 6 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 7 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 8 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 9 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 10 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 11 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 12 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 13 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 14 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1785 | 15 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 0 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 1 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 2 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 3 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 4 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 5 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 6 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 7 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 8 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 9 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 10 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 11 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 12 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 13 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 14 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1786 | 15 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 0 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 1 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 2 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 3 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 4 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 5 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 6 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 7 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 8 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 9 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 10 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 11 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 12 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 13 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 14 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1787 | 15 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 0 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 1 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 2 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 3 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 4 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 5 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 6 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 7 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 8 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 9 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 10 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 11 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 12 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 13 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 14 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1788 | 15 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 0 | 301790 | 04 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 1 | 301790 | 04 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 2 | 301790 | 04 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 3 | 301790 | 04 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 4 | 301790 | 04 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 5 | 301790 | 04 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 6 | 301790 | 04 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 7 | 301790 | 04 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 8 | 301790 | 04 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 9 | 301790 | 04 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 10 | 301790 | 04 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 11 | 301790 | 04 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 12 | 301790 | 04 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 13 | 301790 | 04 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 14 | 301790 | 04 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1789 | 15 | 301790 | 04 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 0 | 301791 | 04 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 1 | 301791 | 04 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 2 | 301791 | 04 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 3 | 301791 | 04 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 4 | 301791 | 04 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 5 | 301791 | 04 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 6 | 301791 | 04 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 7 | 301791 | 04 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 8 | 301791 | 04 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 9 | 301791 | 04 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 10 | 301791 | 04 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 11 | 301791 | 04 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 12 | 301791 | 04 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 13 | 301791 | 04 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 14 | 301791 | 04 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1790 | 15 | 301791 | 04 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 0 | 301792 | 04 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 1 | 301792 | 04 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 2 | 301792 | 04 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 3 | 301792 | 04 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 4 | 301792 | 04 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 5 | 301792 | 04 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 6 | 301792 | 04 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 7 | 301792 | 04 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 8 | 301792 | 04 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 9 | 301792 | 04 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 10 | 301792 | 04 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 11 | 301792 | 04 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 12 | 301792 | 04 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 13 | 301792 | 04 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 14 | 301792 | 04 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1791 | 15 | 301792 | 04 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 0 | 301793 | 04 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 1 | 301793 | 04 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 2 | 301793 | 04 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 3 | 301793 | 04 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 4 | 301793 | 04 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 5 | 301793 | 04 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 6 | 301793 | 04 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 7 | 301793 | 04 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 8 | 301793 | 04 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 9 | 301793 | 04 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 10 | 301793 | 04 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 11 | 301793 | 04 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 12 | 301793 | 04 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 13 | 301793 | 04 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 14 | 301793 | 04 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1792 | 15 | 301793 | 04 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 0 | 301794 | 04 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 1 | 301794 | 04 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 2 | 301794 | 04 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 3 | 301794 | 04 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 4 | 301794 | 04 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 5 | 301794 | 04 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 6 | 301794 | 04 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 7 | 301794 | 04 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 8 | 301794 | 04 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 9 | 301794 | 04 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 10 | 301794 | 04 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 11 | 301794 | 04 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 12 | 301794 | 04 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 13 | 301794 | 04 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 14 | 301794 | 04 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1793 | 15 | 301794 | 04 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 0 | 301795 | 04 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 1 | 301795 | 04 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 2 | 301795 | 04 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 3 | 301795 | 04 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 4 | 301795 | 04 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 5 | 301795 | 04 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 6 | 301795 | 04 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 7 | 301795 | 04 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 8 | 301795 | 04 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 9 | 301795 | 04 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 10 | 301795 | 04 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 11 | 301795 | 04 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 12 | 301795 | 04 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 13 | 301795 | 04 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 14 | 301795 | 04 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1794 | 15 | 301795 | 04 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 0 | 301796 | 04 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 1 | 301796 | 04 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 2 | 301796 | 04 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 3 | 301796 | 04 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 4 | 301796 | 04 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 5 | 301796 | 04 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 6 | 301796 | 04 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 7 | 301796 | 04 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 8 | 301796 | 04 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 9 | 301796 | 04 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 10 | 301796 | 04 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 11 | 301796 | 04 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 12 | 301796 | 04 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 13 | 301796 | 04 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 14 | 301796 | 04 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1795 | 15 | 301796 | 04 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 0 | 301797 | 04 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 1 | 301797 | 04 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 2 | 301797 | 04 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 3 | 301797 | 04 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 4 | 301797 | 04 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 5 | 301797 | 04 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 6 | 301797 | 04 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 7 | 301797 | 04 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 8 | 301797 | 04 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 9 | 301797 | 04 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 10 | 301797 | 04 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 11 | 301797 | 04 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 12 | 301797 | 04 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 13 | 301797 | 04 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 14 | 301797 | 04 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X | X | X
PM Plant logic state | 1796 | 15 | 301797 | 04 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X | X | X
Counter | 1842 |  | 301843 | 04 |  | BB Export, active energy counter, total | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 1842 |  | 301843 | 04 |  | BB Export active energy counter, total | INT32s | ABCD | 0 | kWh |  | X
Counter | 1842 |  | 301843 | 04 |  | Bus B Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 1844 |  | 301845 | 04 |  | BB Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 1844 |  | 301845 | 04 |  | BB Export, active energy counter, month | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 1844 |  | 301845 | 04 |  | Bus B Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 1846 |  | 301847 | 04 |  | BB Export, active energy counter, week | INT32s | ABCD | 0 | kWh |  | X | X | X
Counter | 1846 |  | 301847 | 04 |  | Bus B Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1848 |  | 301849 | 04 |  | BB Export, active energy counter, day | INT32s | ABCD | 0 | kWh |  | X | X | X
Counter | 1848 |  | 301849 | 04 |  | Bus B Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1850 |  | 301851 | 04 |  | BB Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  | X | X
Counter | 1850 |  | 301851 | 04 |  | BB Export, active energy counter, total | INT32s | ABCD | 0 | kvarh |  | X
Counter | 1850 |  | 301851 | 04 |  | Bus B Export, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X
Counter | 1852 |  | 301853 | 04 |  | BB Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  | X | X | X
Counter | 1852 |  | 301853 | 04 |  | Bus B Export, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X
Counter | 1854 |  | 301855 | 04 |  | BB Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  | X | X | X
Counter | 1854 |  | 301855 | 04 |  | Bus B Export, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X
Counter | 1856 |  | 301857 | 04 |  | BB Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  | X | X | X
Counter | 1856 |  | 301857 | 04 |  | Bus B Export, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X
Counter | 1858 |  | 301859 | 04 |  | BB Import, active energy counter, total | INT32s | ABCD | 0 | kWh |  | X | X | X
Counter | 1858 |  | 301859 | 04 |  | Bus B Import, active energy counter, total | INT32s | ABCD | 0 | kWh | X
Counter | 1860 |  | 301861 | 04 |  | BB Import, active energy counter, month | INT32s | ABCD | 0 | kWh |  | X | X | X
Counter | 1860 |  | 301861 | 04 |  | Bus B Import, active energy counter, month | INT32s | ABCD | 0 | kWh | X
Counter | 1862 |  | 301863 | 04 |  | BB Import, active energy counter, week | INT32s | ABCD | 0 | kWh |  | X | X | X
Counter | 1862 |  | 301863 | 04 |  | Bus B Import, active energy counter, week | INT32s | ABCD | 0 | kWh | X
Counter | 1864 |  | 301865 | 04 |  | BB Import, active energy counter, day | INT32s | ABCD | 0 | kWh |  |  | X | X
Counter | 1864 |  | 301865 | 04 |  | BB Import,active energy counter, day | INT32s | ABCD | 0 | kWh |  | X
Counter | 1864 |  | 301865 | 04 |  | Bus B Import, active energy counter, day | INT32s | ABCD | 0 | kWh | X
Counter | 1866 |  | 301867 | 04 |  | BB Import, reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  |  | X | X
Counter | 1866 |  | 301867 | 04 |  | BB Import reactive energy counter, total | INT32s | ABCD | 0 | kvarh |  | X
Counter | 1866 |  | 301867 | 04 |  | Bus B Import, reactive energy counter, total | INT32s | ABCD | 0 | kvarh | X
Counter | 1868 |  | 301869 | 04 |  | BB Import, reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  |  | X | X
Counter | 1868 |  | 301869 | 04 |  | BB Import reactive energy counter, month | INT32s | ABCD | 0 | kvarh |  | X
Counter | 1868 |  | 301869 | 04 |  | Bus B Import, reactive energy counter, month | INT32s | ABCD | 0 | kvarh | X
Counter | 1870 |  | 301871 | 04 |  | BB Import, reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  |  | X | X
Counter | 1870 |  | 301871 | 04 |  | BB Import reactive energy counter, week | INT32s | ABCD | 0 | kvarh |  | X
Counter | 1870 |  | 301871 | 04 |  | Bus B Import, reactive energy counter, week | INT32s | ABCD | 0 | kvarh | X
Counter | 1872 |  | 301873 | 04 |  | BB Import, reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  |  | X | X
Counter | 1872 |  | 301873 | 04 |  | BB Import reactive energy counter, day | INT32s | ABCD | 0 | kvarh |  | X
Counter | 1872 |  | 301873 | 04 |  | Bus B Import, reactive energy counter, day | INT32s | ABCD | 0 | kvarh | X
DC measurement | 1900 |  | 301901 | 04 |  | General purpose PID 1 prioritized input | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 1901 |  | 301902 | 04 |  | General purpose PID 2 prioritized input | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 1902 |  | 301903 | 04 |  | General purpose PID 3 prioritized input | INT16s | AB | 0 |  | X | X | X | X | X | X
DC measurement | 1903 |  | 301904 | 04 |  | General purpose PID 4 prioritized input | INT16s | AB | 0 |  | X | X | X | X | X | X
PM AC measurement | 1917 |  | 301918 | 04 |  | Cos phi from PMS ID 1 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1918 |  | 301919 | 04 |  | Cos phi from PMS ID 2 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1919 |  | 301920 | 04 |  | Cos phi from PMS ID 3 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1920 |  | 301921 | 04 |  | Cos phi from PMS ID 4 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1921 |  | 301922 | 04 |  | Cos phi from PMS ID 5 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1922 |  | 301923 | 04 |  | Cos phi from PMS ID 6 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1923 |  | 301924 | 04 |  | Cos phi from PMS ID 7 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1924 |  | 301925 | 04 |  | Cos phi from PMS ID 8 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1925 |  | 301926 | 04 |  | Cos phi from PMS ID 9 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1926 |  | 301927 | 04 |  | Cos phi from PMS ID 10 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1927 |  | 301928 | 04 |  | Cos phi from PMS ID 11 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1928 |  | 301929 | 04 |  | Cos phi from PMS ID 12 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1929 |  | 301930 | 04 |  | Cos phi from PMS ID 13 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1930 |  | 301931 | 04 |  | Cos phi from PMS ID 14 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1931 |  | 301932 | 04 |  | Cos phi from PMS ID 15 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1932 |  | 301933 | 04 |  | Cos phi from PMS ID 16 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1933 |  | 301934 | 04 |  | Cos phi from PMS ID 17 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1934 |  | 301935 | 04 |  | Cos phi from PMS ID 18 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1935 |  | 301936 | 04 |  | Cos phi from PMS ID 19 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1936 |  | 301937 | 04 |  | Cos phi from PMS ID 20 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1937 |  | 301938 | 04 |  | Cos phi from PMS ID 21 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1938 |  | 301939 | 04 |  | Cos phi from PMS ID 22 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1939 |  | 301940 | 04 |  | Cos phi from PMS ID 23 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1940 |  | 301941 | 04 |  | Cos phi from PMS ID 24 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1941 |  | 301942 | 04 |  | Cos phi from PMS ID 25 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1942 |  | 301943 | 04 |  | Cos phi from PMS ID 26 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1943 |  | 301944 | 04 |  | Cos phi from PMS ID 27 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1944 |  | 301945 | 04 |  | Cos phi from PMS ID 28 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1945 |  | 301946 | 04 |  | Cos phi from PMS ID 29 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1946 |  | 301947 | 04 |  | Cos phi from PMS ID 30 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1947 |  | 301948 | 04 |  | Cos phi from PMS ID 31 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1948 |  | 301949 | 04 |  | Cos phi from PMS ID 32 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1957 |  | 301958 | 04 |  | Apparent power ID 1 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1958 |  | 301959 | 04 |  | Apparent power ID 2 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1959 |  | 301960 | 04 |  | Apparent power ID 3 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1960 |  | 301961 | 04 |  | Apparent power ID 4 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1961 |  | 301962 | 04 |  | Apparent power ID 5 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1962 |  | 301963 | 04 |  | Apparent power ID 6 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1963 |  | 301964 | 04 |  | Apparent power ID 7 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1964 |  | 301965 | 04 |  | Apparent power ID 8 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1965 |  | 301966 | 04 |  | Apparent power ID 9 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1966 |  | 301967 | 04 |  | Apparent power ID 10 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1967 |  | 301968 | 04 |  | Apparent power ID 11 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1968 |  | 301969 | 04 |  | Apparent power ID 12 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1969 |  | 301970 | 04 |  | Apparent power ID 13 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1970 |  | 301971 | 04 |  | Apparent power ID 14 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1971 |  | 301972 | 04 |  | Apparent power ID 15 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1972 |  | 301973 | 04 |  | Apparent power ID 16 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1973 |  | 301974 | 04 |  | Apparent power ID 17 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1974 |  | 301975 | 04 |  | Apparent power ID 18 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1975 |  | 301976 | 04 |  | Apparent power ID 19 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1976 |  | 301977 | 04 |  | Apparent power ID 20 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1977 |  | 301978 | 04 |  | Apparent power ID 21 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1978 |  | 301979 | 04 |  | Apparent power ID 22 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1979 |  | 301980 | 04 |  | Apparent power ID 23 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1980 |  | 301981 | 04 |  | Apparent power ID 24 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1981 |  | 301982 | 04 |  | Apparent power ID 25 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1982 |  | 301983 | 04 |  | Apparent power ID 26 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1983 |  | 301984 | 04 |  | Apparent power ID 27 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1984 |  | 301985 | 04 |  | Apparent power ID 28 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1985 |  | 301986 | 04 |  | Apparent power ID 29 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1986 |  | 301987 | 04 |  | Apparent power ID 30 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1987 |  | 301988 | 04 |  | Apparent power ID 31 | INT16s | AB | 0 |  |  | X | X
PM AC measurement | 1988 |  | 301989 | 04 |  | Apparent power ID 32 | INT16s | AB | 0 |  |  | X | X
PV monitoring area | 40000 |  | 340001 | 04 |  | DC voltage string 05 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40001 |  | 340002 | 04 |  | DC power string 05 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40002 |  | 340003 | 04 |  | DC voltage string 06 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40003 |  | 340004 | 04 |  | DC power string 06 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40004 |  | 340005 | 04 |  | DC voltage string 07 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40005 |  | 340006 | 04 |  | DC power string 07 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40006 |  | 340007 | 04 |  | DC voltage string 08 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40007 |  | 340008 | 04 |  | DC power string 08 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40008 |  | 340009 | 04 |  | DC voltage string 09 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40009 |  | 340010 | 04 |  | DC power string 09 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40010 |  | 340011 | 04 |  | DC voltage string 10 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40011 |  | 340012 | 04 |  | DC power string 10 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40012 |  | 340013 | 04 |  | DC voltage string 11 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40013 |  | 340014 | 04 |  | DC power string 11 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40014 |  | 340015 | 04 |  | DC voltage string 12 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 40015 |  | 340016 | 04 |  | DC power string 12 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 40016 |  | 340017 | 04 |  | DC current string 01 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40017 |  | 340018 | 04 |  | DC current string 02 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40018 |  | 340019 | 04 |  | DC current string 03 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40019 |  | 340020 | 04 |  | DC current string 04 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40020 |  | 340021 | 04 |  | DC current string 05 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40021 |  | 340022 | 04 |  | DC current string 06 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40022 |  | 340023 | 04 |  | DC current string 07 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40023 |  | 340024 | 04 |  | DC current string 08 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40024 |  | 340025 | 04 |  | DC current string 09 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40025 |  | 340026 | 04 |  | DC current string 10 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40026 |  | 340027 | 04 |  | DC current string 11 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40027 |  | 340028 | 04 |  | DC current string 12 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40028 |  | 340029 | 04 |  | DC current string 13 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40029 |  | 340030 | 04 |  | DC current string 14 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40030 |  | 340031 | 04 |  | DC current string 15 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40031 |  | 340032 | 04 |  | DC current string 16 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40032 |  | 340033 | 04 |  | DC current string 17 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40033 |  | 340034 | 04 |  | DC current string 18 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40034 |  | 340035 | 04 |  | DC current string 19 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40035 |  | 340036 | 04 |  | DC current string 20 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40036 |  | 340037 | 04 |  | DC current string 21 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40037 |  | 340038 | 04 |  | DC current string 22 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40038 |  | 340039 | 04 |  | DC current string 23 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 40039 |  | 340040 | 04 |  | DC current string 24 | INT16u | AB | 1 | A |  |  |  | X
PV monitoring area | 47000 |  | 347001 | 04 |  | Inverter serial number 01-02 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47001 |  | 347002 | 04 |  | Inverter serial number 03-04 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47002 |  | 347003 | 04 |  | Inverter serial number 05-06 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47003 |  | 347004 | 04 |  | Inverter serial number 07-08 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47004 |  | 347005 | 04 |  | Inverter serial number 09-10 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47005 |  | 347006 | 04 |  | Inverter serial number 11-12 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47006 |  | 347007 | 04 |  | Inverter serial number 13-14 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47007 |  | 347008 | 04 |  | Inverter serial number 15-16 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47008 |  | 347009 | 04 |  | Inverter serial number 17-18 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47009 |  | 347010 | 04 |  | Inverter serial number 19-20 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47010 |  | 347011 | 04 |  | Inverter serial number 21-22 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47011 |  | 347012 | 04 |  | Inverter serial number 23-24 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47012 |  | 347013 | 04 |  | Inverter serial number 25-26 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47013 |  | 347014 | 04 |  | Inverter serial number 27-28 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47014 |  | 347015 | 04 |  | Inverter serial number 19-30 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47015 |  | 347016 | 04 |  | Inverter serial number 31-32 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47016 |  | 347017 | 04 |  | Inverter model 01-02 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47017 |  | 347018 | 04 |  | Inverter model 03-04 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47018 |  | 347019 | 04 |  | Inverter model 05-06 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47019 |  | 347020 | 04 |  | Inverter model 07-08 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47020 |  | 347021 | 04 |  | Inverter model 09-10 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47021 |  | 347022 | 04 |  | Inverter model 11-12 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47022 |  | 347023 | 04 |  | Inverter model 13-14 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47023 |  | 347024 | 04 |  | Inverter model 15-16 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47024 |  | 347025 | 04 |  | Inverter model 17-18 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47025 |  | 347026 | 04 |  | Inverter model 19-20 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47026 |  | 347027 | 04 |  | Inverter model 21-22 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47027 |  | 347028 | 04 |  | Inverter model 23-24 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47028 |  | 347029 | 04 |  | Inverter model 25-26 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47029 |  | 347030 | 04 |  | Inverter model 27-28 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47030 |  | 347031 | 04 |  | Inverter model 19-30 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47031 |  | 347032 | 04 |  | Inverter model 31-32 (format maker-dependent) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 47032 |  | 347033 | 04 |  | Rated active power size | INT16u | AB | 1 | kW |  |  |  | X
PV monitoring area | 47033 |  | 347034 | 04 |  | Rated reactive power size | INT16u | AB | 1 | kVAr |  |  |  | X
PV monitoring area | 47034 |  | 347035 | 04 |  | Country code (format maker-dependent) | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 47035 |  | 347036 | 04 |  | DC voltage string 01 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47036 |  | 347037 | 04 |  | DC power string 01 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 47037 |  | 347038 | 04 |  | DC voltage string 02 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47038 |  | 347039 | 04 |  | DC power string 02 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 47039 |  | 347040 | 04 |  | DC voltage string 03 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47040 |  | 347041 | 04 |  | DC power string 03 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 47041 |  | 347042 | 04 |  | DC voltage string 04 | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47042 |  | 347043 | 04 |  | DC power string 04 | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 47043 |  | 347044 | 04 |  | AC active power | INT16s | AB | 1 | kW |  |  |  | X
PV monitoring area | 47044 |  | 347045 | 04 |  | AC reactive power | INT16s | AB | 1 | kVAr |  |  |  | X
PV monitoring area | 47045 |  | 347046 | 04 |  | AC apparent power | INT16s | AB | 1 | kVA |  |  |  | X
PV monitoring area | 47046 |  | 347047 | 04 |  | Energy produced | INT32u | ABCD | 0 | kWh |  |  |  | X
PV monitoring area | 47048 |  | 347049 | 04 |  | Energy produced today | INT32u | ABCD | 1 | kWh |  |  |  | X
PV monitoring area | 47050 |  | 347051 | 04 |  | Operating hours | INT32u | ABCD | 0 | hour |  |  |  | X
PV monitoring area | 47052 |  | 347053 | 04 |  | Operating minutes today | INT16u | AB | 0 | minute |  |  |  | X
PV monitoring area | 47053 |  | 347054 | 04 |  | Cabinet temperature | INT16s | AB | 1 | Deg C |  |  |  | X
PV monitoring area | 47054 |  | 347055 | 04 |  | Phase1 to neutral PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47055 |  | 347056 | 04 |  | Phase2 to neutral PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47056 |  | 347057 | 04 |  | Phase3 to neutral PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47057 |  | 347058 | 04 |  | Phase1 to phase2 PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47058 |  | 347059 | 04 |  | Phase2 to phase3 PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47059 |  | 347060 | 04 |  | Phase3 to phase1 PV voltage | INT16u | AB | 1 | V |  |  |  | X
PV monitoring area | 47060 |  | 347061 | 04 |  | Grid frequency | INT16u | AB | 1 | Hz |  |  |  | X
PV monitoring area | 47061 |  | 347062 | 04 |  | Active power reference (format maker-dependent) | INT16s | AB | 0 |  |  |  |  | X
PV monitoring area | 47062 |  | 347063 | 04 |  | Reactive power reference (format maker-dependent) | INT16s | AB | 0 |  |  |  |  | X
PV monitoring area | 47063 |  | 347064 | 04 |  | Inverter state (format maker-dependent) | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 47064 |  | 347065 | 04 |  | Fault code (format maker-dependent) | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 47069 |  | 347070 | 04 |  | 0: Inverter not alive on communication link. 1: Inverter alive on communication link. | INT16s | AB | 0 |  |  |  |  | X
PV monitoring area | 49940 |  | 349941 | 04 |  | PV monitoring version | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49941 |  | 349942 | 04 |  | PV protocol selection | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49942 |  | 349943 | 04 |  | PV protocol selection 01-02 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49943 |  | 349944 | 04 |  | PV protocol selection 03-04 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49944 |  | 349945 | 04 |  | PV protocol selection 05-06 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49945 |  | 349946 | 04 |  | PV protocol selection 07-08 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49946 |  | 349947 | 04 |  | PV protocol selection 09-10 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49947 |  | 349948 | 04 |  | PV protocol selection 11-12 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49948 |  | 349949 | 04 |  | PV protocol selection 13-14 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49949 |  | 349950 | 04 |  | PV protocol selection 15-16 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49950 |  | 349951 | 04 |  | PV protocol selection 17-18 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49951 |  | 349952 | 04 |  | PV protocol selection 19-20 (string access) | string | AB | 0 |  |  |  |  | X
PV monitoring area | 49952 |  | 349953 | 04 |  | Monitoring enabled: 0: Disabled. 1: Enabled | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49953 |  | 349954 | 04 |  | Number of inverter to monitor | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49954 |  | 349955 | 04 |  | Number of inverters missing | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49955 |  | 349956 | 04 |  | Lowest inverter ID missing | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49956 |  | 349957 | 04 |  | Highest inverter ID missing | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49957 |  | 349958 | 04 |  | P ref type: 0: Percentage. 1: kW | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49958 |  | 349959 | 04 |  | Q ref type: 0: Percentage. 1: kW. 2: Cos phi. 3: PF | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49959 |  | 349960 | 04 |  | P ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49960 |  | 349961 | 04 |  | Q ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  |  |  |  | X
PV monitoring area | 49961 |  | 349962 | 04 |  | Lowest Modbus ID of the inverters | INT16u | AB | 0 |  |  |  |  | X