## About
iE 350 Marine Power management Parameter lists
Software version
The information contained in these parameter lists (Revision A) are applicable to software version 2.0.18.x of the iE 350 Marine Power management.
Controller types
This document includes the parameter and I/O function lists for these controller types:
GENSET controller
EMERGENCY genset controller
HYBRID controller
SHAFT generator controller
SHORE connection controller
BUS TIE breaker controller
See the iE 350 Marine Power management Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
Custom parameters and Custom alarm are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include Fieldbus and Communication settings. These are not included in the parameter lists.
Input/output functions
The input/output function lists are based on the functions that can be selected in PICUS, under Configure > Input/ouput.
If you cannot find an input/output function in PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Path = The location of the input/output function.
Name = The name of the input/output function.
IO type = The type of the input/output function.
DI = Digital input function DO = Digital output function AI = Analogue input function AO = Analogue output function
Unit = The default unit of measurement for the input/output function.*
Data type = The data type for the input/output function.
Minimum = The default minimum value of the input/output function.*
Maximum = The default maximum value of the input/output function.*
Decimals = The number of decimal places for the value.*
Hidden = To see this input/output function, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
[User defined] is used where part of the path is configurable.

## GENSET parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on | X
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated | X
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0 |  | X
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Consumer side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > CT - ACM3.2 - Neutral side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Neutral side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Neutral side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker closed
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Stabilised differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > Stabilised differential current | Action | INT32 | Trip generator breaker + AVR + stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > High set differential current | Set point | FLOAT | 800 | % | 50 | 1200 | 0
Generator > Current protections > High set differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > High set differential current | Action | INT32 | Trip generator breaker + AVR + stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > High set differential current | Inhibit |  | Engine not running
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker closed
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker closed
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | 2 |  | 0 | 4 | 0 | 0: Off
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2 |  | X
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Configuration | Generator breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic | X
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1 |  | X
Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
Local power management > Parallel timers > DG-SG max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > DG-SG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Parallel timers > DG-SC max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > DG-SC max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 0 | 3600 | 0
Local power management > Asymmetric load sharing > P configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Asymmetric load sharing > P configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
Local power management > Asymmetric load sharing > P configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Asymmetric load sharing > Q configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Asymmetric load sharing > Q configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
Local power management > Asymmetric load sharing > Q configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Blackout > Blackout close | Allow blackout recovery | INT32 | 1 |  | 0 | 1 | 0
Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 101 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 101 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine

## GENSET IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Engine > Command | Block engine start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
11280003 | Engine > Function | Remove start (release crank relay) | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Function | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180002 | Engine > Idle run | End idle start | DI |  | BOOL_NUM | 0 | 1 | 0
11180003 | Engine > Idle run | End idle stop | DI |  | BOOL_NUM | 0 | 1 | 0
11080100 | Engine > Safety shutdown | Manual reset | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100045 | Regulators > GOV > External set points | Activate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100046 | Regulators > GOV > External set points | Deactivate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100047 | Regulators > GOV > External set points | Activate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100048 | Regulators > GOV > External set points | Deactivate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100039 | Regulators > AVR > External set points | Activate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100040 | Regulators > AVR > External set points | Deactivate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100041 | Regulators > AVR > External set points | Activate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100042 | Regulators > AVR > External set points | Deactivate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100043 | Regulators > AVR > External set points | Activate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100044 | Regulators > AVR > External set points | Deactivate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100051 | Regulators > Common | Regulation ON | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130003 | Power management | Block blackout start | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
90130005 | Power management | Block load-dependent stop | DI |  | BOOL_NUM | 0 | 1 | 0
90130006 | Power management | Deactivate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130007 | Power management | Activate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130009 | Power management | Force all controllers in section to SWBD control | DI |  | BOOL_NUM | 0 | 1 | 0
90130010 | Power management | Force all gensets in section to MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
90130011 | Power management | Force all gensets in section to AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90130015 | Power management | Precautionary genset start | DI |  | BOOL_NUM | 0 | 1 | 0
90230005 | Power management | 1st priority | DI |  | BOOL_NUM | 0 | 1 | 0
90230012 | Power management | Activate asymmetric P load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230013 | Power management | Activate asymmetric Q load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230014 | Power management | Deactivate asymmetric P load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230015 | Power management | Deactivate asymmetric Q load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230017 | Power management | Last priority | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
11480000 | Engine > Controls | Priming | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080021 | Engine > State | Not ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Engine > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Engine > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080024 | Engine > State | Cooldown | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Engine > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11080028 | Engine > State | Extended stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080101 | Engine > Safety shutdown | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Generator breaker > Controls | GB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any GB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any GB + AVR + stop engine alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000503 | Local > Mode | In AUTO | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
126219000 | Load reduction | Load reduction output 1 | DO |  | BOOL_NUM | 0 | 1 | 0
126229000 | Load reduction | Load reduction output 2 | DO |  | BOOL_NUM | 0 | 1 | 0
90220002 | Power management | Is first priority | DO |  | BOOL_NUM | 0 | 1 | 0
90220003 | Power management | Is first standby | DO |  | BOOL_NUM | 0 | 1 | 0
90220009 | Power management | Is second standby | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 2 | X
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
90220004 | Local power management > Asymmetric load sharing | P set point | AI | % | FLOAT | 1 | 100 | 0
90220005 | Local power management > Asymmetric load sharing | Q set point | AI | % | FLOAT | 1 | 100 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40150060 | Generator > Frequency (f) - ACM3.2 | Generator ¦ Frequency | AO | Hz | FLOAT | 0 | 1500000 | 1
40150000 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150001 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150002 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150003 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150004 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150025 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150026 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150027 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150028 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150029 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150050 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150051 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150052 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150053 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150054 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150055 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150056 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150057 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150058 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150059 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## EMERGENCY genset parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on | X
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0 |  | X
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Consumer side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > CT - ACM3.2 - Neutral side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Neutral side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Neutral side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 1 | Inhibit |  | EDG in parallel
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 2 | Inhibit |  | EDG in parallel
Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Over-voltage 3 | Inhibit |  | EDG in parallel
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > Stabilised differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > Stabilised differential current | Action | INT32 | Trip generator breaker + AVR + stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > High set differential current | Set point | FLOAT | 800 | % | 50 | 1200 | 0
Generator > Current protections > High set differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > High set differential current | Action | INT32 | Trip generator breaker + AVR + stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Current protections > High set differential current | Inhibit |  | Engine not running
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Over-frequency 1 | Inhibit |  | EDG in parallel
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Over-frequency 2 | Inhibit |  | EDG in parallel
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 15 | s | 0 | 3600 | 1
Busbar > AC setup > Blackout detection | TB under-voltage timer | FLOAT | 15 | s | 0 | 3600 | 0
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 5 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, Tie breaker open
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, Tie breaker open
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 2: Relay
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Configuration | Generator breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Tie breaker configuration > Configuration | Tie breaker sync enabled | INT32 | 1 |  | 0 | 1 | 0
Breakers > Tie breaker configuration > Configuration | Tie breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.1 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Tie breaker configuration > Synchronisation failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Closing failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > Tie breaker monitoring > Tripped (external) | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > Tie breaker monitoring > Short circuit | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1
Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
Local power management > Parallel timers > EDG max. parallel time | Delay | FLOAT | 30 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > EDG max. parallel time | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Return modes > After EDG test | Mode | INT32 | Auto |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Emergency generator > Test delay | Test time | FLOAT | 30 | s | 10 | 3600 | 0
Local power management > Emergency generator > Test base load | Base load | FLOAT | 50 | % | 10 | 100 | 1
Local power management > Emergency generator > Test type | Type | INT32 | Engine test |  |  |  |  | 0: Engine test, 1: Parallel test, 2: Load take-over test
Local power management > Emergency generator > Blackout handling | Blackout control | INT32 | Open TB and start engine |  |  |  |  | 0: Open TB and start engine, 1: Start engine and open TB
Local power management > Emergency generator > EDG not ready for blackout | Delay | FLOAT | 7 | s | 1 | 180 | 1
Local power management > Emergency generator > EDG not ready for blackout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local power management > Emergency generator > Operator confirms harbour operation | Enable | INT32 | 1 |  | 0 | 1 | 0
Local power management > Emergency generator > Solo supply harbour operation | Enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 8: Trip AVR, 9: Trip generator breaker + AVR, 10: Trip generator breaker + AVR + stop engine, 11: Trip generator breaker + AVR + shutdown engine

## EMERGENCY genset IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Engine > Command | Block engine start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90630000 | Engine > Command | Test genset | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
11280003 | Engine > Function | Remove start (release crank relay) | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Function | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180002 | Engine > Idle run | End idle start | DI |  | BOOL_NUM | 0 | 1 | 0
11180003 | Engine > Idle run | End idle stop | DI |  | BOOL_NUM | 0 | 1 | 0
11080100 | Engine > Safety shutdown | Manual reset | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100045 | Regulators > GOV > External set points | Activate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100046 | Regulators > GOV > External set points | Deactivate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100047 | Regulators > GOV > External set points | Activate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100048 | Regulators > GOV > External set points | Deactivate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100039 | Regulators > AVR > External set points | Activate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100040 | Regulators > AVR > External set points | Deactivate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100041 | Regulators > AVR > External set points | Activate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100042 | Regulators > AVR > External set points | Deactivate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100043 | Regulators > AVR > External set points | Activate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100044 | Regulators > AVR > External set points | Deactivate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100051 | Regulators > Common | Regulation ON | DI |  | BOOL_NUM | 0 | 1 | 0
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
20280028 | Breakers > Tie breaker > Command | TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280029 | Breakers > Tie breaker > Command | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280031 | Breakers > Tie breaker > Command | Block TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280000 | Breakers > Tie breaker > Feedback | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280001 | Breakers > Tie breaker > Feedback | TB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20280004 | Breakers > Tie breaker > Feedback | TB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20280012 | Breakers > Tie breaker > Feedback | TB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130003 | Power management | Block blackout start | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
90130005 | Power management | Block load-dependent stop | DI |  | BOOL_NUM | 0 | 1 | 0
90130006 | Power management | Deactivate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130007 | Power management | Activate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130009 | Power management | Force all controllers in section to SWBD control | DI |  | BOOL_NUM | 0 | 1 | 0
90130010 | Power management | Force all gensets in section to MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
90130011 | Power management | Force all gensets in section to AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90130015 | Power management | Precautionary genset start | DI |  | BOOL_NUM | 0 | 1 | 0
90630004 | Power management | Harbour operation | DI |  | BOOL_NUM | 0 | 1 | 0
90630005 | Power management | Main busbar is OK | DI |  | BOOL_NUM | 0 | 1 | 0
90630006 | Power management | Allow harbour operation | DI |  | BOOL_NUM | 0 | 1 | 0
90630007 | Power management | Reject harbour operation | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
11480000 | Engine > Controls | Priming | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080021 | Engine > State | Not ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Engine > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Engine > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080024 | Engine > State | Cooldown | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Engine > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11080028 | Engine > State | Extended stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080101 | Engine > Safety shutdown | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Generator breaker > Controls | GB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
20280002 | Breakers > Tie breaker > Controls | TB open | DO |  | BOOL_NUM | 0 | 1 | 0
20280003 | Breakers > Tie breaker > Controls | TB close | DO |  | BOOL_NUM | 0 | 1 | 0
20280027 | Breakers > Tie breaker > Controls | TB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20280014 | Breakers > Tie breaker > State | TB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20280015 | Breakers > Tie breaker > State | TB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20280024 | Breakers > Tie breaker > State | TB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20280025 | Breakers > Tie breaker > State | TB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20280026 | Breakers > Tie breaker > State | TB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035011 | Alarm system > State | Any TB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any GB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any GB + AVR + stop engine alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000503 | Local > Mode | In AUTO | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
126219000 | Load reduction | Load reduction output 1 | DO |  | BOOL_NUM | 0 | 1 | 0
126229000 | Load reduction | Load reduction output 2 | DO |  | BOOL_NUM | 0 | 1 | 0
90620001 | Power management | Harbour operation active | DO |  | BOOL_NUM | 0 | 1 | 0
90630008 | Power management | Test sequence is active | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | -100 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 2 | X
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40150060 | Generator > Frequency (f) - ACM3.2 | Generator ¦ Frequency | AO | Hz | FLOAT | 0 | 1500000 | 1
40150000 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150001 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150002 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150003 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150004 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150025 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150026 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150027 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150028 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150029 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150050 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150051 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150052 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150053 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150054 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150055 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150056 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150057 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150058 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150059 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## HYBRID parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Inverter > Start sequence > Restrictions | Allow start when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
Inverter > Start sequence > Start | Start on | FLOAT | 5 | s | 1 | 180 | 1
Inverter > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Stop sequence > Restrictions | Allow stop when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
Inverter > Stop sequence > Stop failure | Delay | FLOAT | 5 | s | 0 | 300 | 0
Inverter > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Inverter > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Inverter > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Inverter > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Inverter > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Inverter > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Inverter > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Inverter > AC setup > CT - ACM3.2 - Consumer side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Inverter > AC setup > CT - ACM3.2 - Consumer side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Inverter > AC setup > CT - ACM3.2 - Consumer side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Inverter > AC setup > CT - ACM3.2 - Neutral side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Inverter > AC setup > CT - ACM3.2 - Neutral side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Inverter > AC setup > CT - ACM3.2 - Neutral side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Inverter > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Inverter > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Inverter > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Inverter > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Inverter > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Inverter > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Inverter > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Inverter > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Inverter > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Inverter > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Inverter > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Inverter > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Inverter > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Inverter > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Inverter > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Inverter > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Inverter > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Inverter > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Inverter > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Inverter > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Inverter > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Inverter > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Inverter > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Inverter > Emergency stop > Emergency stop | Action | INT32 | Trip breaker and stop inverter |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Inverter > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker closed
Inverter > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 1 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 2 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Inverter > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Inverter > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Inverter > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Under-voltage 3 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Inverter > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Inverter > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Inverter > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Inverter > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Inverter > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Inverter > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Inverter > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Inverter > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Inverter > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Inverter > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Inverter > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Inverter > Current protections > Over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Inverter > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Inverter > Current protections > Fast over-current 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Inverter > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Inverter > Current protections > Fast over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Inverter > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Inverter > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Inverter > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Inverter > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Inverter > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Inverter > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Inverter > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Inverter > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Inverter > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Inverter > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Inverter > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Inverter > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Inverter > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Inverter > Current protections > Inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Inverter > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Inverter > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Inverter > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > Stabilised differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Inverter > Current protections > Stabilised differential current | Action | INT32 | Trip breaker + AVR + stop inverter |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > High set differential current | Set point | FLOAT | 800 | % | 50 | 1200 | 0
Inverter > Current protections > High set differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Inverter > Current protections > High set differential current | Action | INT32 | Trip breaker + AVR + stop inverter |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Current protections > High set differential current | Inhibit |  | Inverter not running
Inverter > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Inverter > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker closed
Inverter > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Inverter > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker closed
Inverter > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Inverter > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Frequency protections > Under-frequency 1 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Inverter > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Inverter > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Frequency protections > Under-frequency 2 | Inhibit |  | Inverter not running, Breaker closed
Inverter > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Inverter > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Inverter > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Power protections > Reverse power 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 1 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Inverter > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Inverter > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Inverter > Power protections > Reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Reverse power 2 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Inverter > Power protections > Overload reverse power 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Inverter > Power protections > Overload reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload reverse power 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload reverse power 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Power protections > Overload reverse power 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Inverter > Power protections > Overload reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Power protections > Overload reverse power 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Inverter > Power protections > Overload reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Inverter > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Inverter > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Inverter > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Inverter > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Inverter > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Inverter > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Breaker open, ACM wire break
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 2: Relay
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > Inverter breaker configuration > Configuration | Type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Inverter breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Inverter breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Inverter breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Inverter breaker configuration > Configuration | Breaker open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Inverter breaker configuration > Configuration | Allow breaker close when | INT32 | Inverter is started |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
Breakers > Inverter breaker configuration > Configuration | Allow breaker open when | INT32 | Inverter in any state |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
Breakers > Inverter breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Inverter breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Inverter breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Inverter breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Inverter breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Inverter breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Inverter breaker monitoring > Synchronisation failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Inverter breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Inverter breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Inverter breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Inverter breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Inverter breaker monitoring > Closing failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Inverter breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Inverter breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > Inverter breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > Inverter breaker monitoring > Short circuit | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1
Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
Local power management > Parallel timers > Hybrid-SG max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > Hybrid-SG max. parallel time | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Local power management > Parallel timers > Hybrid-SG max. parallel time | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Local power management > Parallel timers > Hybrid-SC max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > Hybrid-SC max. parallel time | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Local power management > Parallel timers > Hybrid-SC max. parallel time | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
Local power management > Asymmetric load sharing > P configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Asymmetric load sharing > P configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
Local power management > Asymmetric load sharing > P configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Asymmetric load sharing > Q configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Asymmetric load sharing > Q configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
Local power management > Asymmetric load sharing > Q configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Blackout > Blackout close | Allow blackout recovery | INT32 | 1 |  | 0 | 1 | 0
Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 101 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 101 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
Local power management > Hybrid modes > Standby > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
Local power management > Hybrid modes > Standby > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > Standby > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Hybrid modes > Standby > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > Standby > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Hybrid modes > PTO (power take off) > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
Local power management > Hybrid modes > PTO (power take off) > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > PTO (power take off) > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Hybrid modes > PTO (power take off) > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > PTO (power take off) > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Hybrid modes > PTI (power take in) > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
Local power management > Hybrid modes > PTI (power take in) > Configuration | Nominal load | FLOAT | 0 | kW | 0 | 1000000 | 0
Local power management > Hybrid modes > PTI (power take in) > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > PTI (power take in) > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local power management > Hybrid modes > PTI (power take in) > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Local power management > Hybrid modes > PTI (power take in) > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 8: Trip AVR, 9: Trip breaker + AVR, 10: Trip breaker + AVR + stop inverter, 12: Stop inverter

## HYBRID IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Inverter > Command | Start inverter | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Inverter > Command | Stop inverter | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Inverter > Command | Block inverter start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Inverter > Command | Connect (inverter/breaker) | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Inverter > Command | Disconnect (inverter/breaker) | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Inverter > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100045 | Regulators > GOV > External set points | Activate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100046 | Regulators > GOV > External set points | Deactivate external f offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100047 | Regulators > GOV > External set points | Activate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100048 | Regulators > GOV > External set points | Deactivate external P set point | DI |  | BOOL_NUM | 0 | 1 | 0
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100039 | Regulators > AVR > External set points | Activate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100040 | Regulators > AVR > External set points | Deactivate external V offset | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100041 | Regulators > AVR > External set points | Activate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100042 | Regulators > AVR > External set points | Deactivate external Q set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100043 | Regulators > AVR > External set points | Activate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100044 | Regulators > AVR > External set points | Deactivate external cos phi set point | DI |  | BOOL_NUM | 0 | 1 | 0 | X
70100051 | Regulators > Common | Regulation ON | DI |  | BOOL_NUM | 0 | 1 | 0
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Inverter breaker > Command | Breaker close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Inverter breaker > Command | Breaker open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Inverter breaker > Command | Block breaker close | DI |  | BOOL_NUM | 0 | 1 | 0
90930000 | Breakers > Inverter breaker > Command | Block breaker open | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Inverter breaker > Feedback | Breaker open feedback | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Inverter breaker > Feedback | Breaker closed feedback | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Inverter breaker > Feedback | Breaker spring-loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Inverter breaker > Feedback | Breaker short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130003 | Power management | Block blackout start | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
90130005 | Power management | Block load-dependent stop | DI |  | BOOL_NUM | 0 | 1 | 0
90130006 | Power management | Deactivate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130007 | Power management | Activate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130009 | Power management | Force all controllers in section to SWBD control | DI |  | BOOL_NUM | 0 | 1 | 0
90130010 | Power management | Force all gensets in section to MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
90130011 | Power management | Force all gensets in section to AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90130015 | Power management | Precautionary genset start | DI |  | BOOL_NUM | 0 | 1 | 0
90230005 | Power management | 1st priority | DI |  | BOOL_NUM | 0 | 1 | 0
90230012 | Power management | Activate asymmetric P load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230013 | Power management | Activate asymmetric Q load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230014 | Power management | Deactivate asymmetric P load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230015 | Power management | Deactivate asymmetric Q load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
90230017 | Power management | Last priority | DI |  | BOOL_NUM | 0 | 1 | 0
90920150 | Power management | Standby request (Hybrid) | DI |  | BOOL_NUM | 0 | 1 | 0
90920151 | Power management | Standby ready (Hybrid) | DI |  | BOOL_NUM | 0 | 1 | 0
90920200 | Power management | PTI request | DI |  | BOOL_NUM | 0 | 1 | 0
90920201 | Power management | PTI ready | DI |  | BOOL_NUM | 0 | 1 | 0
90920202 | Power management | PTI running | DI |  | BOOL_NUM | 0 | 1 | 0
90920250 | Power management | PTO request | DI |  | BOOL_NUM | 0 | 1 | 0
90920251 | Power management | PTO ready | DI |  | BOOL_NUM | 0 | 1 | 0
90920252 | Power management | PTO running | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11080000 | Inverter > Controls | Run | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Inverter > Controls | Stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Inverter > Controls | Start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Inverter > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Inverter > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Inverter > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11280005 | Inverter > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Inverter > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Inverter > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Inverter > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Inverter > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Inverter > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Inverter > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Inverter > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Inverter > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120018 | Inverter > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Inverter breaker > Controls | Breaker open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Inverter breaker > Controls | Breaker close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Inverter breaker > Controls | Breaker trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Inverter breaker > State | Breaker is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Inverter breaker > State | Breaker is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Inverter breaker > State | Breaker is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Inverter breaker > State | Breaker is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Inverter breaker > State | Breaker is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any breaker trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any breaker trip and stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035013 | Alarm system > State | Any stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any breaker + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any breaker + AVR + stop inverter alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000503 | Local > Mode | In AUTO | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
126219000 | Load reduction | Load reduction output 1 | DO |  | BOOL_NUM | 0 | 1 | 0
126229000 | Load reduction | Load reduction output 2 | DO |  | BOOL_NUM | 0 | 1 | 0
90220002 | Power management | Is first priority | DO |  | BOOL_NUM | 0 | 1 | 0
90220003 | Power management | Is first standby | DO |  | BOOL_NUM | 0 | 1 | 0
90220009 | Power management | Is second standby | DO |  | BOOL_NUM | 0 | 1 | 0
90920153 | Power management | Standby acknowledge (Hybrid) | DO |  | BOOL_NUM | 0 | 1 | 0
90920159 | Power management | Standby active (Hybrid) | DO |  | BOOL_NUM | 0 | 1 | 0
90920203 | Power management | PTI acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0
90920209 | Power management | PTI active | DO |  | BOOL_NUM | 0 | 1 | 0
90920253 | Power management | PTO acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0
90920259 | Power management | PTO active | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40600510 | Inverter > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Inverter > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Inverter > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Inverter > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | -100 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1 | X
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | -100 | 100 | 0 | X
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 2 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
90220004 | Local power management > Asymmetric load sharing | P set point | AI | % | FLOAT | 1 | 100 | 0
90220005 | Local power management > Asymmetric load sharing | Q set point | AI | % | FLOAT | 1 | 100 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40600510 | Inverter > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Inverter > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Inverter > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Inverter > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Inverter > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Inverter > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Inverter > Voltage (V) | Inverter ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Inverter > Voltage (V) | Inverter ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Inverter > Voltage (V) | Inverter ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Inverter > Voltage (V) | Inverter ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Inverter > Voltage (V) | Inverter ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Inverter > Voltage (V) | Inverter ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Inverter > Voltage (V) | Inverter ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Inverter > Voltage (V) | Inverter ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Inverter > Voltage (V) | Inverter ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Inverter > Voltage (V) | Inverter ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Inverter > Voltage (V) | Inverter ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Inverter > Voltage (V) | Inverter ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Inverter > Voltage (V) | Inverter ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Inverter > Voltage (V) | Inverter ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Inverter > Voltage (V) | Inverter ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Inverter > Voltage (V) | Inverter ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Inverter > Frequency (f) (from voltage) | Inverter ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Inverter > Frequency (f) (from voltage) | Inverter ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Inverter > Frequency (f) (from current) | Inverter ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Inverter > Frequency (f) (from current) | Inverter ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Inverter > Frequency (f) (from current) | Inverter ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Inverter > Frequency (f) (from current) | Inverter ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Inverter > Frequency (f) (from current) | Inverter ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Inverter > Current (I) | Inverter ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Inverter > Current (I) | Inverter ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Inverter > Current (I) | Inverter ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Inverter > Current (I) | Inverter ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Inverter > Current (I) | Inverter ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Inverter > Current (I) | Inverter ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Inverter > Current (I) | Inverter ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Inverter > Current (I) | Inverter ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Inverter > Current (I) | Inverter ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Inverter > Current (I) | Inverter ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Inverter > Current (I) | Inverter ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40150060 | Inverter > Frequency (f) - ACM3.2 | Inverter ¦ Frequency | AO | Hz | FLOAT | 0 | 1500000 | 1
40150000 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L1 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150001 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L2 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150002 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L3 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150003 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Min. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150004 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Max. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150025 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L1 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150026 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L2 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150027 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L3 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150028 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Min. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150029 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Max. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150050 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L1 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150051 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L2 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150052 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L3 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150053 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Min. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150054 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Max. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150055 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L1 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150056 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L2 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150057 | Inverter > Current (I) - ACM3.2 | Inverter ¦ L3 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150058 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Min. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150059 | Inverter > Current (I) - ACM3.2 | Inverter ¦ Max. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Inverter > Power (P) | Inverter ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Inverter > Power (P) | Inverter ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Inverter > Power (P) | Inverter ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Inverter > Power (P) | Inverter ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Inverter > Power (P) | Inverter ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Inverter > Power (P) | Inverter ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Inverter > Power (P) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Inverter > Power (P) | Inverter ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Inverter > Power (P) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Inverter > Reactive power (Q) | Inverter ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Inverter > Reactive power (Q) | Inverter ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Inverter > Reactive power (Q) | Inverter ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Inverter > Reactive power (Q) | Inverter ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Inverter > Reactive power (Q) | Inverter ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Inverter > Reactive power (Q) | Inverter ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Inverter > Reactive power (Q) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Inverter > Reactive power (Q) | Inverter ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Inverter > Reactive power (Q) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Inverter > Apparent power (S) | Inverter ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Inverter > Apparent power (S) | Inverter ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Inverter > Apparent power (S) | Inverter ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Inverter > Apparent power (S) | Inverter ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Inverter > Apparent power (S) | Inverter ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Inverter > Apparent power (S) | Inverter ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Inverter > Apparent power (S) | Inverter ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Inverter > Apparent power (S) | Inverter ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Inverter > Apparent power (S) | Inverter ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Inverter > Power factor (PF) | Inverter ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Inverter > Power factor (PF) | Inverter ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Inverter > Phase angle | Inverter ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Inverter > Phase angle | Inverter ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Inverter > Phase angle | Inverter ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Inverter > Phase angle | Inverter ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Inverter > Phase angle | Inverter ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Inverter > Phase angle | Inverter ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## SHAFT generator parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Engine > Engine heater > Engine heater | Source selector | INT32 | 0 |  | 0 | 2147483647 | 0
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Consumer side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Consumer side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > CT - ACM3.2 - Neutral side | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Generator > AC setup > CT - ACM3.2 - Neutral side | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > CT - ACM3.2 - Neutral side | Current reference dir. | INT32 | Towards prot. obj. |  |  |  |  | 0: Towards prot. obj., 1: Away from prot. obj.
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 97 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Shaft breaker closed
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Shaft breaker closed
Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Over-voltage 3 | Inhibit |  | Shaft breaker closed
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Shaft breaker closed
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Shaft breaker closed
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Shaft breaker closed
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > Stabilised differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > Stabilised differential current | Action | INT32 | Trip generator breaker + AVR |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > High set differential current | Set point | FLOAT | 800 | % | 50 | 1200 | 0
Generator > Current protections > High set differential current | Delay | FLOAT | 0 | s | 0 | 60 | 2
Generator > Current protections > High set differential current | Action | INT32 | Trip generator breaker + AVR |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Current protections > High set differential current | Inhibit |  | Engine not running
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Frequency protections > Over-frequency 1 | Inhibit |  | Shaft breaker closed
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Frequency protections > Over-frequency 2 | Inhibit |  | Shaft breaker closed
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, Shaft breaker closed
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, Shaft breaker closed
Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Power protections > Reverse power 1 | Inhibit |  | Power take home active
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Power protections > Reverse power 2 | Inhibit |  | Power take home active
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Reactive power protections > Reactive power import 1 | Inhibit |  | Power take home active
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Generator > Reactive power protections > Reactive power import 2 | Inhibit |  | Power take home active
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Shaft breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Shaft breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Shaft breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Shaft breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Shaft breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Shaft breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Shaft breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Shaft breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Shaft breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Shaft breaker open, ACM wire break
Breakers > Shaft breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Shaft breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Shaft breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Shaft breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Shaft breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Shaft breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Shaft breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Shaft breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Shaft breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Shaft breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shaft breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shaft breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Shaft breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Shaft breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Shaft breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Shaft breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Shaft breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Shaft breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Shaft breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Shaft breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Shaft breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Shaft breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Shaft breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > Shaft breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > Shaft breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local power management > Parallel timers > SG-DG max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > SG-DG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local power management > Parallel timers > SG-Hybrid max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > SG-Hybrid max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local power management > Parallel timers > SG-SG max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
Local power management > Parallel timers > SG-SG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
Local power management > Shaft generator base load > Enable | Base load | INT32 | Off |  |  |  |  | 0: Off, 1: Active, 2: Active with priority
Local power management > Shaft generator base load > Power set point | Set point | FLOAT | 90 | % | 10 | 120 | 0
Local power management > Shaft generator base load > Min. set point | Minimum limit | FLOAT | 5 | % | 1 | 100 | 0
Local power management > Shaft generator base load > Max. set point | Maximum limit | FLOAT | 95 | % | 1 | 120 | 0
Local power management > Shaft generator PTH mode > Open point | Open point enabled | INT32 | 0 |  | 0 | 1 | 0
Local power management > Shaft generator PTH mode > Open point | Open when power below | FLOAT | 5 | % | 2 | 100 | 0
Local power management > Shaft generator PTH mode > Connect load | PTH connect load | FLOAT | 100 | kW | 1 | 900000 | 0
Local power management > Shaft generator f [Hz] variation > Frequency [Hz] variation | Enable | INT32 | 1 |  | 0 | 1 | 0
Local power management > Shaft generator f [Hz] variation > Engine start | Low frequency limit | FLOAT | 91 | % | 90 | 100 | 1
Local power management > Shaft generator f [Hz] variation > Engine start | High frequency limit | FLOAT | 109 | % | 100 | 110 | 1
Local power management > Shaft generator f [Hz] variation > Engine start | Delay | FLOAT | 0.5 | s | 0 | 10 | 1
Local power management > Shaft generator f [Hz] variation > Connect gensets | Low frequency limit | FLOAT | 90 | % | 90 | 100 | 1
Local power management > Shaft generator f [Hz] variation > Connect gensets | High frequency limit | FLOAT | 110 | % | 100 | 110 | 1
Local power management > Shaft generator f [Hz] variation > Connect gensets | Delay | FLOAT | 0.5 | s | 0 | 10 | 1
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker, 8: Trip AVR, 9: Trip generator breaker + AVR

## SHAFT generator IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180028 | Breakers > Shaft generator breaker > Command | SGB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Shaft generator breaker > Command | SGB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Shaft generator breaker > Command | Block SGB close | DI |  | BOOL_NUM | 0 | 1 | 0
90320003 | Breakers > Shaft generator breaker > Command | SG fixed speed | DI |  | BOOL_NUM | 0 | 1 | 0
90330003 | Breakers > Shaft generator breaker > Command | PTH mode | DI |  | BOOL_NUM | 0 | 1 | 0
90330004 | Breakers > Shaft generator breaker > Command | Zero pitch | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Shaft generator breaker > Feedback | SGB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Shaft generator breaker > Feedback | SGB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Shaft generator breaker > Feedback | SGB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Shaft generator breaker > Feedback | SGB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130003 | Power management | Block blackout start | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
90130005 | Power management | Block load-dependent stop | DI |  | BOOL_NUM | 0 | 1 | 0
90130006 | Power management | Deactivate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130007 | Power management | Activate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130009 | Power management | Force all controllers in section to SWBD control | DI |  | BOOL_NUM | 0 | 1 | 0
90130010 | Power management | Force all gensets in section to MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
90130011 | Power management | Force all gensets in section to AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90130015 | Power management | Precautionary genset start | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Generator > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Generator > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Shaft generator breaker > Controls | SGB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Shaft generator breaker > Controls | SGB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Shaft generator breaker > Controls | SGB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Shaft generator breaker > State | SGB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Shaft generator breaker > State | SGB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Shaft generator breaker > State | SGB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Shaft generator breaker > State | SGB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Shaft generator breaker > State | SGB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled open breaker alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any SGB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any SGB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
126219000 | Load reduction | Load reduction output 1 | DO |  | BOOL_NUM | 0 | 1 | 0
126229000 | Load reduction | Load reduction output 2 | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40150060 | Generator > Frequency (f) - ACM3.2 | Generator ¦ Frequency | AO | Hz | FLOAT | 0 | 1500000 | 1
40150000 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150001 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150002 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150003 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150004 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Consumer side) | AO | A | FLOAT | 0 | 1500000 | 1
40150025 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150026 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150027 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150028 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150029 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. (Neutral side) | AO | A | FLOAT | 0 | 1500000 | 1
40150050 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150051 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150052 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 differential | AO | A | FLOAT | 0 | 1500000 | 1
40150053 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150054 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. differential | AO | A | FLOAT | 0 | 1500000 | 1
40150055 | Generator > Current (I) - ACM3.2 | Generator ¦ L1 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150056 | Generator > Current (I) - ACM3.2 | Generator ¦ L2 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150057 | Generator > Current (I) - ACM3.2 | Generator ¦ L3 restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150058 | Generator > Current (I) - ACM3.2 | Generator ¦ Min. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40150059 | Generator > Current (I) - ACM3.2 | Generator ¦ Max. restraint | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## SHORE connection parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
Shore connection > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Shore connection > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Shore connection > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Shore connection > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Shore connection > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Shore connection > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Shore connection > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Shore connection > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Shore connection > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Shore connection > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Shore connection > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Shore connection > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Shore connection > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Shore connection > AC setup > Phase sequence error | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Shore connection > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Shore connection > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Shore connection > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Shore connection > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Shore connection > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Shore connection > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Shore connection > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Shore connection > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Shore connection > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Shore connection > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Shore connection > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Shore connection > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Shore connection > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Shore connection > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Shore connection > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Shore connection > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Shore connection > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Shore connection > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Shore connection > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Shore connection > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Shore connection > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Shore connection > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Shore connection > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Shore connection > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Shore connection > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Shore connection > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Shore connection > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Shore connection > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Shore connection > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Shore connection > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Shore connection > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Shore connection > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Shore connection > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Shore connection > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Shore connection > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Shore connection > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Shore connection > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Shore connection > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Over-voltage 1 | Inhibit |  | Shore connection breaker closed
Shore connection > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Shore connection > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Over-voltage 2 | Inhibit |  | Shore connection breaker closed
Shore connection > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Shore connection > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Over-voltage 3 | Inhibit |  | Shore connection breaker closed
Shore connection > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Shore connection > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Under-voltage 1 | Inhibit |  | Shore connection breaker closed, No shore voltage
Shore connection > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Shore connection > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Under-voltage 2 | Inhibit |  | Shore connection breaker closed, No shore voltage
Shore connection > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Shore connection > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Shore connection > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Shore connection > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Under-voltage 3 | Inhibit |  | Shore connection breaker closed, No shore voltage
Shore connection > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Shore connection > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Shore connection > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Shore connection > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Shore connection > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Shore connection > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Shore connection > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Shore connection > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Shore connection > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Shore connection > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Shore connection > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Shore connection > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Shore connection > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Shore connection > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Shore connection > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Shore connection > Current protections > Over-current 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Shore connection > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Shore connection > Current protections > Fast over-current 1 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Shore connection > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Shore connection > Current protections > Fast over-current 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Shore connection > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Shore connection > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Shore connection > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Shore connection > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Shore connection > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Shore connection > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Shore connection > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Shore connection > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Shore connection > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Shore connection > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Shore connection > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Shore connection > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Shore connection > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Shore connection > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Shore connection > Current protections > Inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Shore connection > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Frequency protections > Over-frequency 1 | Inhibit |  | Shore connection breaker closed
Shore connection > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Shore connection > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Shore connection > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Frequency protections > Over-frequency 2 | Inhibit |  | Shore connection breaker closed
Shore connection > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Shore connection > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Frequency protections > Under-frequency 1 | Inhibit |  | Shore connection breaker closed, No shore voltage
Shore connection > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Shore connection > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Shore connection > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Frequency protections > Under-frequency 2 | Inhibit |  | Shore connection breaker closed, No shore voltage
Shore connection > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Shore connection > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Shore connection > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Shore connection > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Shore connection > Power protections > Overload 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Shore connection > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Shore connection > Power protections > Overload 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
Shore connection > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Power protections > Reverse power 1 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Power protections > Reverse power 1 | Inhibit |  | Ship-to-ship active
Shore connection > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
Shore connection > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Shore connection > Power protections > Reverse power 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Power protections > Reverse power 2 | Inhibit |  | Ship-to-ship active
Shore connection > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Shore connection > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Shore connection > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Shore connection > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Shore connection > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Shore connection > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Reactive power protections > Reactive power import 1 | Inhibit |  | Ship-to-ship active
Shore connection > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
Shore connection > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Shore connection > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Shore connection > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Shore connection > Reactive power protections > Reactive power import 2 | Inhibit |  | Ship-to-ship active
Shore connection > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Shore connection > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Shore connection > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Shore connection > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Shore connection > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Shore connection > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Shore connection > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Shore connection > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Shore connection breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Shore connection breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Shore connection breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Shore connection breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Shore connection breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Shore connection breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Shore connection breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Shore connection breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Shore connection breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Shore connection breaker open, ACM wire break
Breakers > Shore breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Shore breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Shore breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Shore breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Shore breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Shore breaker configuration > Configuration | Overlap | INT32 | 0 |  | 0 | 1 | 0
Breakers > Shore breaker configuration > Configuration | Breaker action | INT32 | Open shore connection breaker |  |  |  |  | 0: Open shore connection breaker, 1: Open without de-loading, 2: Operator select
Breakers > Shore breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Shore breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Shore breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Shore breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Shore breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shore breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Shore breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Shore breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Shore breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Shore breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Shore breaker monitoring > Synchronisation failure | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Shore breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Shore breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Shore breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Shore breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Shore breaker monitoring > Closing failure | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Shore breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Shore breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > Shore breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > Shore breaker monitoring > Short circuit | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Parallel timers > SC-DG max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > SC-DG max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Parallel timers > SC-Hybrid max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
Local power management > Parallel timers > SC-Hybrid max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Parallel timers > SC-SG max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
Local power management > Parallel timers > SC-SG max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Parallel timers > SC-SC max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
Local power management > Parallel timers > SC-SC max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
Local power management > Shore connection base load > Enable | Base load | INT32 | 0 |  | 0 | 1 | 0
Local power management > Shore connection base load > Power set point | Set point | FLOAT | 90 | % | 10 | 120 | 0
Local power management > Shore connection base load > Min. set point | Minimum limit | FLOAT | 5 | % | 1 | 100 | 0
Local power management > Shore connection base load > Max. set point | Maximum limit | FLOAT | 95 | % | 1 | 120 | 0
Local power management > Shore connection ship-to-ship > Open point | Open point enabled | INT32 | 0 |  | 0 | 1 | 0
Local power management > Shore connection ship-to-ship > Open point | Open when power below | FLOAT | 5 | % | 2 | 100 | 0
Local power management > Shore connection ship-to-ship > Connect load | Ship-to-ship connect load | FLOAT | 100 | kW | 1 | 900000 | 0
Local power management > Shore connection close load > Shore connection breaker | Minimum load on ship busbar | FLOAT | 5 | % | 0 | 100 | 1
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker

## SHORE connection IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
20180028 | Breakers > Shore connection breaker > Command | SCB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Shore connection breaker > Command | SCB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Shore connection breaker > Command | Block SCB close | DI |  | BOOL_NUM | 0 | 1 | 0
90430005 | Breakers > Shore connection breaker > Command | SCB action open | DI |  | BOOL_NUM | 0 | 1 | 0
90430006 | Breakers > Shore connection breaker > Command | SCB action open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Shore connection breaker > Feedback | SCB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Shore connection breaker > Feedback | SCB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Shore connection breaker > Feedback | SCB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Shore connection breaker > Feedback | SCB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130003 | Power management | Block blackout start | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
90130005 | Power management | Block load-dependent stop | DI |  | BOOL_NUM | 0 | 1 | 0
90130006 | Power management | Deactivate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130007 | Power management | Activate secured mode | DI |  | BOOL_NUM | 0 | 1 | 0
90130009 | Power management | Force all controllers in section to SWBD control | DI |  | BOOL_NUM | 0 | 1 | 0
90130010 | Power management | Force all gensets in section to MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
90130011 | Power management | Force all gensets in section to AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
90130015 | Power management | Precautionary genset start | DI |  | BOOL_NUM | 0 | 1 | 0
90430000 | Power management | Ship-to-ship supply | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
40219000 | Shore connection > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Shore connection > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Shore connection > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Shore connection > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Shore connection > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Shore connection > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Shore connection breaker > Controls | SCB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Shore connection breaker > Controls | SCB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Shore connection breaker > Controls | SCB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Shore connection breaker > State | SCB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Shore connection breaker > State | SCB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Shore connection breaker > State | SCB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Shore connection breaker > State | SCB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Shore connection breaker > State | SCB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled open breaker alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any SCB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
126219000 | Load reduction | Load reduction output 1 | DO |  | BOOL_NUM | 0 | 1 | 0
126229000 | Load reduction | Load reduction output 2 | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Shore connection > Voltage (V) | Shore ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Shore connection > Voltage (V) | Shore ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Shore connection > Voltage (V) | Shore ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Shore connection > Voltage (V) | Shore ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Shore connection > Voltage (V) | Shore ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Shore connection > Voltage (V) | Shore ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Shore connection > Voltage (V) | Shore ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Shore connection > Voltage (V) | Shore ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Shore connection > Voltage (V) | Shore ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Shore connection > Voltage (V) | Shore ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Shore connection > Voltage (V) | Shore ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Shore connection > Voltage (V) | Shore ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Shore connection > Voltage (V) | Shore ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Shore connection > Voltage (V) | Shore ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Shore connection > Voltage (V) | Shore ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Shore connection > Voltage (V) | Shore ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Shore connection > Frequency (f) (from voltage) | Shore ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Shore connection > Frequency (f) (from voltage) | Shore ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Shore connection > Frequency (f) (from voltage) | Shore ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Shore connection > Frequency (f) (from voltage) | Shore ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Shore connection > Frequency (f) (from voltage) | Shore ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Shore connection > Frequency (f) (from voltage) | Shore ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Shore connection > Frequency (f) (from current) | Shore ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Shore connection > Frequency (f) (from current) | Shore ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Shore connection > Frequency (f) (from current) | Shore ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Shore connection > Frequency (f) (from current) | Shore ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Shore connection > Frequency (f) (from current) | Shore ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Shore connection > Current (I) | Shore ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Shore connection > Current (I) | Shore ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Shore connection > Current (I) | Shore ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Shore connection > Current (I) | Shore ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Shore connection > Current (I) | Shore ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Shore connection > Current (I) | Shore ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Shore connection > Current (I) | Shore ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Shore connection > Current (I) | Shore ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Shore connection > Current (I) | Shore ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Shore connection > Current (I) | Shore ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Shore connection > Current (I) | Shore ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Shore connection > Power (P) | Shore ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Shore connection > Power (P) | Shore ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Shore connection > Power (P) | Shore ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Shore connection > Power (P) | Shore ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Shore connection > Power (P) | Shore ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Shore connection > Power (P) | Shore ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Shore connection > Power (P) | Shore ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Shore connection > Power (P) | Shore ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Shore connection > Power (P) | Shore ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Shore connection > Reactive power (Q) | Shore ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Shore connection > Reactive power (Q) | Shore ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Shore connection > Reactive power (Q) | Shore ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Shore connection > Reactive power (Q) | Shore ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Shore connection > Reactive power (Q) | Shore ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Shore connection > Reactive power (Q) | Shore ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Shore connection > Reactive power (Q) | Shore ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Shore connection > Reactive power (Q) | Shore ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Shore connection > Reactive power (Q) | Shore ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Shore connection > Apparent power (S) | Shore ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Shore connection > Apparent power (S) | Shore ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Shore connection > Apparent power (S) | Shore ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Shore connection > Apparent power (S) | Shore ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Shore connection > Apparent power (S) | Shore ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Shore connection > Apparent power (S) | Shore ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Shore connection > Apparent power (S) | Shore ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Shore connection > Apparent power (S) | Shore ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Shore connection > Apparent power (S) | Shore ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Shore connection > Power factor (PF) | Shore ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Shore connection > Power factor (PF) | Shore ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Shore connection > Phase angle | Shore ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Shore connection > Phase angle | Shore ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Shore connection > Phase angle | Shore ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Shore connection > Phase angle | Shore ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Shore connection > Phase angle | Shore ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Shore connection > Phase angle | Shore ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## BUS TIE breaker parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -1212.47 | 1212.47 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
Local power management > Bus tie breaker > Supply mode after BTB close | Supply mode after connecting | INT32 | Stay on DG supply |  |  |  |  | 0: Stay on DG supply, 2: Stay on SG/SC supply
Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99.5 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 100.5 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99.5 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 100.5 | % | 90 | 110 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Overload on a DG | Set point | FLOAT | 120 | % | 70 | 250 | 1
Local power management > Advanced blackout prevention > Overload on a DG | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Overload on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Reverse power on a DG | Set point | FLOAT | -5 | % | -25 | -0.1 | 1
Local power management > Advanced blackout prevention > Reverse power on a DG | Delay | FLOAT | 3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Reverse power on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Reactive power export on a DG | Set point | FLOAT | 120 | % | 0.1 | 250 | 1
Local power management > Advanced blackout prevention > Reactive power export on a DG | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Reactive power export on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Reactive power import on a DG | Set point | FLOAT | -100 | % | -120 | -0.1 | 1
Local power management > Advanced blackout prevention > Reactive power import on a DG | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Reactive power import on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local power management > Advanced blackout prevention > Over-current on a DG | Set point | FLOAT | 200 | % | 70 | 250 | 1
Local power management > Advanced blackout prevention > Over-current on a DG | Delay | FLOAT | 0.3 | s | 0 | 3600 | 1
Local power management > Advanced blackout prevention > Over-current on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > EIM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
Hardware > EIM3.1 1 > Relay 4 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > EIM3.1 1 > Relay 4 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker

## BUS TIE breaker IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
90530003 | Additional functions > Supply mode | Stay on DG supply after BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
90530004 | Additional functions > Supply mode | Stay on SG/SC supply after BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
90020000 | Local > Mode | Switchboard control | DI |  | BOOL_NUM | 0 | 1 | 0
90020007 | Local > Mode | PMS control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
90130004 | Power management | Acknowledge all alarms in system | DI |  | BOOL_NUM | 0 | 1 | 0
110500100 | Power management | Deactivate selected power management rule | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500110 | Power management | Activate power management rule 1 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500120 | Power management | Activate power management rule 2 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500130 | Power management | Activate power management rule 3 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500140 | Power management | Activate power management rule 4 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500150 | Power management | Activate power management rule 5 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500160 | Power management | Activate power management rule 6 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500170 | Power management | Activate power management rule 7 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110500180 | Power management | Activate power management rule 8 | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120080002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120180002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120280002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120380002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120480002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580000 | Heavy consumers > [User defined] | Request | DI |  | BOOL_NUM | 0 | 1 | 0 | X
120580002 | Heavy consumers > [User defined] | Feedback | DI |  | BOOL_NUM | 0 | 1 | 0 | X
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Bus tie breaker > Controls | BTB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled open breaker alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90020005 | Local > Mode | Under switchboard control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
110100111 | Power management | Secured mode active in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100112 | Power management | Precautionary genset start in section | DO |  | BOOL_NUM | 0 | 1 | 0
110100115 | Power management | Load-dependent start timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110100116 | Power management | Load-dependent stop timer running | DO |  | BOOL_NUM | 0 | 1 | 0
110500210 | Power management | Power management rule 1 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500220 | Power management | Power management rule 2 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500230 | Power management | Power management rule 3 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500240 | Power management | Power management rule 4 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500250 | Power management | Power management rule 5 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500260 | Power management | Power management rule 6 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500270 | Power management | Power management rule 7 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110500280 | Power management | Power management rule 8 active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120080001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120180001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120280001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120380001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120480001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
120580001 | Heavy consumers > [User defined] | Acknowledge | DO |  | BOOL_NUM | 0 | 1 | 0 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
120080003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120180003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120280003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120380003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120480003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
120580003 | Heavy consumers > [User defined] | Feedback | AI | % | FLOAT | 0 | 100 | 0 | X
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | Power management | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100101 | Power management | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000 | 0
110100102 | Power management | Section ¦ PMS P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100103 | Power management | Section ¦ PMS P avail. | AO | % | FLOAT | -100 | 100 | 0
110100105 | Power management | Section ¦ PMS P used | AO | % | FLOAT | -100 | 100 | 0
110100106 | Power management | Section ¦ Conn. P avail. | AO | kW | FLOAT | 0 | 10000 | 0
110100107 | Power management | Section ¦ Conn. P used | AO | kW | FLOAT | 0 | 10000 | 0
110100108 | Power management | Section ¦ Conn. P nom. | AO | kW | FLOAT | 0 | 10000 | 0
110100109 | Power management | Section ¦ Conn. P avail. | AO | % | FLOAT | -100 | 100 | 0
110100110 | Power management | Section ¦ Conn. P used | AO | % | FLOAT | -100 | 100 | 0
110100114 | Power management | Number of feeders connected in PMS | AO |  | INT32 | 0 | 100 | 0
120080004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120080005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120180004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120180005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120280004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120280005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120380004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120380005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120480004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120480005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
120580004 | Heavy consumers > [User defined] | Load | AO | % | FLOAT | 0 | 100 | 0 | X
120580005 | Heavy consumers > [User defined] | Load | AO | kW | FLOAT | 0 | 9000000 | 0 | X
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
100049000 | Hardware > Power supply > EIM3.1 1 | EIM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1