## About
AGC 150 PMS lite parameter list
Software version
The information contained in this parameter list (Revision A) are applicable to software version 1.38.x of the AGC 150.
Controller types
This document includes the parameter lists for this controller type:
PMS lite controller
See the AGC 150 PMS lite Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the utility software, under Parameters.
Column names
Offset = The parameter address.
Channel = The parameter number.
Category = The selectable category in the parameter list.
Path = The path in the parameter tree.
Name = The name of the parameter.
Description = The parameter description. This is shown as mouseover text in the parameter list.
Default = The default value or selection for the parameter.
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Unit = The unit of measurement for the parameter value.*
Selections = The drop-down choices for the parameter.*
Timer default = The default value for the timer.*
Timer minimum = The minimum value for the timer.*
Timer maximum = The maximum value for the timer.*
RelayA name = The selection for relay A.*
RelayB name = The selection for relay B.*
Default alarm action = The default alarm action when the parameter(s) are for an alarm.
Notes
* Only included where relevant.
Some parameter attributes (for example, Inhibits, and Auto acknowledge) are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include ECU & D-AVR configuration, I/O & Hardware setup and Ethernet setting (TCP/IP). These are not included in the parameter lists.

## Parameters
Offset | Channel | Category | Path | Name | Description | Default | Minimum | Maximum | Unit | Selections | Timer default | Timer minimum | Timer maximum | RelayA name | RelayB name | Default alarm action
1 | 1000 | Protection | Generator > Power protections > Reverse power | -P> 1 | Reverse power protection level 1 (ANSI 32) | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip GB
2 | 1010 | Protection | Generator > Power protections > Reverse power | -P> 2 | Reverse power protection level 2 (ANSI 32) | -5 | -200 | 0 | % |  | 100 | 1 | 1000 |  |  | Trip GB
4 | 1030 | Protection | Generator > Current protections > Over-current | I> 1 | Overcurrent protection level 1 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000
5 | 1040 | Protection | Generator > Current protections > Over-current | I> 2 | Overcurrent protection level 2 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip GB
6 | 1050 | Protection | Generator > Current protections > Over-current | I> 3 | Overcurrent protection level 3 (ANSI 50) | 115 | 50 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip GB
7 | 1060 | Protection | Generator > Current protections > Over-current | I> 4 | Overcurrent protection level 4 (ANSI 50) | 120 | 50 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip GB
870 | 1070 | Protection | Generator > Power protections > Reverse power | -P> 3 | Reverse power protection level 3 (ANSI 32) | -5 | -200 | 30 | % |  | 1000 | 0 | 30000 |  |  | Trip GB
1251 | 1101 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (50%) | Voltage dependent overcurrent curve setting 1 | 110 | 50 | 200 | %
1252 | 1102 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (60%) | Voltage dependent overcurrent curve setting 2 | 125 | 50 | 200 | %
1253 | 1103 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (70%) | Voltage dependent overcurrent curve setting 3 | 140 | 50 | 200 | %
1254 | 1104 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (80%) | Voltage dependent overcurrent curve setting 4 | 155 | 50 | 200 | %
1255 | 1105 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (90%) | Voltage dependent overcurrent curve setting 5 | 170 | 50 | 200 | %
1256 | 1106 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> (100%) | Voltage dependent overcurrent curve setting 6 | 200 | 50 | 200 | %
9 | 1110 | Protection | Generator > Current protections > Voltage dependent over-current | G Iv> | Voltage dependent overcurrent protection (ANSI 50V) | [5 empty] | 10 | 1 | 100 |  |  | Trip GB
10 | 1130 | Protection | Generator > Current protections > Fast over-current | I>> 1 | Fast overcurrent protection level 1 (ANSI 50) | 150 | 150 | 300 | % |  | 20 | 0 | 32000 |  |  | Trip GB
11 | 1140 | Protection | Generator > Current protections > Fast over-current | I>> 2 | Fast overcurrent protection level 1 (ANSI 50) | 200 | 150 | 300 | % |  | 5 | 0 | 32000 |  |  | Trip GB
12 | 1150 | Protection | Generator > Voltage protections > Over-voltage | G U> 1 | Generator overvoltage protection level 1 (ANSI 59) | 103 | 100 | 130 | % |  | 100 | 1 | 1000
13 | 1160 | Protection | Generator > Voltage protections > Over-voltage | G U> 2 | Generator overvoltage protection level 2 (ANSI 59) | 105 | 100 | 130 | % |  | 50 | 1 | 1000
14 | 1170 | Protection | Generator > Voltage protections > Under-voltage | G U< 1 | Generator undervoltage protection level 1 (ANSI 27) | 97 | 40 | 100 | % |  | 100 | 1 | 1000
15 | 1180 | Protection | Generator > Voltage protections > Under-voltage | G U< 2 | Generator undervoltage protection level 2 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000
16 | 1190 | Protection | Generator > Voltage protections > Under-voltage | G U< 3 | Generator undervoltage protection level 3 (ANSI 27) | 95 | 40 | 100 | % |  | 50 | 1 | 1000
17 | 1201 | Protection | Generator > Voltage protections > Voltage detect. type | G U detect. type | Generator meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N | [5 empty] | Warning
31 | 1202 | Protection | Busbar > Voltage protections > Voltage detect. type | BB U detect. type | Busbar meassurement type phase-phase or phase-neutral | Ph-Ph |  |  |  | 0: Ph-Ph, 1: Ph-N | [5 empty] | Warning
1608 | 1203 | Protection | Generator > Current protections > Unbalance current | Unbalance I | Current unbalance calculation method | Ref. to nominal |  |  |  | 0: Ref. to nominal, 1: Ref. to average | [5 empty] | Warning
173 | 1204 | Protection | Generator > Frequency protections > Frequency detection type | Freq. detect. type | Frequency trip type selection for over- and underfrequency alarms. | L1 or L2 or L3 |  |  |  | 0: L1, 1: L2, 2: L3, 3: L1 or L2 or L3, 4: L1 and L2 and L3 | [5 empty] | Warning
18 | 1210 | Protection | Generator > Frequency protections > Over-frequency | G f> 1 | Generator overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 100 | 2 | 1000
19 | 1220 | Protection | Generator > Frequency protections > Over-frequency | G f> 2 | Generator overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000
20 | 1230 | Protection | Generator > Frequency protections > Over-frequency | G f> 3 | Generator overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 50 | 2 | 1000
21 | 1240 | Protection | Generator > Frequency protections > Under-frequency | G f< 1 | Generator underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 100 | 2 | 1000
22 | 1250 | Protection | Generator > Frequency protections > Under-frequency | G f< 2 | Generator underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000
23 | 1260 | Protection | Generator > Frequency protections > Under-frequency | G f< 3 | Generator underfrequency protection level 3 (ANSI 81) | 95 | 80 | 100 | % |  | 50 | 2 | 1000
24 | 1270 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 1 | Busbar overvoltage protection level 1 (ANSI 59) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999
25 | 1280 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 2 | Busbar overvoltage protection level 2 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999
26 | 1290 | Protection | Busbar > Voltage protections > Over-voltage | BB U> 3 | Busbar overvoltage protection level 3 (ANSI 59) | 105 | 100 | 120 | % |  | 500 | 4 | 9999
27 | 1300 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 1 | Busbar undervoltage protection level 1 (ANSI 27) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999
28 | 1310 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 2 | Busbar undervoltage protection level 2 (ANSI 27) | 95 | 40 | 100 | % |  | 500 | 4 | 9999
29 | 1320 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 3 | Busbar undervoltage protection level 3 (ANSI 27) | 97 | 40 | 100 | % |  | 1000 | 4 | 9999
30 | 1330 | Protection | Busbar > Voltage protections > Under-voltage | BB U< 4 | Busbar undervoltage protection level 4 (ANSI 27) | 95 | 40 | 100 | % |  | 500 | 4 | 9999
32 | 1350 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 1 | Busbar overfrequency protection level 1 (ANSI 81) | 103 | 100 | 120 | % |  | 1000 | 4 | 9999
33 | 1360 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 2 | Busbar overfrequency protection level 2 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999
34 | 1370 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 3 | Busbar overfrequency protection level 3 (ANSI 81) | 105 | 100 | 120 | % |  | 500 | 4 | 9999
35 | 1380 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 1 | Busbar underfrequency protection level 1 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999
36 | 1390 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 2 | Busbar underfrequency protection level 2 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999
37 | 1400 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 3 | Busbar underfrequency protection level 3 (ANSI 81) | 97 | 80 | 100 | % |  | 1000 | 4 | 9999
38 | 1410 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 4 | Busbar underfrequency protection level 4 (ANSI 81) | 95 | 80 | 100 | % |  | 500 | 4 | 9999
43 | 1450 | Protection | Generator > Power protections > Overload | P> 1 | Generator overload protection level 1 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000
44 | 1460 | Protection | Generator > Power protections > Overload | P> 2 | Generator overload protection level 2 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip GB
45 | 1470 | Protection | Generator > Power protections > Overload | P> 3 | Generator overload protection level 3 (ANSI 32) | 100 | -200 | 200 | % |  | 100 | 1 | 32000 |  |  | Trip GB
46 | 1480 | Protection | Generator > Power protections > Overload | P> 4 | Generator overload protection level 4 (ANSI 32) | 110 | -200 | 200 | % |  | 50 | 1 | 32000 |  |  | Trip GB
47 | 1490 | Protection | Generator > Power protections > Overload | P< 5 | Generator overload protection level 5 (ANSI 32) | 30 | -200 | 200 | % |  | 32000 | 1 | 32000 |  |  | Trip GB
48 | 1500 | Protection | Generator > Current protections > Unbalance current | Unbalance I 1 | Generator unbalanced current (ANSI 46) | 30 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip GB
49 | 1510 | Protection | Generator > Voltage protections > Voltage unbalance | G unbalance U | Generator unbalanced voltage (ANSI 47) | 10 | 0 | 50 | % |  | 100 | 1 | 1000 |  |  | Trip GB
50 | 1520 | Protection | Generator > Reactive power protections > Underexcitation | -Q> | Loss of excitation (ANSI 40) | 50 | 0 | 150 | % |  | 100 | 1 | 1000
51 | 1530 | Protection | Generator > Reactive power protections > Overexcitation | Q> | Overexcitation (ANSI 40) | 60 | 0 | 100 | % |  | 100 | 1 | 1000
873 | 1620 | Protection | Busbar > Voltage protections > Voltage unbalance | BB unbalance U | Busbar unbalanced voltage (ANSI 47) | 6 | 0 | 50 | % |  | 100 | 1 | 1000
58 | 1710 | Protection | Generator > Current protections > Unbalance current | Unbalance I 2 | Generator unbalanced current level 2 (ANSI 46) | 40 | 0 | 100 | % |  | 100 | 1 | 1000 |  |  | Trip GB
1494 | 1721 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Type | In> curve selection (IEC/IEEE inverse time overcurrent (ANSI 51)) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom | [5 empty] | Warning
1495 | 1722 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse Limit | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 30 | 2 | 120 | % | [6 empty] | Warning
1496 | 1723 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse TMS | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 1 | 0.01 | 100 | /100 | [6 empty] | Warning
1497 | 1724 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse k | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.14 | 0.001 | 32 | s | [6 empty] | Warning
1498 | 1725 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse c | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0 | 0 | 32 | s | [6 empty] | Warning
1499 | 1726 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse a | In> (IEC/IEEE inverse time overcurrent (ANSI 51)) | 0.02 | 0.001 | 32 | /1000 | [6 empty] | Warning
1500 | 1727 | Protection | Generator > Current protections > Neutral inverse time over-current (4th CT) | In> inverse | In> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip GB
1501 | 1731 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Type | Ie> curve selection (IEC/IEEE inverse time overcurrent) | IEC Inverse |  |  |  | 0: IEC Inverse, 1: IEC Very Inverse, 2: IEC Extremely Inv., 3: IEEE Moderately Inv., 4: IEEE Very Inverse, 5: IEEE Extremely Inv., 6: Custom | [5 empty] | Warning
1502 | 1732 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse Limit | Ie> (IEC/IEEE inverse time overcurrent) | 10 | 2 | 120 | % | [6 empty] | Warning
1503 | 1733 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse TMS | Ie> (IEC/IEEE inverse time overcurrent) | 1 | 0.01 | 100 | /100 | [6 empty] | Warning
1504 | 1734 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse k | Ie> (IEC/IEEE inverse time overcurrent) | 0.14 | 0.001 | 32 | s | [6 empty] | Warning
1505 | 1735 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse c | Ie> (IEC/IEEE inverse time overcurrent) | 0 | 0 | 32 | s | [6 empty] | Warning
1506 | 1736 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse a | Ie> (IEC/IEEE inverse time overcurrent) | 0.02 | 0.001 | 32 | /1000 | [6 empty] | Warning
1507 | 1737 | Protection | Generator > Current protections > Earth fault inverse time over-current (4th CT) | Ie> inverse | Ie> (IEC/IEEE inverse time overcurrent) | [10 empty] | Trip GB
859 | 1920 | Protection | Busbar > Frequency protections > Over-frequency | BB f> 4 | Busbar overfrequency protection level 4 (ANSI 81) | 102 | 100 | 120 | % |  | 5600 | 1500 | 6000
860 | 1930 | Protection | Busbar > Frequency protections > Under-frequency | BB f< 5 | Busbar underfrequency protection level 5 (ANSI 81) | 95 | 80 | 100 | % |  | 5600 | 1500 | 6000
1273 | 1981 | Protection | Breakers > Generator breaker > Breaker monitoring | GB Ext. tripped | Generator breaker externally tripped alarm
1274 | 1983 | Protection | Breakers > Mains breaker > Breaker monitoring | MB Ext. tripped | Mains Breaker externally tripped alarm
65 | 2021 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dfMax | Max. allowable frequency difference for Dynamic synchronisation | 0.3 | 0 | 0.5 | Hz | [6 empty] | Warning
66 | 2022 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dfMin | Min. allowable frequency difference for Dynamic synchronisation | 0 | -0.5 | 0.3 | Hz | [6 empty] | Warning
67 | 2023 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dUMax | Max. allowable voltage difference for Dynamic synchronisation | 5 | 2 | 10 | % | [6 empty] | Warning
1615 | 2024 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. dUMin | Max. allowable value the regulated voltage must be below voltage to sync to | -5 | -10 | 0 | % | [6 empty] | Warning
68 | 2025 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. time GB | Max. allowable breaker closing time for Dynamic synchronisation | 50 | 40 | 300 | ms | [6 empty] | Warning
69 | 2026 | Synchronisation | Synchronisation > Dynamic synchronisation | Sync. time MB | Max. allowable breaker closing time for Dynamic synchronisation | 50 | 40 | 300 | ms | [6 empty] | Warning
74 | 2041 | Synchronisation | Synchronisation > Synchronisation regulator | f sync. Kp (Gain ) | Proportional gain value of the PID controller for Dynamic synchronisation | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
75 | 2042 | Synchronisation | Synchronisation > Synchronisation regulator | f sync. Ti (Sta. ) | Integral time value of the PID controller for Dynamic synchronisation | 1.5 | 0 | 60 | s | [6 empty] | Warning
76 | 2043 | Synchronisation | Synchronisation > Synchronisation regulator | f sync. Td (Deri.) | Differential time value of the PID controller for Dynamic synchronisation | 0 | 0 | 2 | s | [6 empty] | Warning
77 | 2050 | Synchronisation | Synchronisation > Synchronisation regulator | f sync Kp relay(Ga.) | Proportional gain value of the controller for Dynamic synchronisation | 10 | 0 | 100 | [7 empty] | Warning
78 | 2061 | Synchronisation | Synchronisation > Static synchronisation > Static synchronisation regulator | Phase Kp(Gain) | Proportional gain value of the PID controller for Static synchronisation | 0.5 | 0 | 60 | /100 | [6 empty] | Warning
79 | 2062 | Synchronisation | Synchronisation > Static synchronisation > Static synchronisation regulator | Phase Ti(Stability) | Integral time value of the PID controller for Static synchronisation | 3 | 0 | 60 | s | [6 empty] | Warning
80 | 2063 | Synchronisation | Synchronisation > Static synchronisation > Static synchronisation regulator | Phase Td(Derivative) | Differential time value of the PID controller for Static synchronisation | 0 | 0 | 2 | s | [6 empty] | Warning
81 | 2070 | Synchronisation | Synchronisation > Static synchronisation > Static synchronisation regulator | Phase Kp relay(Gain) | Proportional gain value of the controller for Static synchronisation | 10 | 0 | 100 | [7 empty] | Warning
1307 | 2111 | Synchronisation | Generator > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f< | Max. allowable frequency difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz | [6 empty] | Warning
94 | 2112 | Synchronisation | Generator > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / f> | Max. allowable frequency difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 3 | 0 | 5 | Hz | [6 empty] | Warning
1308 | 2113 | Synchronisation | Generator > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U< | Max. allowable voltage difference from nominal setting BELOW nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | % | [6 empty] | Warning
95 | 2114 | Synchronisation | Generator > AC configuration > Voltage and frequency OK > Blackout / Hz/V OK | Blackout / U> | Max. allowable voltage difference from nominal setting ABOVE nominal for closing in case of blackout. This setting is also used to determine Hz/V OK | 5 | 2 | 20 | % | [6 empty] | Warning
97 | 2120 | Synchronisation | Synchronisation > Deadbus closing | Sync Window | Generator voltage and frequency limits for closing in case of blackout | 15 | 2 | 20 | % |  | 5 | 1 | 20 |  |  | Warning
98 | 2130 | Synchronisation | Synchronisation > Synchronisation failure > GB synchronisation failure | GB Sync failure | Max. allowable time for synchronisation of the generator breaker (alarm) | [5 empty] | 600 | 50 | 9999 |  |  | Block
99 | 2140 | Synchronisation | Synchronisation > Synchronisation failure > MB synchronisation failure | MB Sync failure | Max. allowable time for synchronisation of the connection breaker (alarm) | [5 empty] | 600 | 50 | 9999
100 | 2150 | Synchronisation | Generator > AC configuration > Phase sequence error | Phase seq error DG | Supervision of the rotation direction of the generator phases | [5 empty] | 10 | 10 | 10 |  |  | Block
1193 | 2154 | Synchronisation | Generator > AC configuration > Phase direction | Phase rotation | Expected direction of the phase rotation | L1L2L3 |  |  |  | 0: L1L2L3, 1: L1L3L2 | [5 empty] | Warning
1616 | 2155 | Synchronisation | Busbar > AC configuration > Phase sequence error | Phase seq error BB | Supervision of the rotation direction of the mains or busbar (depending on the plant configuration) phases | [5 empty] | 10 | 10 | 10 |  |  | Block
101 | 2160 | Synchronisation | Breakers > Generator breaker > Breaker monitoring | GB Open fail | Generator breaker open failure | [5 empty] | 20 | 10 | 100
102 | 2170 | Synchronisation | Breakers > Generator breaker > Breaker monitoring | GB Close fail | Generator breaker close failure | [5 empty] | 20 | 10 | 9000
103 | 2180 | Synchronisation | Breakers > Generator breaker > Breaker monitoring | GB Pos fail | Generator breaker position feedback failure | [5 empty] | 10 | 10 | 50
107 | 2200 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Open fail | Mains breaker open failure | [5 empty] | 20 | 10 | 100
108 | 2210 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Close fail | Mains breaker close failure | [5 empty] | 20 | 10 | 50
109 | 2220 | Synchronisation | Breakers > Mains breaker > Breaker monitoring | MB Pos fail | Mains breaker position feedback failure | [5 empty] | 10 | 10 | 50
110 | 2240 | Synchronisation | Synchronisation > Synchronisation failure > Separate synchronisation relay | Sep Sync relay | Additional synchronisation relay to be used in series with the primary synchronisation relay (GL demand). OutA = GB. OutB = MB. | [10 empty] | Warning
1712 | 2281 | Synchronisation | Synchronisation > Mains synchronisation inhibit | M sync. inh U | M sync. inh. low limit U | 85 | 80 | 100 | % | [6 empty] | Warning
1713 | 2282 | Synchronisation | Synchronisation > Mains synchronisation inhibit | M sync. inh U | M sync. inh. high limit U | 110 | 100 | 120 | % | [6 empty] | Warning
1714 | 2283 | Synchronisation | Synchronisation > Mains synchronisation inhibit | M sync. inh F | M sync. inh. low limit f | 95 | 90 | 100 | % | [6 empty] | Warning
1715 | 2284 | Synchronisation | Synchronisation > Mains synchronisation inhibit | M sync. inh F | M sync. inh. high limit f | 101 | 100 | 110 | % | [6 empty] | Warning
1716 | 2285 | Synchronisation | Synchronisation > Mains synchronisation inhibit | Mains sync inh | M sync. inh. failure | [10 empty] | Trip GB
1717 | 2291 | Synchronisation | Synchronisation > Mains synchronisation inhibit | Delay act. rec 2 | recovery selection timer | [5 empty] | 30 | 0 | 200 |  |  | Warning
1718 | 2292 | Synchronisation | Synchronisation > Mains synchronisation inhibit | Recovery delay 1 | recovery delay 1 | [5 empty] | 50 | 0 | 600 |  |  | Warning
1719 | 2294 | Synchronisation | Synchronisation > Mains synchronisation inhibit | Recovery delay 2 | recovery delay 2 | [5 empty] | 600 | 0 | 9000 |  |  | Warning
122 | 2511 | Regulation | Engine > Speed control > Speed PID > Island (analog/EIC) | f Kp (Gain) | Proportional gain value of the PID controller for frequency regulation | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
123 | 2512 | Regulation | Engine > Speed control > Speed PID > Island (analog/EIC) | f Ti (Stability) | Integral time value of the PID controller for frequency regulation | 1.5 | 0 | 60 | s | [6 empty] | Warning
124 | 2513 | Regulation | Engine > Speed control > Speed PID > Island (analog/EIC) | f Td (Derivative) | Differential time value of the PID controller for frequency regulation | 0 | 0 | 2 | s | [6 empty] | Warning
125 | 2514 | Regulation | Engine > Speed control > Speed PID > Island (analog/EIC) | f Droop | Frequency droop setting for Analogue regulation | 4 | 0 | 10 | % | [6 empty] | Warning
126 | 2531 | Regulation | Engine > Speed control > Speed PID > Mains parallel (analog/EIC) | P Kp (Gain) | Proportional gain value of the PID controller for power regulation | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
127 | 2532 | Regulation | Engine > Speed control > Speed PID > Mains parallel (analog/EIC) | P Ti (Stability) | Integral time value of the PID controller for power regulation | 1.5 | 0 | 60 | s | [6 empty] | Warning
128 | 2533 | Regulation | Engine > Speed control > Speed PID > Mains parallel (analog/EIC) | P Td (Derivative) | Differential time value of the PID controller for power regulation | 0 | 0 | 2 | s | [6 empty] | Warning
129 | 2541 | Regulation | Engine > Speed control > Speed PID > Load share (analog/EIC) | P loadsh. f Kp | Proportional gain value of the PID controller for load sharing | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
130 | 2542 | Regulation | Engine > Speed control > Speed PID > Load share (analog/EIC) | P loadsh. f Ti | Integral time value of the PID controller for load sharing | 1.5 | 0 | 60 | s | [6 empty] | Warning
131 | 2543 | Regulation | Engine > Speed control > Speed PID > Load share (analog/EIC) | P loadsh. f Td | Differential time value of the PID controller for load sharing | 0 | 0 | 2 | s | [6 empty] | Warning
132 | 2544 | Regulation | Engine > Speed control > Speed PID > Load share (analog/EIC) | P LS P weight | Weight factor of the power feedback of the PID controller for load sharing | 10 | 0 | 100 | % | [6 empty] | Warning
133 | 2551 | Regulation | Engine > Speed control > Offset for control signal | GOV output offset 1 | Offset of the analogue output used for governor regulation set point 1 | 50 | 0 | 100 | % | [6 empty] | Warning
1633 | 2552 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 2 > Offset control signals | GOV output offset 2 | Offset of the analogue output used for governor regulation set point 2 | 50 | 0 | 100 | % | [6 empty] | Warning
1634 | 2553 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 3 > Offset control signals | GOV output offset 3 | Offset of the analogue output used for governor regulation set point 3 | 50 | 0 | 100 | % | [6 empty] | Warning
1635 | 2554 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 4 > Offset control signals | GOV output offset 4 | Offset of the analogue output used for governor regulation set point 4 | 50 | 0 | 100 | % | [6 empty] | Warning
1513 | 2555 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 5 > Offset control signals | GOV output offset 5 | Offset of the analogue output used for governor regulation set point 5 | 50 | 0 | 100 | % | [6 empty] | Warning
1514 | 2556 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 6 > Offset control signals | GOV output offset 6 | Offset of the analogue output used for governor regulation set point 6 | 50 | 0 | 100 | % | [6 empty] | Warning
134 | 2560 | Regulation | Engine > Speed control > Regulation failure | GOV reg. fail | Supervision of the governor regulation | 30 | 1 | 100 | % |  | 600 | 100 | 3000
135 | 2571 | Regulation | Engine > Speed control > Speed PID > Island (relay) | f deadband | Deadband of the controller for frequency regulation | 1 | 0.2 | 10 | % | [6 empty] | Warning
136 | 2572 | Regulation | Engine > Speed control > Speed PID > Island (relay) | f Kp relay (Gain) | Proportional gain value of the controller for frequency regulation | 10 | 0 | 100 | [7 empty] | Warning
1375 | 2573 | Regulation | Engine > Speed control > Speed PID > Island (relay) | f Droop relay | Frequency droop setting for Relay regulation | 4 | 0 | 10 | % | [6 empty] | Warning
137 | 2581 | Regulation | Engine > Speed control > Speed PID > Mains parallel (relay) | P deadband | Deadband of the controller for frequency regulation | 2 | 0.2 | 10 | % | [6 empty] | Warning
138 | 2582 | Regulation | Engine > Speed control > Speed PID > Mains parallel (relay) | P Kp relay (Gain) | Proportional gain value of the controller for frequency regulation | 10 | 0 | 100 | [7 empty] | Warning
139 | 2591 | Regulation | Engine > Speed control > Speed PID > Load share (relay) | P LS f deadband | Deadband of the frequency regulation in load sharing | 1 | 0.2 | 10 | % | [6 empty] | Warning
140 | 2592 | Regulation | Engine > Speed control > Speed PID > Load share (relay) | P ls. f Kp rel. | Proportional gain value of the frequency control in load sharing | 10 | 0 | 100 | [7 empty] | Warning
141 | 2593 | Regulation | Engine > Speed control > Speed PID > Load share (relay) | P LS P deadband | Deadband of the power regulation in load sharing | 2 | 0.2 | 10 | % | [6 empty] | Warning
142 | 2594 | Regulation | Engine > Speed control > Speed PID > Load share (relay) | P LS P weight | Weight factor of the power in load sharing | 10 | 0 | 100 | % | [6 empty] | Warning
143 | 2601 | Regulation | Engine > Speed control > Relay configuration > Output and period | GOV ON time | The min. ON time of the relay outputs used for governor relay regulation | 500 | 10 | 6500 | ms | [6 empty] | Warning
144 | 2602 | Regulation | Engine > Speed control > Relay configuration > Output and period | GOV period time | The regulator period time used for governor relay regulation | 2500 | 250 | 32500 | ms | [6 empty] | Warning
146 | 2611 | Regulation | Power set points > Loading/Deloading ramps > kW ramp up speed | Power ramp up speed | Power ramp up speed 1 | 2 | 0.1 | 20 | %/s | [6 empty] | Warning
147 | 2612 | Regulation | Power set points > Loading/Deloading ramps > kW ramp up speed | Power ramp up setp. | Power ramp up delay point | 10 | 1 | 100 | % |  | 10 | 0 | 9900 |  |  | Warning
1282 | 2614 | Regulation | Power set points > Loading/Deloading ramps > kW ramp up speed | Island ramp | Activation of island ramp function | [10 empty] | Warning
1283 | 2615 | Regulation | Power set points > Loading/Deloading ramps > kW ramp up speed | Power ramp up steps | Power ramp up loads/steps | 1 | 0 | 100 | [7 empty] | Warning
451 | 2616 | Regulation | Power set points > Loading/Deloading ramps > kW ramp up speed | Power ramp up spe 2 | Power ramp up speed 2 | 0.1 | 0.1 | 20 | %/s | [6 empty] | Warning
148 | 2621 | Regulation | Power set points > Loading/Deloading ramps > kW ramp down speed | Power ramp down spee | Power ramp down speed 1 | 3.3 | 0.1 | 20 | %/s | [6 empty] | Warning
149 | 2622 | Regulation | Breakers > Generator breaker > Breaker configuration | Breaker open point | Max. allowable power when opening the breaker | 5 | 1 | 20 | % |  | 4 | 4 | 4 |  |  | Warning
145 | 2623 | Regulation | Power set points > Loading/Deloading ramps > Auto ramp select | Power ramp down spe2 | Power ramp down speed 2 (Only used for ramp down, not deload) (Enable to activate automatic ramp speed selection) | 0.1 | 0.1 | 20 | %/s | [6 empty] | Warning
150 | 2630 | Regulation | Power set points > Loading/Deloading ramps > Deload error | Deload error | Supervision of the deload sequence. Alarm is raised in case the ramp down speed is too low compared to the setting in menu 2621/2623 | [5 empty] | 100 | 0 | 600
151 | 2641 | Regulation | Generator > AVR > Voltage PID > Island (analog/EIC) | U Kp (Gain) | Proportional gain value of the PID controller for voltage regulation | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
152 | 2642 | Regulation | Generator > AVR > Voltage PID > Island (analog/EIC) | U Ti (Stability) | Integral time value of the PID controller for voltage regulation | 1.5 | 0 | 60 | s | [6 empty] | Warning
153 | 2643 | Regulation | Generator > AVR > Voltage PID > Island (analog/EIC) | U Td (Derivative) | Differential time value of the PID controller for voltage regulation | 0 | 0 | 2 | s | [6 empty] | Warning
1374 | 2644 | Regulation | Generator > AVR > Voltage PID > Island (analog/EIC) | U Droop | Voltage droop setting for Analogue regulation | 4 | 0 | 10 | % | [6 empty] | Warning
154 | 2651 | Regulation | Generator > AVR > Voltage PID > Mains parallel (analog/EIC) | Q Kp (Gain) | Proportional gain value of the PID controller for reactive power regulation | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
155 | 2652 | Regulation | Generator > AVR > Voltage PID > Mains parallel (analog/EIC) | Q Ti (Stability) | Integral time value of the PID controller for reactive power regulation | 1.5 | 0 | 60 | s | [6 empty] | Warning
156 | 2653 | Regulation | Generator > AVR > Voltage PID > Mains parallel (analog/EIC) | Q Td (Derivative) | Differential time value of the PID controller for reactive power regulation | 0 | 0 | 2 | s | [6 empty] | Warning
157 | 2661 | Regulation | Generator > AVR > Voltage PID > Load share (analog/EIC) | Q loadsh. U Kp(Gain) | Proportional gain value of the PID controller for reactive load sharing | 2.5 | 0 | 60 | /100 | [6 empty] | Warning
158 | 2662 | Regulation | Generator > AVR > Voltage PID > Load share (analog/EIC) | Q loadsh. U Ti | Integral time value of the PID controller for reactive load sharing | 1.5 | 0 | 60 | s | [6 empty] | Warning
159 | 2663 | Regulation | Generator > AVR > Voltage PID > Load share (analog/EIC) | Q loadsh. U Td | Differential time value of the PID controller for reactive load sharing | 0 | 0 | 2 | s | [6 empty] | Warning
160 | 2664 | Regulation | Generator > AVR > Voltage PID > Load share (analog/EIC) | Q LS Q weight | Weight factor of the power feedback of the PID controller for reactive load sharing | 10 | 0 | 100 | % | [6 empty] | Warning
161 | 2671 | Regulation | Generator > AVR > Offset for control signal | AVR output offset 1 | Offset of the analogue output used for AVR regulation set point 1 | 50 | 0 | 100 | % | [6 empty] | Warning
1636 | 2672 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 2 > Offset control signals | AVR output offset 2 | Offset of the analogue output used for AVR regulation set point 2 | 50 | 0 | 100 | % | [6 empty] | Warning
1637 | 2673 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 3 > Offset control signals | AVR output offset 3 | Offset of the analogue output used for AVR regulation set point 3 | 50 | 0 | 100 | % | [6 empty] | Warning
1638 | 2674 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 4 > Offset control signals | AVR output offset 4 | Offset of the analogue output used for AVR regulation set point 4 | 50 | 0 | 100 | % | [6 empty] | Warning
1515 | 2675 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 5 > Offset control signals | AVR output offset 5 | Offset of the analogue output used for AVR regulation set point 5 | 50 | 0 | 100 | % | [6 empty] | Warning
1516 | 2676 | Regulation | Alternative configuration > Generator nominal settings > Nominal settings 6 > Offset control signals | AVR output offset 6 | Offset of the analogue output used for AVR regulation set point 6 | 50 | 0 | 100 | % | [6 empty] | Warning
162 | 2680 | Regulation | Generator > AVR > Regulation failure | AVR reg. fail | Supervision of the AVR regulation | 30 | 1 | 100 | % |  | 600 | 100 | 3000
163 | 2691 | Regulation | Generator > AVR > Voltage PID > Island (relay) | U deadband | Deadband for the voltage regulation | 2 | 0 | 10 | % | [6 empty] | Warning
164 | 2692 | Regulation | Generator > AVR > Voltage PID > Island (relay) | U Kp relay (Gain) | Proportional gain value of the controller for voltage regulation | 10 | 0 | 100 | [7 empty] | Warning
1376 | 2693 | Regulation | Generator > AVR > Voltage PID > Island (relay) | U Droop relay | Voltage droop setting for Relay regulation | 4 | 0 | 10 | % | [6 empty] | Warning
165 | 2701 | Regulation | Generator > AVR > Voltage PID > Mains parallel (relay) | Q deadband | Deadband of the controller for reactive power regulation | 2 | 0 | 10 | % | [6 empty] | Warning
166 | 2702 | Regulation | Generator > AVR > Voltage PID > Mains parallel (relay) | Q Kp relay (Gain) | Proportional gain value for the reactive power regulation | 10 | 0 | 100 | [7 empty] | Warning
167 | 2711 | Regulation | Generator > AVR > Voltage PID > Load share (relay) | Q LS U deadband | Deadband of the voltage regulation in load sharing | 1 | 0 | 10 | % | [6 empty] | Warning
168 | 2712 | Regulation | Generator > AVR > Voltage PID > Load share (relay) | Q ls. U Kp rel. | Proportional gain value for the reactive load sharing | 10 | 0 | 100 | [7 empty] | Warning
169 | 2713 | Regulation | Generator > AVR > Voltage PID > Load share (relay) | Q LS Q deadband | Deadband of the reactive load sharing | 2 | 0 | 10 | % | [6 empty] | Warning
170 | 2714 | Regulation | Generator > AVR > Voltage PID > Load share (relay) | Q LS Q weight | Weight factor of the power for reactive load sharing | 10 | 0 | 100 | % | [6 empty] | Warning
171 | 2721 | Regulation | Generator > AVR > Relay configuration > Output and period | AVR ON time | Min. ON time of the relay outputs for AVR regulation | 100 | 10 | 3000 | ms | [6 empty] | Warning
172 | 2722 | Regulation | Generator > AVR > Relay configuration > Output and period | AVR period time | AVR duty cycle time | 500 | 50 | 15000 | ms | [6 empty] | Warning
178 | 2740 | Regulation | Engine > Start sequence > After crank > Regulator delay at start | Delay reg. | Delay of activating regulation after running feedback has been detected. | [5 empty] | 3 | 0 | 9900 |  |  | Warning
1303 | 2751 | Regulation | Engine > Speed control > Frequency recovery | Freq. recovery | Choose if the frequency recovery should be enabled and from what source. | Off |  |  |  | 0: Off, 1: Volvo Penta EMS 2.4, 2: Frequency measurement | [5 empty] | Warning
1304 | 2752 | Regulation | Engine > Speed control > Frequency recovery | Freq. recov lim | Only active when frequency recovery type is set to frequency measurement. Set a delta frequency below the nominal setting where if the frequency goes below, regulation is turned off, until frequency has been above the limit for the specified time at least. | 3 | 0 | 20 | Hz |  | 10 | 0 | 100 |  |  | Warning
180 | 2760 | Regulation | Mains > Overlap | Overlap | Maximum short time paralleling | Off |  |  |  | 0: Off, 1: On | 30 | 10 | 9990 |  |  | Warning
183 | 2781 | Regulation | Engine > Speed control > General configuration | Reg. output GOV | Selection of regulation output used for governor regulation | EIC |  |  |  | 0: Relay, 0: Relay, 0: Relay, 1: Analogue, 2: EIC | [5 empty] | Warning
184 | 2782 | Regulation | Generator > AVR > General configuration | Reg. output AVR | Selection of regulation output used for AVR regulation | Analogue |  |  |  | 0: Relay, 0: Relay, 0: Relay, 1: Analogue, 2: EIC, 2: EIC, 2: EIC | [5 empty] | Warning
1792 | 2783 | Regulation | Engine > Speed control > Manual step | Man. Step GOV | Length of the GOV up/down pulse | 5 | 0.1 | 10 | s | [6 empty] | Warning
1793 | 2784 | Regulation | Generator > AVR > Manual step | Man. Step AVR | Length of the AVR up/down pulse | 5 | 0.1 | 10 | s | [6 empty] | Warning
1611 | 2791 | Regulation | Engine > ECU configuration > Additional EIC features | Local Norm sw. pos | EIC Speed Demand switch setup: Local Normal switch position | Analogue CAN |  |  |  | 0: Analogue CAN, 1: Up/Down ECU, 2: Up/Down CAN, 3: Analogue ECU, 4: Analogue ECU relative, 5: Frequency | [5 empty] | Warning
1612 | 2792 | Regulation | Engine > ECU configuration > Additional EIC features | Local Emerg sw. pos | EIC Speed Demand switch setup: Local Emergency switch position | Analogue CAN |  |  |  | 0: Analogue CAN, 1: Up/Down ECU, 2: Up/Down CAN, 3: Analogue ECU, 4: Analogue ECU relative, 5: Frequency | [5 empty] | Warning
1613 | 2793 | Regulation | Engine > ECU configuration > Additional EIC features | Remote Norm sw. pos | EIC Speed Demand switch setup: Remote Normal switch position | Analogue CAN |  |  |  | 0: Analogue CAN, 1: Up/Down ECU, 2: Up/Down CAN, 3: Analogue ECU, 4: Analogue ECU relative, 5: Frequency | [5 empty] | Warning
1614 | 2794 | Regulation | Engine > ECU configuration > Additional EIC features | Remote Emerg sw. pos | EIC Speed Demand switch setup: Remote Emergency switch position | Analogue CAN |  |  |  | 0: Analogue CAN, 1: Up/Down ECU, 2: Up/Down CAN, 3: Analogue ECU, 4: Analogue ECU relative, 5: Frequency | [5 empty] | Warning
1609 | 2961 | Regulation | Engine > Start sequence > Warm up ramp | Warm up ramp type | Warm Up Ramp type (Selection of temperature measurement input) | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: MLogic, 5: EIC Cooling water/oil temp., 6: EIC Cooling water temp., 7: EIC Oil temp., 8: EIC Ambient temp., 9: EIC Intercool temp., 10: EIC Fuel temp., 19: CIO 308 1.08, 20: CIO 308 1.11, 21: CIO 308 1.14, 22: CIO 308 1.17, 23: CIO 308 1.20, 24: CIO 308 1.23, 25: CIO 308 1.26, 26: CIO 308 1.29, 27: CIO 308 2.08, 28: CIO 308 2.11, 29: CIO 308 2.14, 30: CIO 308 2.17, 31: CIO 308 2.20, 32: CIO 308 2.23, 33: CIO 308 2.26, 34: CIO 308 2.29, 35: CIO 308 3.08, 36: CIO 308 3.11, 37: CIO 308 3.14, 38: CIO 308 3.17, 39: CIO 308 3.20, 40: CIO 308 3.23, 41: CIO 308 3.26, 42: CIO 308 3.29 | [5 empty] | Warning
1610 | 2962 | Regulation | Engine > Start sequence > Warm up ramp | Warm up ramp thresh. | Warm Up Ramp threshold (set point of temperature measurement) | 0 | 0 | 482 | deg |  | 1 | 1 | 1 |  |  | Warning
1884 | 2971 | Regulation |  | GOV step test | GOV step test settings | 0 | -100 | 100 | % |  | 40 | 10 | 500 |  |  | Warning
1885 | 2972 | Regulation |  | GOV step test enable | GOV step test enable | OFF |  |  |  | 0: OFF, 1: ON | [5 empty] | Warning
1791 | 2973 | Regulation |  | AVR step test | AVR step test settings | 0 | -100 | 100 | % |  | 40 | 10 | 500 |  |  | Warning
1790 | 2974 | Regulation |  | AVR step test enable | AVR step test enable | OFF |  |  |  | 0: OFF, 1: ON | [5 empty] | Warning
236 | 3490 | Digital In | I/O settings > Inputs > Digital input | Emergency STOP | Setup of digital input for emergency stop (terminal 4) | [5 empty] | 0 | 0 | 600 |  |  | Shutdown
1722 | 3570 | Digital In | Functions > M-Logic alarms > M-Logic alarm 01 | M-Logic alarm 01 | M-Logic alarm 1 | [5 empty] | 100 | 0 | 32000
1723 | 3580 | Digital In | Functions > M-Logic alarms > M-Logic alarm 02 | M-Logic alarm 02 | M-Logic alarm 2 | [5 empty] | 100 | 0 | 32000
1724 | 3590 | Digital In | Functions > M-Logic alarms > M-Logic alarm 03 | M-Logic alarm 03 | M-Logic alarm 3 | [5 empty] | 100 | 0 | 32000
1725 | 3600 | Digital In | Functions > M-Logic alarms > M-Logic alarm 04 | M-Logic alarm 04 | M-Logic alarm 4 | [5 empty] | 100 | 0 | 32000
1726 | 3610 | Digital In | Functions > M-Logic alarms > M-Logic alarm 05 | M-Logic alarm 05 | M-Logic alarm 5 | [5 empty] | 100 | 0 | 32000
1824 | 3621 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Range selection for extended timer alarm 1 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset | [5 empty] | Warning
1828 | 3622 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 1 | M-Logic ext al 1 | Extended timer alarm 1 setup | 50 | 1 | 3200 | [7 empty] | Warning
1825 | 3631 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Range selection for extended timer alarm 2 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset | [5 empty] | Warning
1829 | 3632 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 2 | M-Logic ext al 2 | Extended timer alarm 2 setup | 50 | 1 | 3200 | [7 empty] | Warning
1826 | 3641 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Range selection for extended timer alarm 3 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset | [5 empty] | Warning
1830 | 3642 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 3 | M-Logic ext al 3 | Extended timer alarm 3 setup | 50 | 1 | 3200 | [7 empty] | Warning
1827 | 3651 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Range selection for extended timer alarm 4 | Minute(s) - auto reset |  |  |  | 0: Minute(s) - manual reset, 1: Hour(s) - manual reset, 2: Day(s) - manual reset, 3: Minute(s) - auto reset, 4: Hour(s) - auto reset, 5: Day(s) - auto reset | [5 empty] | Warning
1831 | 3652 | Digital In | Functions > M-Logic alarms > M-Logic ext alarm 4 | M-Logic ext al 4 | Extended timer alarm 4 setup | 50 | 1 | 3200 | [7 empty] | Warning
1853 | 3660 | Digital In | Functions > M-Logic alarms > M-Logic alarm 10 | M-Logic alarm 10 | M-Logic alarm 10 | [5 empty] | 100 | 0 | 32000
1854 | 3670 | Digital In | Functions > M-Logic alarms > M-Logic alarm 11 | M-Logic alarm 11 | M-Logic alarm 11 | [5 empty] | 100 | 0 | 32000
1855 | 3680 | Digital In | Functions > M-Logic alarms > M-Logic alarm 12 | M-Logic alarm 12 | M-Logic alarm 12 | [5 empty] | 100 | 0 | 32000
1856 | 3690 | Digital In | Functions > M-Logic alarms > M-Logic alarm 13 | M-Logic alarm 13 | M-Logic alarm 13 | [5 empty] | 100 | 0 | 32000
1857 | 3700 | Digital In | Functions > M-Logic alarms > M-Logic alarm 14 | M-Logic alarm 14 | M-Logic alarm 14 | [5 empty] | 100 | 0 | 32000
307 | 4510 | Analogue In | Engine > Protections > RPM - based protections > Overspeed | Overspeed 1 | Engine overspeed protection level 1 | 110 | 80 | 150 | % |  | 50 | 0 | 32000
308 | 4520 | Analogue In | Engine > Protections > RPM - based protections > Overspeed | Overspeed 2 | Engine overspeed protection level 2 | 120 | 80 | 150 | % |  | 10 | 0 | 32000 |  |  | Shutdown
309 | 4530 | Analogue In | Engine > Start sequence > Crank > Crank failure | Crank failure | Supervision of rpm during start sequence. Requires MPU selected to primary running feedback in menu 6172 | 50 | 1 | 400 | RPM |  | 20 | 0 | 200
310 | 4540 | Analogue In | Engine > Running detection > Running feedback fail | Run feedback fail | Supervision of primary running feedback selected in menu 6172 | [5 empty] | 20 | 0 | 200
945 | 4551 | Analogue In | Engine > Running detection > MPU wirebreak | MPU sensor type | MPU sensor type | Tacho sensor |  |  |  | 0: Tacho sensor, 1: Hall sensor | [5 empty] | Warning
311 | 4552 | Analogue In | Engine > Running detection > MPU wirebreak | MPU wirebreak | Wire break supervision of Magnetic Pick-Up (MPU) input | [5 empty] | 100 | 100 | 100
312 | 4560 | Analogue In | Generator > AC configuration > Voltage and frequency OK > Hz/V failure | Hz/V failure | Supervision of voltage and frequency when engine is running | [5 empty] | 300 | 10 | 990 |  |  | Shutdown
313 | 4570 | Analogue In | Engine > Start sequence > Crank > Start failure | Start failure | Number of start attempts has been exceeded. Max. allowable start attempts are set in menu 6191 | [10 empty] | Trip GB
314 | 4580 | Analogue In | Engine > Stop sequence > Stop failure | Stop failure | Max. allowable time for stopping the gen-set | [5 empty] | 300 | 100 | 1200 |  |  | Shutdown
1322 | 4590 | Analogue In | Engine > Protections > RPM - based protections > Underspeed | Underspeed | Engine underspeed protection level 1 | 90 | 50 | 120 | % |  | 50 | 0 | 32000
1482 | 4601 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpA | Input for A for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1483 | 4602 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 InpB | Input for B for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1484 | 4603 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpA | Input for A for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1485 | 4604 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 InpB | Input for B for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1486 | 4605 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpA | Input for A for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1487 | 4606 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 InpB | Input for B for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1488 | 4610 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 1 | Delta analogue alarm 1 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1489 | 4620 | Analogue In | Functions > Delta alarms > Set 1 | Delta ana1 2 | Delta analogue alarm 1 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1490 | 4630 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 1 | Delta analogue alarm 2 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1491 | 4640 | Analogue In | Functions > Delta alarms > Set 2 | Delta ana2 2 | Delta analogue alarm 2 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1492 | 4650 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 1 | Delta analogue alarm 3 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1493 | 4660 | Analogue In | Functions > Delta alarms > Set 3 | Delta ana3 2 | Delta analogue alarm 3 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1678 | 4671 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpA | Input for A for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1679 | 4672 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 InpB | Input for B for analogue delta (A-B) alarm 1 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1680 | 4673 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpA | Input for A for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1681 | 4674 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 InpB | Input for B for analogue delta (A-B) alarm 2 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1682 | 4675 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpA | Input for A for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1683 | 4676 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 InpB | Input for B for analogue delta (A-B) alarm 3 | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pres. (SPN 100), 21: EIC Cooling water temp. (SPN 110), 23: EIC Oil temp. (SPN 175), 24: EIC Ambient temp. (SPN 171), 25: EIC Intercool temp. (SPN 52), 26: EIC Fuel temp. (SPN 174), 27: EIC Fuel delivery pres. (SPN 94), 28: EIC Air filter1 diff. pres. (SPN 107), 29: EIC Air filter2 diff. pres. (SPN 2809), 30: EIC Fuel supply pump pres. (SPN 1381), 31: EIC Fuel filter diff. pres. SS (SPN 1382), 32: EIC Oil filter diff. pres. (SPN 99), 33: EIC T. Exhaust left (SPN 2434), 34: EIC T. Exhaust right (SPN 2433), 36: EIC Fuel filter diff. pres. (SPN 95), 37: EIC Percent load at current speed (SPN 92), 38: EIC T. Winding Highest, 39: EIC T. Winding Lowest, 60: EIC T. Winding 1, 61: EIC T. Winding 2, 62: EIC T. Winding 3, 63: EIC DEF Level (SPN 1761), 64: EIC DEF Temp (SPN 3031), 66: DEIF DVC 550 PT100_1, 67: DEIF DVC 550 PT100_2, 68: DEIF DVC 550 PT100_3, 69: DEIF DVC 550 PT100_4, 70: DEIF DVC 550 PT100_5, 71: EIC Speed (SPN 190), 72: MPU speed, 97: KWG ISO5 insulation resistance, 98: EIC Estimated Percent Fan Speed (SPN 975), 99: EIC Fan speed RPM (SPN 1639), 100: EIC Drivers demand engine - percent torque (SPN 512), 101: EIC Actual engine - percent torque (SPN 513), 113: EIC Crankcase pressure [kPa] (SPN 101), 114: EIC Engine oil level (SPN 98), 115: EIC Coolant Level (SPN 111), 116: EIC Boost Pressure (SPN 102), 117: EIC Charge Air Temperature (SPN 105), 118: EIC Fuel supply pump pres. 2 (YC-ECU-A), 119: EIC Fuel filter diff. pres. SS 2 (YC-ECU-A), 122: EIC Engine Filtered Fuel Delivery Pressure (SPN 5579), 123: EIC Coolant Pressure (SPN 109), 125: Configurable CAN RX-1, 126: Configurable CAN RX-2, 127: Configurable CAN RX-3, 128: Configurable CAN RX-4, 129: Configurable CAN RX-5, 130: Configurable CAN RX-6, 131: Configurable CAN RX-7, 132: Configurable CAN RX-8, 133: Configurable CAN RX-9, 134: Configurable CAN RX-10, 135: Configurable CAN RX-11, 136: Configurable CAN RX-12, 137: Configurable CAN RX-13, 138: Configurable CAN RX-14, 139: Configurable CAN RX-15, 140: Configurable CAN RX-16 | [5 empty] | Warning
1684 | 4680 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 1 | Delta analogue alarm 4 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1685 | 4690 | Analogue In | Functions > Delta alarms > Set 4 | Delta ana4 2 | Delta analogue alarm 4 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1686 | 4700 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 1 | Delta analogue alarm 5 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1687 | 4710 | Analogue In | Functions > Delta alarms > Set 5 | Delta ana5 2 | Delta analogue alarm 5 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1688 | 4720 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 1 | Delta analogue alarm 6 level 1 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
1689 | 4730 | Analogue In | Functions > Delta alarms > Set 6 | Delta ana6 2 | Delta analogue alarm 6 level 2 | 1 | -999.9 | 999.9 | /10 |  | 50 | 0 | 9990
315 | 4960 | Analogue In | Engine > Battery/Aux supply > Alarms | U< aux. term. 1 | Low supply voltage (terminals 1 and 2) | 18 | 8 | 32 | V |  | 10 | 0 | 9990
316 | 4970 | Analogue In | Engine > Battery/Aux supply > Alarms | U> aux. term. 1 | High supply voltage (terminals 1 and 2) | 30 | 12 | 36 | V |  | 10 | 0 | 9990
943 | 4990 | Analogue In | Engine > Running detection > Charger Gen fail | Charger Gen fail | Charger gen / D+ | 6 | 5.5 | 30 | V |  | 100 | 0 | 9990
245 | 5693 | Analogue Out | I/O settings > Outputs > Transducer > kW > P output current | P ref Output type | Active power reference transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
247 | 5713 | Analogue Out | I/O settings > Outputs > Transducer > Cos phi > Cos phi output current | Cos phi ref Outp typ | Cos phi reference transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
1262 | 5721 | Analogue Out | Engine > Speed control > Analogue configuration > PWM 52 setup | PWM 52 Limits | Pulse-width modulation terminal 52 - minimun value of span | 10 | 0 | 50 | % | [6 empty] | Warning
1263 | 5722 | Analogue Out | Engine > Speed control > Analogue configuration > PWM 52 setup | PWM 52 Limits | Pulse-width modulation terminal 52 - maximum value of span | 90 | 50 | 100 | % | [6 empty] | Warning
952 | 5723 | Analogue Out | Engine > Speed control > Analogue configuration > PWM 52 setup | PWM Out 52 Gov Type | Setup of PWM for governor type | Adjustable |  |  |  | 0: Adjustable, 1: Caterpillar: 6V / 500Hz | [5 empty] | Warning
941 | 5724 | Analogue Out | Engine > Speed control > Analogue configuration > PWM 52 setup | PWM amplitude | Set voltage amplitude for PWM 52 output | 5 | 1 | 10.5 | V | [6 empty] | Warning
942 | 5725 | Analogue Out | Engine > Speed control > Analogue configuration > PWM 52 setup | PWM frequency | Set frequency for PWM 52 output | 500 | 1 | 2500 | Hz | [6 empty] | Warning
953 | 5801 | Analogue Out | Engine > Speed control > Analogue configuration > AOUT 52 limits | AOUT 52 Gov Type | Setup of analog out 52 for governor type | Adjustable |  |  |  | 0: Adjustable, 1: Fixed Gov type: 1 to 5V | [5 empty] | Warning
352 | 5802 | Analogue Out | Engine > Speed control > Analogue configuration > AOUT 52 limits | AOUT 52 Limits | Minimum limit for analogue output 52 | -10 | -10.5 | 5 | V | [6 empty] | Warning
353 | 5803 | Analogue Out | Engine > Speed control > Analogue configuration > AOUT 52 limits | AOUT 52 Limits | Maximum limit for analogue output 52 | 10 | -5 | 10.5 | V | [6 empty] | Warning
954 | 5811 | Analogue Out | Generator > AVR > Analogue configuration > AOUT 55 Limits | AOUT 55 AVR Type | Setup of analog out 55 for AVR type | Adjustable |  |  |  | 0: Adjustable, 1: Fixed AVR type: 1 to 5V | [5 empty] | Warning
354 | 5812 | Analogue Out | Generator > AVR > Analogue configuration > AOUT 55 Limits | AOUT 55 Limits | Minimum limit for analogue output 55 | -10 | -10.5 | 5 | V | [6 empty] | Warning
355 | 5813 | Analogue Out | Generator > AVR > Analogue configuration > AOUT 55 Limits | AOUT 55 Limits | Maximum limit for analogue output 55 | 10 | -5 | 10.5 | V | [6 empty] | Warning
356 | 5823 | Analogue Out | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output type | Power transducer output type | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
391 | 5824 | Analogue Out | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output max | Transducer output maximum scale for generator active power 1 | 500 | 0 | 20000 | kW | [6 empty] | Warning
374 | 5825 | Analogue Out | I/O settings > Outputs > Transducer > kW > P output actual | P1 Output min | Transducer output minimum scale for generator active power 1 | 0 | -9999 | 20000 | kW | [6 empty] | Warning
359 | 5853 | Analogue Out | I/O settings > Outputs > Transducer > kVA | S Output type | Apparent power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
394 | 5854 | Analogue Out | I/O settings > Outputs > Transducer > kVA | S Output max | Transducer output maximum scale for generator apparent power | 600 | 0 | 20000 | kVA | [6 empty] | Warning
377 | 5855 | Analogue Out | I/O settings > Outputs > Transducer > kVA | S Output min | Transducer output minimum scale for generator apparent power | 0 | 0 | 20000 | kVA | [6 empty] | Warning
360 | 5863 | Analogue Out | I/O settings > Outputs > Transducer > kvar | Q Output type | Reactive power transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
395 | 5864 | Analogue Out | I/O settings > Outputs > Transducer > kvar | Q Output max | Transducer output maximum scale for generator reactive power | 400 | 0 | 16000 | kvar | [6 empty] | Warning
378 | 5865 | Analogue Out | I/O settings > Outputs > Transducer > kvar | Q Output min | Transducer output minimum scale for generator reactive power | 0 | -8000 | 16000 | kvar | [6 empty] | Warning
361 | 5873 | Analogue Out | I/O settings > Outputs > Transducer > Cos phi > Cos phi output | PF Output type | Power factor transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
396 | 5874 | Analogue Out | I/O settings > Outputs > Transducer > Cos phi > Cos phi output | PF Output max | Transducer output maximum scale for the power factor | 0.8 | 0.5 | 0.99 | PF | [6 empty] | Warning
379 | 5875 | Analogue Out | I/O settings > Outputs > Transducer > Cos phi > Cos phi output | PF Output min | Transducer output minimum scale for the power factor | -0.8 | -0.99 | -0.5 | PF | [6 empty] | Warning
362 | 5883 | Analogue Out | I/O settings > Outputs > Transducer > Generator Hz | f Output type | Generator frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
397 | 5884 | Analogue Out | I/O settings > Outputs > Transducer > Generator Hz | f Output max | Transducer output maximum scale for generator frequency | 55 | 0 | 70 | Hz | [6 empty] | Warning
380 | 5885 | Analogue Out | I/O settings > Outputs > Transducer > Generator Hz | f Output min | Transducer output minimum scale for generator frequency | 45 | 0 | 70 | Hz | [6 empty] | Warning
363 | 5893 | Analogue Out | I/O settings > Outputs > Transducer > Generator voltage | U Output type | Generator voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
398 | 5894 | Analogue Out | I/O settings > Outputs > Transducer > Generator voltage | U Output max | Transducer output maximum scale for generator voltage | 500 | 0 | 28000 | V | [6 empty] | Warning
381 | 5895 | Analogue Out | I/O settings > Outputs > Transducer > Generator voltage | U Output min | Transducer output minimum scale for generator voltage | 0 | 0 | 28000 | V | [6 empty] | Warning
364 | 5903 | Analogue Out | I/O settings > Outputs > Transducer > Ampere | I Output type | Current transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
399 | 5904 | Analogue Out | I/O settings > Outputs > Transducer > Ampere | I Output max | Transducer output maximum scale for current | 1000 | 0 | 9000 | A | [6 empty] | Warning
382 | 5905 | Analogue Out | I/O settings > Outputs > Transducer > Ampere | I Output min | Transducer output minimum scale for current | 0 | 0 | 9000 | A | [6 empty] | Warning
365 | 5913 | Analogue Out | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output type | Busbar voltage transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
400 | 5914 | Analogue Out | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output max | Transducer output maximum scale for busbar voltage | 500 | 0 | 28000 | V | [6 empty] | Warning
383 | 5915 | Analogue Out | I/O settings > Outputs > Transducer > Busbar voltage | U BB Output min | Transducer output minimum scale for busbar voltage | 0 | 0 | 28000 | V | [6 empty] | Warning
366 | 5923 | Analogue Out | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output type | Busbar frequency transducer output signal | Disabled |  |  |  | 0: Disabled, 4: -10 to 10V | [5 empty] | Warning
401 | 5924 | Analogue Out | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output max | Transducer output maximum scale for busbar frequency | 55 | 0 | 70 | Hz | [6 empty] | Warning
384 | 5925 | Analogue Out | I/O settings > Outputs > Transducer > Busbar Hz | f BB Output min | Transducer output minimum scale for busbar frequency | 45 | 0 | 70 | Hz | [6 empty] | Warning
372 | 5981 | Analogue Out | Engine > Speed control > Analogue configuration | Governor output | Transducer selection number in case of analogue output for the speed governor | [8 empty] | Terminal 5 |  | Warning
373 | 5991 | Analogue Out | Generator > AVR > Analogue configuration | AVR output | Transducer selection number in case of analogue output for the voltage regulator | [8 empty] | Terminal 6 |  | Warning
407 | 6001 | General | Basic settings > Nominal settings > Frequency | Nom. f 1 | Nominal generator frequency set point 1 | 50 | 48 | 62 | Hz | [6 empty] | Warning
408 | 6002 | General | Basic settings > Nominal settings > Power > 3 phase nominal | Nom. P 1 | Nominal generator power set point 1 | 480 | 10 | 20000 | kW | [6 empty] | Warning
409 | 6003 | General | Basic settings > Nominal settings > Current > 3 phase nominal | Nom. I 1 | Nominal generator current set point 1 | 867 | 0 | 9000 | A | [6 empty] | Warning
410 | 6004 | General | Basic settings > Nominal settings > Voltage > Generator nominal U | Nom. U 1 | Nominal generator voltage set point 1 | 400 | 100 | 25000 | V | [6 empty] | Warning
411 | 6005 | General | Basic settings > Nominal settings > RPM | Nom. RPM 1 | Nominal generator rpm set point 1 | 1500 | 100 | 4000 | RPM | [6 empty] | Warning
412 | 6006 | General | Alternative configuration > Generator nominal settings > Nominal set selection | Enable nom. set | Selection of nominal setting to be used | Nominal setting 1 |  |  |  | 0: Nominal setting 1, 1: Nominal setting 2, 2: Nominal setting 3, 3: Nominal setting 4, 4: Nominal setting 5, 5: Nominal setting 6 | [5 empty] | Warning
1460 | 6007 | General | Basic settings > Nominal settings > Current > 4th CT nominal | Nom. I E/N/M 1 | Nom I E/N/M 1 (Nominal current Earth/Neutral/Mains set point 1) | 867 | 0 | 9000 | A | [6 empty] | Warning
413 | 6011 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. f 2 | Nominal generator frequency set point 2 | 50 | 48 | 62 | Hz | [6 empty] | Warning
414 | 6012 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. P 2 | Nominal generator power set point 2 | 230 | 10 | 20000 | kW | [6 empty] | Warning
415 | 6013 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. I 2 | Nominal generator current set point 2 | 345 | 0 | 9000 | A | [6 empty] | Warning
416 | 6014 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. U 2 | Nominal generator voltage set point 2 | 480 | 100 | 25000 | V | [6 empty] | Warning
417 | 6015 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. RPM 2 | Nominal generator rpm set point 2 | 1500 | 100 | 4000 | RPM | [6 empty] | Warning
1461 | 6016 | General | Alternative configuration > Generator nominal settings > Nominal settings 2 > Basic settings | Nom. I E/N/M 2 | Nom I E/N/M 2 (Nominal current Earth/Neutral/Mains set point 2) | 867 | 0 | 9000 | A | [6 empty] | Warning
1229 | 6017 | General | Alternative configuration > Block nominal change | Block nom chang | Block nominal parameter, nominal set selection, when engine is running | Off |  |  |  | 0: Off, 1: On | [5 empty] | Warning
418 | 6021 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. f 3 | Nominal generator frequency set point 3 | 60 | 48 | 62 | Hz | [6 empty] | Warning
419 | 6022 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. P 3 | Nominal generator power set point 3 | 230 | 10 | 20000 | kW | [6 empty] | Warning
420 | 6023 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. I 3 | Nominal generator current set point 3 | 345 | 0 | 9000 | A | [6 empty] | Warning
421 | 6024 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. U 3 | Nominal generator voltage set point 3 | 480 | 100 | 25000 | V | [6 empty] | Warning
422 | 6025 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. RPM 3 | Nominal generator rpm set point 3 | 1800 | 100 | 4000 | RPM | [6 empty] | Warning
1462 | 6026 | General | Alternative configuration > Generator nominal settings > Nominal settings 3 > Basic settings | Nom. I E/N/M 3 | Nom I E/N/M 3 (Nominal current Earth/Neutral/Mains set point 3) | 867 | 0 | 9000 | A | [6 empty] | Warning
423 | 6031 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. f 4 | Nominal generator frequency set point 4 | 60 | 48 | 62 | Hz | [6 empty] | Warning
424 | 6032 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. P 4 | Nominal generator power set point 4 | 230 | 10 | 20000 | kW | [6 empty] | Warning
425 | 6033 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. I 4 | Nominal generator current set point 4 | 345 | 0 | 9000 | A | [6 empty] | Warning
426 | 6034 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. U 4 | Nominal generator voltage set point 4 | 480 | 100 | 25000 | V | [6 empty] | Warning
427 | 6035 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. RPM 4 | Nominal generator rpm set point 4 | 1800 | 100 | 4000 | RPM | [6 empty] | Warning
1463 | 6036 | General | Alternative configuration > Generator nominal settings > Nominal settings 4 > Basic settings | Nom. I E/N/M 4 | Nom I E/N/M 4 (Nominal current Earth/Neutral/Mains set point 4) | 867 | 0 | 9000 | A | [6 empty] | Warning
428 | 6041 | General | Basic settings > Measurement setup > Voltage transformer > Generator VT | G primary U | Generator voltage transformer value primary side | 400 | 100 | 25000 | V | [6 empty] | Warning
429 | 6042 | General | Basic settings > Measurement setup > Voltage transformer > Generator VT | G secondary U | Generator voltage transformer value secondary side | 400 | 100 | 690 | V | [6 empty] | Warning
430 | 6043 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | G primary I | Generator current transformer value primary side | 1000 | 5 | 9000 | A | [6 empty] | Warning
431 | 6044 | General | Basic settings > Measurement setup > Current transformer > 3 phase CT | G secondary I | Generator current transformer value secondary side | 1A |  |  |  | 1: 1A, 5: 5A | [5 empty] | Warning
1383 | 6045 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M primary I | E/N/M Primary I (Earth/Neutral/Mains current transformer value Primary side) | 1000 | 5 | 9000 | A | [6 empty] | Warning
1384 | 6046 | General | Basic settings > Measurement setup > Current transformer > 4th CT | E/N/M secondary I | E/N/M Secondary I (Earth/Neutral/Mains current transformer value secondary side) | 1A |  |  |  | 1: 1A, 5: 5A | [5 empty] | Warning
432 | 6051 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB primary U 1 | Busbar voltage transformer value primary side set point 1 | 400 | 100 | 25000 | V | [6 empty] | Warning
433 | 6052 | General | Basic settings > Measurement setup > Voltage transformer > Busbar VT | BB second. U 1 | Busbar voltage transformer value secondary side set point 1 | 400 | 100 | 690 | V | [6 empty] | Warning
1326 | 6053 | General | Basic settings > Nominal settings > Voltage > Busbar nominal U | BB nominal U 1 | Nominal busbar voltage set point 1 | 400 | 100 | 25000 | V | [6 empty] | Warning
1664 | 6055 | General | Basic settings > Nominal settings > Power > 4th CT nominal | 4th CT nom. P 1 | 4th CT Nominal power set point 1 | 480 | 10 | 9000 | kW | [6 empty] | Warning
435 | 6070 | General | Basic settings > Application type > Genset type > Genset/plant mode | Genset Mode | Generator running mode | Island operation |  |  |  | 0: Island operation, 1: Auto. Mains Failure, 2: Peak shaving, 3: Fixed Power, 4: Mains Power Export, 5: Load take over | [5 empty] | Warning
436 | 6081 | General | Basic settings > Controller settings > Language | Language | Language selection | English |  |  |  | 0: English, 1: Language 1, 2: Language 2, 3: Language 3, 4: Language 4, 5: Language 5, 6: Language 6, 7: Language 7, 8: Language 8, 9: Language 9, 10: Language 10, 11: Language 11 | [5 empty] | Warning
486 | 6082 | General | Basic settings > Controller settings > Display | LED mimic | Change LED mimic scheme | Standard with genset |  |  |  | 0: Standard with genset, 1: Standard, 2: Guided with genset, 3: Guided | [5 empty] | Warning
955 | 6083 | General | Basic settings > Controller settings > Display | National regulations | Setup of area specific or national specific rules | No rule |  |  |  | 0: No rule, 1: German V0108 | [5 empty] | Warning
485 | 6084 | General | Basic settings > Controller settings > Display | LED colors | Change LED color scheme | LED Color Scheme 1 |  |  |  | 0: LED Color Scheme 1, 1: LED Color Scheme 2 | [5 empty] | Warning
439 | 6101 | General |  | Running hours offset | Offset for running hours (0 to 999h) | 0 | 0 | 999 | Hours | [6 empty] | Warning
440 | 6102 | General |  | Running Th.h. offset | Offset for running hours (1000 to 999000h) | 0 | 0 | 99 | Hours | [6 empty] | Warning
437 | 6103 | General |  | GB Operations | Offset for generator breaker operations | 0 | 0 | 20000 | [7 empty] | Warning
438 | 6104 | General |  | MB operations | Offset mains breaker operations | 0 | 0 | 20000 | [7 empty] | Warning
441 | 6105 | General |  | Reset kWh counter | Reset of KWh counter | [10 empty] | Warning
442 | 6106 | General |  | Start attempts | Offset for start attempts | 0 | 0 | 20000 | [7 empty] | Warning
443 | 6111 | General | Engine > Maintenance > Service timer 1 | Service timer 1 hour | Setup of service timer 1 running hours | 500 | 0 | 9000 | [7 empty] | Warning
444 | 6113 | General | Engine > Maintenance > Service timer 1 | Service timer 1 day | Setup of service timer 1 days | 365 | 1 | 1000 | [7 empty] | Warning
445 | 6116 | General | Engine > Maintenance > Service timer 1 | Service timer 1 res | Reset of service timer 1 | [5 empty] | 1 | 1 | 1 |  |  | Warning
446 | 6121 | General | Engine > Maintenance > Service timer 2 | Service timer 2 hour | Setup of service timer 2 running hours | 500 | 0 | 9000 | [7 empty] | Warning
447 | 6123 | General | Engine > Maintenance > Service timer 2 | Service timer 2 day | Setup of service timer 2 days | 365 | 1 | 1000 | [7 empty] | Warning
448 | 6126 | General | Engine > Maintenance > Service timer 2 | Service timer 2 res | Reset of service timer 2 | [5 empty] | 1 | 1 | 1 |  |  | Warning
449 | 6130 | General | Functions > Alarm horn timer | Alarm horn | Setup of the Alarm Horn timer | [5 empty] | 200 | 0 | 9900 |  |  | Warning
1455 | 6151 | General | Engine > Start sequence > Before crank > Run coil | Run coil delay | Time for activation prior to crank relay | [5 empty] | 10 | 0 | 6000 |  |  | Warning
1456 | 6152 | General | Engine > Start sequence > Before crank > Run coil | Run coil type | Pulse: Reset for each start attempt. Continuous: High throughout all start attempts | Pulse |  |  |  | 0: Pulse, 1: Continuous | [5 empty] | Warning
452 | 6160 | General | Functions > Run status | Run status | Setup of the Run Status output | [5 empty] | 50 | 0 | 3000 |  |  | Warning
83 | 6165 | General | Engine > Running detection | Freq. Detect Lvl | Running status based on the this frequency | 32 | 10 | 35 | Hz | [6 empty] | Warning
453 | 6171 | General | Engine > Running detection | Number of teeth | Setup of number of teeth on the flywheel. Only used when MPU is selected in menu 6172 | 0 | 0 | 500 | [7 empty] | Warning
454 | 6172 | General | Engine > Running detection | Run detect type | Setup of primary running detection | Frequency |  |  |  | 0: Binary input, 1: MPU input, 2: Frequency, 3: EIC, 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23 | [5 empty] | Warning
455 | 6173 | General | Engine > Running detection | Running detect | Setup of Running detection limit. Only used when MPU is selected in menu 6172 | 1000 | 0 | 4000 | RPM | [6 empty] | Warning
456 | 6174 | General | Engine > Start sequence > After crank > Remove starter | Remove starter | Setup of Remove Starter limit. Only used when MPU is selected in menu 6172 | 400 | 1 | 2000 | RPM | [6 empty] | Warning
1101 | 6175 | General | Engine > Running detection | Oil pressure level | Used if oil pressure is used for Running detection | 0 | 0 | 150 | /10 | [6 empty] | Warning
1096 | 6176 | General | Engine > Running detection | Not running delay | Hysteresis timer for when running feedback unexpectedly disappears. | [5 empty] | 0 | 0 | 50 |  |  | Warning
458 | 6181 | General | Engine > Start sequence > Before crank > Start prepare | Start prepare | Setup of Start Prepare timer | [5 empty] | 50 | 0 | 6000 |  |  | Warning
459 | 6182 | General | Engine > Start sequence > Before crank > Start prepare | Ext. start prepare | Setup of extended Start Prepare timer | [5 empty] | 0 | 0 | 6000 |  |  | Warning
460 | 6183 | General | Engine > Start sequence > Crank > Crank timers | Start on time | Setup of Starter ON time during cranking. | [5 empty] | 50 | 10 | 6000 |  |  | Warning
461 | 6184 | General | Engine > Start sequence > Crank > Crank timers | Start off time | Setup of Starter OFF time before a new start attempt is made | [5 empty] | 50 | 10 | 990 |  |  | Warning
1102 | 6185 | General | Engine > Start sequence > Before crank > Start threshold | Start threshold type | RMI input selection when using oil pressure as running feedback. | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23 | [5 empty] | Warning
1103 | 6186 | General | Engine > Start sequence > Before crank > Start threshold | Start threshold | Starter threshold when using oil pressure as running feedback. | 0 | 0 | 300 | bar | [6 empty] | Warning
462 | 6191 | General | Engine > Start sequence > Crank > Start attempts | Start attempts | Max. number of start attempts. When the number of start attempts is exceeded a 'Start failure' alarm is activated (menu 4570) | 3 | 1 | 100 | [7 empty] | Warning
1373 | 6192 | General | Engine > Start sequence > Crank > Start attempts | Double starter | Number of normal/alternative starter attempts before switching back to normal/alternative starter. | 0 | 0 | 10
463 | 6201 | General | Engine > Shutdown Override | Shutd ovr start att | Max. number of start attempts with Shutdown Override active | 7 | 1 | 10 | [7 empty] | Warning
464 | 6202 | General | Engine > Shutdown Override | Shutd ovr cool down | Cooling down time with Shutdown Override active | [5 empty] | 240 | 0 | 9900 |  |  | Warning
465 | 6203 | General | Engine > Shutdown Override | Reset ShdOvr counter | Reset of Shutdown Override Running time | [10 empty] | Warning
466 | 6211 | General | Engine > Stop sequence > Cooldown | Cooldown time | Cooling down time | [5 empty] | 240 | 0 | 9900 |  |  | Warning
467 | 6212 | General | Engine > Stop sequence > Extended stop | Extended stop time | Extended Stop time | [5 empty] | 50 | 0 | 3000 |  |  | Warning
1319 | 6213 | General | Engine > Stop sequence > Stop threshold | Stop threshold type | Stop threshold type (Selection of temperature input for temperature dependent stop) | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: MLogic, 5: EIC Cooling water/oil temp., 6: EIC Cooling water temp., 7: EIC Oil temp., 8: EIC Ambient temp., 9: EIC Intercool temp., 10: EIC Fuel temp., 19: CIO 308 1.08, 20: CIO 308 1.11, 21: CIO 308 1.14, 22: CIO 308 1.17, 23: CIO 308 1.20, 24: CIO 308 1.23, 25: CIO 308 1.26, 26: CIO 308 1.29, 27: CIO 308 2.08, 28: CIO 308 2.11, 29: CIO 308 2.14, 30: CIO 308 2.17, 31: CIO 308 2.20, 32: CIO 308 2.23, 33: CIO 308 2.26, 34: CIO 308 2.29, 35: CIO 308 3.08, 36: CIO 308 3.11, 37: CIO 308 3.14, 38: CIO 308 3.17, 39: CIO 308 3.20, 40: CIO 308 3.23, 41: CIO 308 3.26, 42: CIO 308 3.29 | [5 empty] | Warning
1320 | 6214 | General | Engine > Stop sequence > Stop threshold | Stop threshold | Stop threshold (set point of engine temperature for temperature dependent stop) | 0 | 0 | 482 | deg |  | 1 | 1 | 1 |  |  | Warning
468 | 6220 | General | Generator > AC configuration > Voltage and frequency OK > Hz/V OK timer | Hz/V OK | Voltage and frequency OK delay after detection of running. Limits for voltage and frequency are set in menu 2111 and 2112 | [5 empty] | 50 | 0 | 990 |  |  | Warning
469 | 6231 | General | Breakers > Generator breaker > Breaker configuration | GB close delay | GB close delay at blackout | [5 empty] | 20 | 0 | 300 |  |  | Warning
847 | 6232 | General | Breakers > Generator breaker > Breaker configuration | GB Load time | Time needed to charge Generator breaker spring before closing | [5 empty] | 0 | 0 | 300 |  |  | Warning
754 | 6234 | General | Breakers > Generator breaker > Breaker configuration | GB reclose attempts | Choose how many times to attempt to close the breaker after the first close attempt has failed. | No reclose attempts |  |  |  | 0: No reclose attempts, 1: 1 reclose attempt, 2: 2 reclose attempt, 3: 3 reclose attempt | [5 empty] | Warning
480 | 6291 | General | Engine > Start sequence > Idle run | Idle start timer | Idle speed start duration | [5 empty] | 3000 | 0 | 9990 |  |  | Warning
481 | 6292 | General | Engine > Start sequence > Idle run | Idle start enable | Idle speed start enable | [5 empty] | 1 | 1 | 1 |  |  | Warning
482 | 6293 | General | Engine > Stop sequence > Idle stop | Idle stop timer | Idle speed stop duration | [5 empty] | 3000 | 0 | 9990 |  |  | Warning
483 | 6294 | General | Engine > Stop sequence > Idle stop | Idle stop enable | Idle speed stop enable | [5 empty] | 1 | 1 | 1 |  |  | Warning
484 | 6295 | General | Engine > Start sequence > Idle run | Idle active | Idle speed enable | [10 empty] | Warning
848 | 6297 | General | Engine > Start sequence > Idle run | Idle interrupt | Idle run interrupt via START/STOP in MANUAL | [10 empty] | Warning
491 | 6321 | General | Functions > Engine heater | Engine heater setp | Set point for engine heater controlled by analog input or EIC | 40 | 20 | 250 | deg | [6 empty] | Warning
492 | 6322 | General | Functions > Engine heater | Engine heater relay | output for engine heater controlled by analog input or EIC | [10 empty] | Warning
493 | 6323 | General | Functions > Engine heater | Engine heater input | Input selection for engine heater controlled by analog input or EIC | Multi input 20 |  |  |  | 0: Multi input 20, 1: Multi input 21, 2: Multi input 22, 3: Multi input 23, 4: EIC Cooling water temp., 5: EIC Oil temp., 6: EIC Ambient temp., 7: EIC Intercool temp., 8: EIC Fuel temp., 17: CIO 308 1.08, 18: CIO 308 1.11, 19: CIO 308 1.14, 20: CIO 308 1.17, 21: CIO 308 1.20, 22: CIO 308 1.23, 23: CIO 308 1.26, 24: CIO 308 1.29, 25: CIO 308 2.08, 26: CIO 308 2.11, 27: CIO 308 2.14, 28: CIO 308 2.17, 29: CIO 308 2.20, 30: CIO 308 2.23, 31: CIO 308 2.26, 32: CIO 308 2.29, 33: CIO 308 3.08, 34: CIO 308 3.11, 35: CIO 308 3.14, 36: CIO 308 3.17, 37: CIO 308 3.20, 38: CIO 308 3.23, 39: CIO 308 3.26, 40: CIO 308 3.29 | [5 empty] | Warning
494 | 6324 | General | Functions > Engine heater | Engine heater hyst | Hysteresis for engine heater controlled by analog input or EIC | 3 | 1 | 70 | deg | [6 empty] | Warning
495 | 6330 | General | Functions > Engine heater | Engine heater 1 | Alarm for engine heater controlled by analog input or EIC | 30 | 10 | 250 | deg |  | 100 | 10 | 3000 |  |  | Warning
470 | 6351 | General | Engine > Running detection | Run detection | Time allowed before running detection must be reached after cranking. | [5 empty] | 10 | 1 | 1200 |  |  | Warning
676 | 6352 | General | Engine > Stop sequence > Engine stopped (ext) | External engine stop | Detect external stop of the engine | [5 empty] | 10 | 1 | 1200
1309 | 6381 | General | Functions > Load shedding/adding | Load group start | Load shedding / adding: Number of groups at start | 3 | 0 | 5 | [7 empty] | Warning
1310 | 6382 | General | Functions > Load shedding/adding | Load shedding trip | Load shedding / adding: Trip level and timer between shedding | 80 | 30 | 100 | % |  | 5 | 1 | 100 |  |  | Warning
1311 | 6384 | General | Functions > Load shedding/adding | Load adding return | Load shedding / adding: Return level and timer between adding | 70 | 30 | 100 | % |  | 5 | 1 | 100 |  |  | Warning
1312 | 6386 | General | Functions > Load shedding/adding | Load shed/add enable | Load shedding / adding: Enable | Off |  |  |  | 0: Off, 1: On | [5 empty] | Warning
490 | 6391 | General | I/O settings > External I/O > IOM 2x0 > Analogue loadsharing | Loadshare type | Setup of load sharing type | Adjustable |  |  |  | 0: Adjustable, 1: Selco T4800, 2: Cummins PCC, 3: Woodward SPM-D11 | [5 empty] | Warning
489 | 6392 | General | I/O settings > External I/O > IOM 2x0 > Analogue loadsharing | Loadshare P out | Adjustment of the analogue load sharing P line signal value at 100% kW | 4 | 1 | 5 | V | [6 empty] | Warning
605 | 6393 | General | I/O settings > External I/O > IOM 2x0 > Analogue loadsharing | Loadshare Q out | Adjustment of the analogue load sharing Q line signal value at 100% kvar | 4 | 1 | 5 | V | [6 empty] | Warning
500 | 6411 | General | Engine > Battery/Aux supply > Test | Battery test | Battery test voltage level | 18 | 8 | 32 | V |  | 20 | 20 | 20 |  |  | Warning
501 | 6412 | General | Engine > Battery/Aux supply > Test | Battery test timer | Battery test timer setting | [5 empty] | 20 | 1 | 300 |  |  | Warning
502 | 6413 | General | Engine > Battery/Aux supply > Test | Battery test input | Battery test input selection | Power supply |  |  |  | 0: Power supply, 1: Multi input 20, 2: Multi input 21, 3: Multi input 22, 4: Multi input 23, 5: Power supply + Start Sequence, 6: Multi input 20 + Start Sequence, 7: Multi input 21 + Start Sequence, 8: Multi input 22 + Start Sequence, 9: Multi input 23 + Start Sequence | [5 empty] | Warning
503 | 6421 | General | Engine > Battery/Aux supply > Test | Auto Battery test | automatic battery test settings | Monday |  |  |  | 0: Monday, 1: Tuesday, 2: Wednesday, 3: Thursday, 4: Friday, 5: Saturday, 6: Sunday | [5 empty] | Warning
504 | 6423 | General | Engine > Battery/Aux supply > Test | Auto Batt test hours | Start hour for automatic battery test | 10 | 0 | 23 | [7 empty] | Warning
505 | 6424 | General | Engine > Battery/Aux supply > Test | Auto Batt test weeks | Weekly interval between automatic battery test | 52 | 1 | 52 | [7 empty] | Warning
506 | 6425 | General | Engine > Battery/Aux supply > Test | Auto Batt test relay | Relay output activated to crank engine during battery test | [10 empty] | Warning
513 | 6460 | General | Functions > Fan > Single fan start/stop > Fan configuration > Max ventilation | Max ventilation setp | set point for the ventilaton fan controlled analog input or EIC | 90 | 20 | 250 | deg | [6 empty] | Warning
514 | 6461 | General | Functions > Fan > Single fan start/stop > Fan configuration > Max ventilation | Max ventilation conf | output for the ventilaton fan controlled analog input or EIC | [10 empty] | Warning
515 | 6463 | General | Functions > Fan > Single fan start/stop > Fan configuration > Max ventilation | Max ventilation hyst | Hysteresis for the ventilaton fan controlled analog input or EIC | 5 | 1 | 70 | deg | [6 empty] | Warning
516 | 6470 | General | Functions > Fan > Single fan start/stop > Fan alarms > Max ventilation 1 | Max ventilation 1 | Alarm 1 for the ventilaton fan controlled analog input or EIC | 95 | 20 | 250 | deg |  | 10 | 0 | 600
517 | 6480 | General | Functions > Fan > Single fan start/stop > Fan alarms > Max ventilation 2 | Max ventilation 2 | Alarm 2 for the ventilaton fan controlled analog input or EIC | 98 | 20 | 250 | deg |  | 10 | 0 | 600 |  |  | Shutdown
518 | 6490 | General |  | Summer/Winter time | Enable switch to summer time | [10 empty] | Warning
522 | 6540 | General | Functions > Not in Auto | Not in AUTO | Alarm for AGC unit not in auto | [5 empty] | 3000 | 100 | 9000
523 | 6551 | General | Functions > Fuel | Fuel pump log. start | Fuel pump log. Start (Fuel transfer pump start point) | 20 | 0 | 100 | % |  | 10 | 10 | 100 |  |  | Warning
524 | 6552 | General | Functions > Fuel | Fuel pump log. stop | Fuel pump log. Stop (Fuel transfer pump stop point) | 80 | 0 | 100 | % | [6 empty] | Warning
525 | 6553 | General | Functions > Fuel | Fuel fill check | Fuel fill check (Fuel transfer pump alarm) | [5 empty] | 600 | 1 | 9999 |  |  | Warning
526 | 6554 | General | Functions > Fuel | Fuel pump log. input | Input/output selection for fuel pump logic. (Note: Relay setup in I/O setup) | Auto detection |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 22: Auto detection, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29 | [5 empty] | Warning
89 | 6557 | General | Functions > Fuel | Fuel fill slope | Fuel fill slope percentage | 2 | 1 | 10 | % |  | 1 | 1 | 1 |  |  | Warning
1604 | 6701 | General | Engine > ECU configuration > Diagnostics | Diagnostics | Activate Diagnostics Mode to read ECU data without starting the engine | [5 empty] | 300 | 0 | 300 | Limits | Limits | Warning
757 | 6721 | General | Functions > Diesel Exhaust Fluid | DEF pump log. start | DEF pump log start | 20 | 0 | 100 | % |  | 10 | 10 | 100 |  |  | Warning
758 | 6722 | General | Functions > Diesel Exhaust Fluid | DEF pump log. stop | DEF pump log stop | 80 | 0 | 100 | % | [6 empty] | Warning
759 | 6723 | General | Functions > Diesel Exhaust Fluid | DEF fill check | Fill check for DEF (Transfer pump alarm) (Note: Relay setup in I/O setup) | [5 empty] | 600 | 1 | 9999 |  |  | Warning
760 | 6724 | General | Functions > Diesel Exhaust Fluid | DEF fill slope | DEF fill slope | 2 | 1 | 10 | % |  | 1 | 1 | 1 |  |  | Warning
761 | 6731 | General | Functions > Generic fluid | Fluid pump start | Generic pump log. start | 20 | 0 | 100 | % |  | 10 | 10 | 100 |  |  | Warning
762 | 6732 | General | Functions > Generic fluid | Fluid pump stop | Generic pump log. stop | 80 | 0 | 100 | % | [6 empty] | Warning
763 | 6733 | General | Functions > Generic fluid | Fluid fill check | Generic Fluid fill check(Fluid transfer pump alarm) | [5 empty] | 600 | 1 | 9999 |  |  | Warning
764 | 6734 | General | Functions > Generic fluid | Fluid pump logic | Input/output selection for fluid pump logic. (Note: Relay setup in I/O setup) | Multi input 20 |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29 | [5 empty] | Warning
765 | 6735 | General | Functions > Generic fluid | Fluid fill slope | Generic fill slope | 2 | 1 | 10 | % |  | 1 | 1 | 1 |  |  | Warning
1916 | 6801 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. f 5 | Nominal generator frequency set point 5 | 50 | 45 | 62 | Hz | [6 empty] | Warning
1917 | 6802 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. P 5 | Nominal generator power set point 5 | 480 | 10 | 20000 | kW | [6 empty] | Warning
1918 | 6803 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. I 5 | Nominal generator current set point 5 | 867 | 0 | 9000 | A | [6 empty] | Warning
1919 | 6804 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. U 5 | Nominal generator voltage set point 5 | 400 | 100 | 25000 | V | [6 empty] | Warning
1896 | 6805 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. RPM 5 | Nominal generator rpm set point 5 | 1500 | 100 | 4000 | RPM | [6 empty] | Warning
1898 | 6806 | General | Alternative configuration > Generator nominal settings > Nominal settings 5 > Basic settings | Nom. I E/N/M 5 | Nom I E/N/M 3 (Nominal current Earth/Neutral/Mains set point 5) | 867 | 0 | 9000 | A | [6 empty] | Warning
1920 | 6811 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. f 6 | Nominal generator frequency set point 6 | 50 | 45 | 62 | Hz | [6 empty] | Warning
1921 | 6812 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. P 6 | Nominal generator power set point 6 | 230 | 10 | 20000 | kW | [6 empty] | Warning
1922 | 6813 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. I 6 | Nominal generator current set point 6 | 345 | 0 | 9000 | A | [6 empty] | Warning
1923 | 6814 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. U 6 | Nominal generator voltage set point 6 | 480 | 100 | 25000 | V | [6 empty] | Warning
1897 | 6815 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. RPM 6 | Nominal generator rpm set point 6 | 1500 | 100 | 4000 | RPM | [6 empty] | Warning
1899 | 6816 | General | Alternative configuration > Generator nominal settings > Nominal settings 6 > Basic settings | Nom. I E/N/M 6 | Nom I E/N/M 4 (Nominal current Earth/Neutral/Mains set point 6) | 867 | 0 | 9000 | A | [6 empty] | Warning
1626 | 6841 | General | Generator > Current protections > Peak and Mean values | I thermal demand | Setup of I thermal demand period. Enable is used for reset | [5 empty] | 80 | 0 | 200 |  |  | Warning
1625 | 6843 | General | Generator > Current protections > Peak and Mean values | I max demand | Reset I max demand | [10 empty] | Warning
1600 | 6891 | General | Engine > Maintenance > Oil reneval | Oil renewal | Setup of relay output for engine oil renewal | 750 | 1 | 9999 | Hours | [6 empty] | Warning
82 | 6893 | General |  | Adj reset value | Change the reset level for the oil renewal | 1000 | 100 | 10000 | Hours | [6 empty] | Warning
1912 | 6951 | General | Functions > Command timer > Command timer 1 | Command timer 1 week | Select which week(s) in month command timer 1 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28) | [5 empty] | Warning
1913 | 6952 | General | Functions > Command timer > Command timer 2 | Command timer 2 week | Select which week(s) in month command timer 2 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28) | [5 empty] | Warning
1914 | 6953 | General | Functions > Command timer > Command timer 3 | Command timer 3 week | Select which week(s) in month command timer 3 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28) | [5 empty] | Warning
1915 | 6954 | General | Functions > Command timer > Command timer 4 | Command timer 4 week | Select which week(s) in month command timer 4 start/stop is active | All weeks in month |  |  |  | 0: All weeks in month, 1: First week (1 - 7), 2: Second week (8 - 14), 3: Third week (15 - 21), 4: Fourth week (22 - 28) | [5 empty] | Warning
701 | 6961 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup day(s) for activation of Command timer 1 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
702 | 6962 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of hour for activation of Command timer 1 | 10 | 0 | 23 | Hours | [6 empty] | Warning
703 | 6963 | General | Functions > Command timer > Command timer 1 | Start timer 1 | Setup of minute for activation of Command timer 1 | 0 | 0 | 59 | [7 empty] | Warning
705 | 6964 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup day(s) for deactivation of Command timer 1 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
706 | 6965 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of hour for deactivation of Command timer 1 | 10 | 0 | 23 | Hours | [6 empty] | Warning
707 | 6966 | General | Functions > Command timer > Command timer 1 | Stop timer 1 | Setup of minute for deactivation of Command timer 1 | 0 | 0 | 59 | [7 empty] | Warning
709 | 6971 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup day(s) for activation of Command timer 2 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
710 | 6972 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of hour for activation of Command timer 2 | 10 | 0 | 23 | Hours | [6 empty] | Warning
711 | 6973 | General | Functions > Command timer > Command timer 2 | Start timer 2 | Setup of minute for activation of Command timer 2 | 0 | 0 | 59 | [7 empty] | Warning
713 | 6974 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup day(s) for deactivation of Command timer 2 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
714 | 6975 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of hour for deactivation of Command timer 2 | 10 | 0 | 23 | Hours | [6 empty] | Warning
715 | 6976 | General | Functions > Command timer > Command timer 2 | Stop timer 2 | Setup of minute for deactivation of Command timer 2 | 0 | 0 | 59 | [7 empty] | Warning
717 | 6981 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup day(s) for activation of Command timer 3 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
718 | 6982 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of hour for activation of Command timer 3 | 10 | 0 | 23 | Hours | [6 empty] | Warning
719 | 6983 | General | Functions > Command timer > Command timer 3 | Start timer 3 | Setup of minute for activation of Command timer 3 | 0 | 0 | 59 | [7 empty] | Warning
721 | 6984 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup day(s) for deactivation of Command timer 3 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
722 | 6985 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of hour for deactivation of Command timer 3 | 10 | 0 | 23 | Hours | [6 empty] | Warning
723 | 6986 | General | Functions > Command timer > Command timer 3 | Stop timer 3 | Setup of minute for deactivation of Command timer 3 | 0 | 0 | 59 | [7 empty] | Warning
725 | 6991 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup day(s) for activation of Command timer 4 | OFF |  |  |  | 0: OFF, 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
726 | 6992 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of hour for activation of Command timer 4 | 10 | 0 | 23 | Hours | [6 empty] | Warning
727 | 6993 | General | Functions > Command timer > Command timer 4 | Start timer 4 | Setup of minute for activation of Command timer 4 | 0 | 0 | 59 | [7 empty] | Warning
729 | 6994 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup day(s) for deactivation of Command timer 4 | MO-TU-WE-TH-FR-SA-SU |  |  |  | 1: MO, 2: TU, 3: WE, 4: TH, 5: FR, 6: SA, 7: SU, 8: MO-TU-WE-TH, 9: MO-TU-WE-TH-FR, 10: SA-SU, 11: MO-TU-WE-TH-FR-SA-SU | [5 empty] | Warning
730 | 6995 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of hour for deactivation of Command timer 4 | 10 | 0 | 23 | Hours | [6 empty] | Warning
731 | 6996 | General | Functions > Command timer > Command timer 4 | Stop timer 4 | Setup of minute for deactivation of Command timer 4 | 0 | 0 | 59 | [7 empty] | Warning
527 | 7001 | Mains | Power set points > MPE/Peak shaving > Day/Night power set point | Day Setting | Day time setting for peakshaving/mains power export | 750 | -20000 | 20000 | kW | [6 empty] | Warning
528 | 7002 | Mains | Power set points > MPE/Peak shaving > Day/Night power set point | Night Setting | Night time setting for peakshaving/mains power export | 1000 | -20000 | 20000 | kW | [6 empty] | Warning
529 | 7003 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range max | Mains power transducer maximum setting | 0 | 0 | 20000 | kW | [6 empty] | Warning
530 | 7004 | Mains | Basic settings > Measurement setup > Mains transducer settings | Transducer range min | Mains power transducer minimum setting | 0 | -20000 | 0 | kW | [6 empty] | Warning
1440 | 7005 | Mains | Basic settings > Measurement setup > Wiring connection | Mains power measure | Mains power meas (Selection of mains power measuring input) | 4th CT power meas (internal) |  |  |  | 0: Multi input 20 (transducer), 1: 4th CT power meas (internal) | [5 empty] | Warning
531 | 7011 | Mains | Power set points > MPE/Peak shaving > Day/Night settings | Start Hour | Start hour for peakshaving/mains power export | 8 | 0 | 23 | [7 empty] | Warning
532 | 7012 | Mains | Power set points > MPE/Peak shaving > Day/Night settings | Start Minute | start minute for peakshaving/mains power export | 0 | 0 | 59 | [7 empty] | Warning
533 | 7013 | Mains | Power set points > MPE/Peak shaving > Day/Night settings | Stop Hour | Stop hour for peakshaving/mains power export | 16 | 0 | 23 | [7 empty] | Warning
534 | 7014 | Mains | Power set points > MPE/Peak shaving > Day/Night settings | Stop Minute | Stop hour for peakshaving/mains power export | 0 | 0 | 59 | [7 empty] | Warning
535 | 7021 | Mains | Power set points > MPE/Peak shaving > Day/Night power set point | Start generator | Start generator peakshaving/mains power export set point | 80 | 5 | 100 | % |  | 100 | 0 | 9900 |  |  | Warning
536 | 7023 | Mains | Power set points > MPE/Peak shaving > Day/Night power set point | Minimum Load | Minimum load (Peak shaving minimum generator load) | 5 | 0 | 100 | % | [6 empty] | Warning
537 | 7031 | Mains | Power set points > MPE/Peak shaving > Day/Night power set point | Stop generator | Stop peakshaving/mains power export set point | 60 | 0 | 80 | % |  | 300 | 0 | 9900 |  |  | Warning
538 | 7041 | Mains | Power set points > Test | Test | set point for load test. | 1 | 1 | 100 |  |  | 0 | 0 | 9990 |  |  | Warning
539 | 7043 | Mains | Power set points > Test | Return mode | Return mode after completed test sequence. | No mode change |  |  |  | 0: MANUAL mode, 1: AUTO mode, 2: No mode change, 3: No Regulation | [5 empty] | Warning
540 | 7044 | Mains | Power set points > Test | Test type | Selection of test type. Note: StandAlone cannot run Load test. | Simple test |  |  |  | 0: Simple test, 1: Load test (not StandAlone), 2: Full test | [5 empty] | Warning
541 | 7051 | Mains | Power set points > Fixed power | Contr. settings P | Fixed power set point | 100 | 0 | 100 | % | [6 empty] | Warning
542 | 7052 | Mains | Power set points > Cos phi or Fixed reactive power | Ctrl cos phi set | Fixed cos phi set point | 0.9 | 0.6 | 1 | PF | [6 empty] | Warning
1236 | 7053 | Mains | Power set points > Cos phi or Fixed reactive power | Ctrl cos phi type | Inductive or capacitive PF regulation | Inductive |  |  |  | 0: Inductive, 1: Capacitive | [5 empty] | Warning
1370 | 7054 | Mains | Power set points > Cos phi or Fixed reactive power | Contr. settings Q | Fixed reactive power set point | 0 | -100 | 100 | % | [6 empty] | Warning
1299 | 7055 | Mains | Power set points > Cos phi or Fixed reactive power | CtrlSet cos phi or Q | Set origin of cos phi reference | Off |  |  |  | 0: Off, 3: Superior (power management), 4: Fixed Q (single DG parallel) | [5 empty] | Warning
543 | 7061 | Mains | Mains > AMF functions > AMF timer | U mains failure | Timer for mains failure voltage detection | [5 empty] | 50 | 5 | 9900 |  |  | Warning
544 | 7062 | Mains | Mains > AMF functions > AMF timer | Mains OK Delay U | Timer for mains voltage ok detection | [5 empty] | 60 | 2 | 9900 |  |  | Warning
545 | 7063 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Voltage | set point for mains voltage range low | 90 | 30 | 100 | % | [6 empty] | Warning
546 | 7064 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Voltage | set point for mains voltage range high | 110 | 100 | 120 | % | [6 empty] | Warning
547 | 7065 | Mains | Mains > AMF functions > Start sequence in AMF mode | Mains fail ctrl | Start sequence in AMF mode | Start eng. + open MB |  |  |  | 0: Start eng. + open MB, 1: Start engine, 2: Open MB when engine ready | [5 empty] | Warning
874 | 7066 | Mains | Mains > Voltage and frequency limits > Voltage settings | Unbalance voltage | Mains voltage unbalance setting | 100 | 2 | 100 | % | [6 empty] | Warning
548 | 7071 | Mains | Mains > AMF functions > AMF timer | f mains failure | Timer for mains failure frequency detection | [5 empty] | 50 | 5 | 9900 |  |  | Warning
549 | 7072 | Mains | Mains > AMF functions > AMF timer | Mains OK Delay f | Timer for mains frequency ok detection | [5 empty] | 60 | 2 | 9900 |  |  | Warning
550 | 7073 | Mains | Mains > Voltage and frequency limits > Frequnecy settings | Low Frequency | set point for mains frequency range low | 95 | 80 | 100 | % | [6 empty] | Warning
551 | 7074 | Mains | Mains > Voltage and frequency limits > Frequnecy settings | High Frequency | set point for mains frequency range high | 105 | 100 | 120 | % | [6 empty] | Warning
1770 | 7075 | Mains | Mains > AMF functions > Mains fail assumption | Mains fail assumpt. | In the case that a controller is powered ON and finds the mains source healthy, it can be specified how it should approach connecting to the mains. | Mains has recovered |  |  |  | 0: Mains has recovered, 1: Mains is recovering | [5 empty] | Warning
552 | 7081 | Mains | Mains > AMF functions > AMF timer | Modeshift | Allow switch to AMF mode | Mode shift off |  |  |  | 0: Mode shift off, 1: Mode shift on | [5 empty] | Warning
553 | 7082 | Mains | Breakers > Mains breaker > Breaker configuration | MB close delay | MB breaker close delay. | [5 empty] | 5 | 0 | 300 |  |  | Warning
554 | 7083 | Mains | Synchronisation > Mains parallel settings | Back Synchronising | synchronising ON/OFF | [10 empty] | Warning
555 | 7084 | Mains | Synchronisation > Mains parallel settings | Sync. to mains | Allow synchronising MB | [10 empty] | Warning
846 | 7085 | Mains | Breakers > Mains breaker > Breaker configuration | MB Load time | Time needed to charge Mains breaker spring before closing | [5 empty] | 0 | 0 | 300 |  |  | Warning
174 | 7091 | Mains | Mains > Voltage and frequency limits > Voltage settings | Low Volt. Hyst. | Low voltage mains hysteresis | 0 | 0 | 70 | % | [6 empty] | Warning
175 | 7092 | Mains | Mains > Voltage and frequency limits > Voltage settings | High Volt Hyst. | High voltage mains hysteresis | 0 | 0 | 20 | % | [6 empty] | Warning
176 | 7093 | Mains | Mains > Voltage and frequency limits > Frequnecy settings | Low Freq. Hyst. | Low frequency mains hysteresis | 0 | 0 | 20 | % | [6 empty] | Warning
177 | 7094 | Mains | Mains > Voltage and frequency limits > Frequnecy settings | High Freq Hyst. | High frequency mains hysteresis | 0 | 0 | 20 | % | [6 empty] | Warning
1476 | 7221 | Mains | Power set points > Offset > Power offset | Power offset 1 | Offset to power reference 1 | 0 | -20000 | 20000 | kW |  | 1 | 1 | 1 |  |  | Warning
1477 | 7223 | Mains | Power set points > Offset > Power offset | Power offset 2 | Offset to power reference 2 | 0 | -20000 | 20000 | kW |  | 1 | 1 | 1 |  |  | Warning
1478 | 7225 | Mains | Power set points > Offset > Power offset | Power offset 3 | Offset to power reference 3 | 0 | -20000 | 20000 | kW |  | 1 | 1 | 1 |  |  | Warning
1479 | 7241 | Mains | Power set points > Offset > Cos phi offset | Cos phi offset 1 | Offset to cos phi reference 1 | 0 | -0.8 | 0.8 | PF | [6 empty] | Warning
1480 | 7243 | Mains | Power set points > Offset > Cos phi offset | Cos phi offset 2 | Offset to cos phi reference 2 | 0 | -0.8 | 0.8 | PF | [6 empty] | Warning
1481 | 7245 | Mains | Power set points > Offset > Cos phi offset | Cos phi offset 3 | Offset to cos phi reference 3 | 0 | -0.8 | 0.8 | PF | [6 empty] | Warning
557 | 7501 | Communication | Power set points > External power set point | Comm bus control P | Modbus communication. Power control ON/OFF. | [10 empty] | Warning
558 | 7502 | Communication | Power set points > External power set point | Comm bus control f | Modbus communication. Frequency control ON/OFF. | [10 empty] | Warning
559 | 7503 | Communication | Power set points > External power set point | Comm bus control U | Modbus communication. Voltage control ON/OFF. | [10 empty] | Warning
560 | 7504 | Communication | Power set points > External power set point | Comm bus ctrl cosphi | Modbus communication. cos phi control ON/OFF. | [10 empty] | Warning
561 | 7505 | Communication | Power set points > External power set point | Comm bus control Q | Modbus communication. Reactive power control ON/OFF. | [10 empty] | Warning
562 | 7511 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm. ID 1 | Configuration of external communication port 1 ID number | 3 | 1 | 247 | [7 empty] | Warning
563 | 7512 | Communication | Communication > RS485 > RS485 1 > Settings | Ext. comm.speed1 | Configuration of external communication port 1 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud | [5 empty] | Warning
565 | 7513 | Communication | Communication > RS485 > RS485 1 > Communication error | Ext comm. error 1 | External communication port 1 supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
1099 | 7521 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm. ID 2 | Configuration of external communication port 2 ID number | 3 | 1 | 247 | [7 empty] | Warning
1100 | 7522 | Communication | Communication > RS485 > RS485 2 > Settings | Ext. comm.speed2 | Configuration of external communication port 2 speed | 9600 Baud |  |  |  | 0: 9600 Baud, 1: 19200 Baud, 2: 38400 Baud, 3: 115200 Baud | [5 empty] | Warning
951 | 7523 | Communication | Communication > RS485 > RS485 2 > Communication error | Ext comm. error 2 | External communication port 2 supervision | [5 empty] | 100 | 10 | 1000 |  |  | Warning
1437 | 7841 | Communication | Communication > CAN protocols | CAN A Protocol | CAN bus protocol selection | H5 EIC |  |  |  | 0: OFF, 3: H5 EIC, 4: Canshare, 4: Canshare, 4: Canshare, 5: AOP2, 12: Digital AVR, 11: Ext. Modules DEIF, 13: PMS lite, 14: 3rd party loadshare, 14: 3rd party loadshare, 14: 3rd party loadshare | [5 empty] | Warning
1438 | 7842 | Communication | Communication > CAN protocols | CAN B Protocol | CAN bus protocol selection | PMS lite |  |  |  | 0: OFF, 3: H5 EIC, 4: Canshare, 4: Canshare, 4: Canshare, 5: AOP2, 12: Digital AVR, 11: Ext. Modules DEIF, 13: PMS lite, 14: 3rd party loadshare, 14: 3rd party loadshare, 14: 3rd party loadshare | [5 empty] | Warning
1804 | 7860 | Communication |  | CAN Share failure | Can Share Communication supervision | [5 empty] | 0 | 0 | 1000
1805 | 7866 | Communication |  | CAN Sha fail mode | Selection of running mode in case of Can Share failure. | No regulation mode |  |  |  | 0: No regulation mode, 1: Manual mode, 2: No mode change | [5 empty] | Warning
1711 | 7891 | Communication | I/O settings > External I/O > CIO > Enable | CIO Enable | Configuration of CIO enable | OFF |  |  |  | 0: OFF, 3: ON | [5 empty] | Warning
1639 | 7900 | Communication | Communication > Ethernet comm. error | Ethernet comm. error | Ethernet communication supervision | [5 empty] | 100 | 10 | 1000
1396 | 8501 | PMS lite | PMS lite > Load dependent start/stop config > LDSS percent/timer config | Ld. start | Setup of Load dependent Start limits | 90 | 1 | 100 | % |  | 100 | 0 | 9900 |  |  | Warning
1398 | 8503 | PMS lite | PMS lite > Load dependent start/stop config > LDSS percent/timer config | Ld. stop | Setup of Load dependent Stop limits | 70 | 1 | 100 | % |  | 300 | 50 | 9900 |  |  | Warning
1403 | 8505 | PMS lite | PMS lite > Load dependent start/stop config > Start/stop config | Start/stop | Setup type of Auto start/stop signal to use | Load dependent start/stop |  |  |  | 0: Load dependent start/stop, 1: PLC start/stop | [5 empty] | Warning
1359 | 8511 | PMS lite | PMS lite > PMS lite general | PMS lite ID | Used to manually select an ID in PMS lite (0 = auto detect) | 0 | 0 | 254 | [7 empty] | Warning
1393 | 8512 | PMS lite | PMS lite > PMS lite general | Priority | Select a priority level for this genset. 0 is no priority (ID is used) | 0 | 0 | 254 | [7 empty] | Warning
1833 | 8513 | PMS lite | PMS lite > PMS lite general | PMS lite fail mode | Change to this mode if alarm 8570 (ID missing/added) or 8590 (Duplicated ID) occurs | MANUAL |  |  |  | 0: NoReg, 1: MANUAL, 2: No mode change | [5 empty] | Warning
1394 | 8514 | PMS lite | PMS lite > PMS lite general | Share parameters | Enable to share parameters with other controllers (oneshot command). Shared parameters: 8501, 8503, 8513, 8530, 8540, 8550, 8560, 8570, 8580 and 8590 | Off |  |  |  | 0: Off, 1: On | [5 empty] | Warning
1800 | 8515 | PMS lite | PMS lite > PMS lite general | PMS lite baudrate | Change the baudrate for PMS lite | 125kbps |  |  |  | 1: 125kbps, 2: 250kbps | [5 empty] | Warning
1405 | 8521 | PMS lite | PMS lite > Load dependent start/stop config > Multi start config | Multi start config | Should this genset start when multi starting? Longest connected timer decides time | No action on fail |  |  |  | 0: No action on fail, 1: Start all other DGs | 600 | 0 | 9999 | Limits | Limits | Warning
1406 | 8531 | PMS lite | PMS lite > Running hour config > Running hours | Running hours | Forces running hour mode on all connected gensets, and uses the setpoint for the amount of hours to run | 2 | 1 | 20000 | Hours | [6 empty] | Warning
1407 | 8533 | PMS lite | PMS lite > Running hour config > Running hour type | Running Hour Type | Select type of Running hour mode | Relative / trip |  |  |  | 0: Absolute, 1: Relative / trip, 2: Load Profiled | [5 empty] | Warning
121 | 8540 | PMS lite | PMS lite > Avaliable power | Available Power | Setup of the Available power limit alarm | 1000 | 10 | 30000 | kW | [6 empty] | Warning
1404 | 8550 | PMS lite | PMS lite > Minimum number to run | Min. run. | Nbr of gensets required to be running | 1 | 1 | 254 |  |  | 10 | 0 | 3600 |  |  | Warning
1807 | 8560 | PMS lite | PMS lite > Minimum number of units | Min. units | Nbr of units required to be connected to plant | 1 | 1 | 254 |  |  | 0 | 0 | 3600 |  |  | Warning
1801 | 8570 | PMS lite | PMS lite > Missing/added ID | ID missing/added | Alarm is triggered if number of units is changed after number of units has been stable for 30s | [5 empty] | 0 | 0 | 10 |  |  | Warning
1360 | 8580 | PMS lite | PMS lite > ID not available | ID not avaliable | Occurs if the selected ID isnt avaliable (running, manual selected etc.) | [10 empty] | Warning
1806 | 8590 | PMS lite | PMS lite > Duplicated ID | Duplicated ID | Occurs if multiple units has the same ID. | [10 empty] | Warning
1408 | 8603 | PMS lite | PMS lite > Sections | DG Busbar | Select the busbar section for the generator if used in setup with BTB(s). 0 = No section | 0 | 0 | 65 | [7 empty] | Warning
1372 | 9030 | Jump | Basic settings > Measurement setup > Scaling > Scaling | Scaling | Select the voltage range of operation | 100 to 25000V |  |  |  | 0: 10 to 2500V, 1: 100 to 25000V, 2: 10 to 160kV, 3: 0.4 to 75kV | [5 empty] | Warning
695 | 9111 | Jump | Basic settings > Controller settings > Password | Customer password | Setup of Customer Password | 2000 | 1 | 32000 | [7 empty] | Warning
696 | 9112 | Jump | Basic settings > Controller settings > Password | Service password | Setup of Service Password | 2001 | 1 | 32000 | [7 empty] | Warning
697 | 9113 | Jump | Basic settings > Controller settings > Password | Master password | Setup of Master Password | 2002 | 1 | 32000 | [7 empty] | Warning
1107 | 9131 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration | Menu is used to choose between the different AC measurement systems. | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3, 1: 2 phase L1L3, 2: 2 phase L1L2, 3: 1 phase L1 | [5 empty] | Warning
946 | 9132 | Jump | Basic settings > Measurement setup > Wiring connection > AC configuration | AC configuration BB | Bus connection of Neutral wire | 3 phase 3W4 |  |  |  | 0: 3 phase 3W4, 10: 3 phase 3W3 | [5 empty] | Warning
699 | 9151 | Jump | Basic settings > Controller settings > Display > Display Control | Backlight dimmer | Setup of backlight level | 12 | 0 | 15 | [7 empty] | Warning
939 | 9152 | Jump | Basic settings > Controller settings > Display > Display Control | Green LEDs dimmer | Adjust level for green leds | 15 | 1 | 15 | [7 empty] | Warning
940 | 9153 | Jump | Basic settings > Controller settings > Display > Display Control | Red LEDs dimmer | Adjust level for red leds | 15 | 1 | 15 | [7 empty] | Warning
685 | 9154 | Jump | Basic settings > Controller settings > Display > Display Control | Contrast setting | Display contrast level | 0 | -20 | 20 | [7 empty] | Warning
937 | 9155 | Jump | Basic settings > Controller settings > Display > Display Control | Sleep mode | Sleep mode enable | [5 empty] | 60 | 1 | 1800 | Limits | Limits | Warning
1227 | 9157 | Jump | Basic settings > Controller settings > Display > Display Control | Alarm Jump | Display behavior when and alarm is activated. ON: jump to the Alarm list, OFF: stay at present view | On |  |  |  | 0: Off, 1: On | [5 empty] | Warning
797 | 9158 | Jump | Basic settings > Controller settings > Display > Display Control | Engineering units | Engineering units Bar/celsius or Psi/fahrenheit | Bar/celsius |  |  |  | 0: Bar/celsius, 1: Psi/fahrenheit | [5 empty] | Warning
1819 | 9159 | Jump | Communication > Remote Display | Remote display setup | Setup of remote display | OFF |  |  |  | 0: OFF, 1: ON view only, 2: ON view + controls | [5 empty] | Warning
1275 | 9181 | Jump | Basic settings > Application type > Application config | Apply config | Application config - Apply configuration from MB/GB configuration and Mains present. | Off |  |  |  | 0: Off, 1: On | [5 empty] | Warning
1278 | 9182 | Jump | Basic settings > Application type > Application config | GB Type | Application config GB configuration | Pulse |  |  |  | 0: Pulse, 3: Continuous, 4: Compact | [5 empty] | Warning
1279 | 9183 | Jump | Basic settings > Application type > Application config | Mains Present | Application config mains present | No mains present |  |  |  | 0: Mains present, 1: No mains present | [5 empty] | Warning
1277 | 9184 | Jump | Basic settings > Application type > Application config | MB Type | Application config MB configuration | No MB |  |  |  | 0: Pulse, 1: No MB, 3: Continuous, 4: Compact | [5 empty] | Warning
1602 | 9220 | Jump | Basic settings > Controller settings > Parameter filter | Parameter list setup | Parameter list selection | Master tree |  |  |  | 0: Parameter list, 1: Custom tree, 2: Service tree, 3: Master tree | [5 empty] | Warning
1603 | 11200 | USW | USW specific parameters > Parameter name | Parameter name | This parameter can be used to identify which parameter list is used on the unit | [10 empty] | Warning
1510 | 13010 | SuperVision | USW specific parameters > Sensor selection | Oil press. input USW | Input for oil pressure display on USW SuperVision page | Auto detection |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 20: EIC Oil pressure, 22: Auto detection | [5 empty] | Warning
1511 | 13011 | SuperVision | USW specific parameters > Sensor selection | Cool water input USW | Input for cooling water display on USW SuperVision page | Auto detection |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 21: EIC Water temp, 22: Auto detection | [5 empty] | Warning
1512 | 13012 | SuperVision | USW specific parameters > Sensor selection | Fuel level input USW | Input for fuel level display on USW SuperVision page | Auto detection |  |  |  | 4: Multi input 20, 5: Multi input 21, 6: Multi input 22, 7: Multi input 23, 12: CIO 308 1.08, 13: CIO 308 1.11, 14: CIO 308 1.14, 15: CIO 308 1.17, 16: CIO 308 1.20, 17: CIO 308 1.23, 18: CIO 308 1.26, 19: CIO 308 1.29, 44: CIO 308 2.08, 45: CIO 308 2.11, 46: CIO 308 2.14, 47: CIO 308 2.17, 48: CIO 308 2.20, 49: CIO 308 2.23, 50: CIO 308 2.26, 51: CIO 308 2.29, 52: CIO 308 3.08, 53: CIO 308 3.11, 54: CIO 308 3.14, 55: CIO 308 3.17, 56: CIO 308 3.20, 57: CIO 308 3.23, 58: CIO 308 3.26, 59: CIO 308 3.29, 22: Auto detection | [5 empty] | Warning
1835 | 13013 | SuperVision | USW specific parameters > Sensor selection | RPM input USW | Engine speed(rpm) measurement for supervision | Auto detection |  |  |  | 22: Auto detection, 71: EIC, 72: MPU, 43: Generator frequency | [5 empty] | Warning
1305 | 14201 | Prot: 4th CT | Basic settings > Measurement setup > 4th CT protection > 4th CT input selector | 4th CT trip select | 4th CT selection of alarm type due to use of this input. | OFF |  |  |  | 0: OFF, 1: Mains/BB current, 2: Neutral current, 3: Earth fault current | [5 empty] | Warning
1079 | 14210 | Prot: 4th CT | Generator > Current protections > Neutral over-current (4th CT) | 4th CT In> 1 | 4th CT neutral current protection level 1 | 30 | 2 | 120 | % |  | 100 | 1 | 32000
1080 | 14220 | Prot: 4th CT | Generator > Current protections > Neutral over-current (4th CT) | 4th CT In> 2 | 4th CT neutral current protection level 2 | 30 | 2 | 120 | % |  | 100 | 1 | 32000
1081 | 14230 | Prot: 4th CT | Generator > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 1 | 4th CT earth fault current protection level 1 | 10 | 2 | 120 | % |  | 100 | 1 | 32000
1082 | 14240 | Prot: 4th CT | Generator > Current protections > Earth fault over-current (4th CT) | 4th CT Ie> 2 | 4th CT earth fault current protection level 2 | 10 | 2 | 120 | % |  | 100 | 1 | 32000
752 | 14250 | Prot: 4th CT | Mains > Protections > Busbar over-current protections (4th CT) | 4th CT I> 1 | 4th CT busbar current protection level 1 | 115 | 50 | 200 | % |  | 100 | 1 | 32000
753 | 14260 | Prot: 4th CT | Mains > Protections > Busbar over-current protections (4th CT) | 4th CT I> 2 | 4th CT busbar current protection level 2 | 120 | 50 | 200 | % |  | 100 | 1 | 32000
606 | 14270 | Prot: 4th CT | Mains > Protections > Power protections (4th CT) | 4th CT -P> 1 | 4th CT Reverse power protection level 1 | -5 | -200 | 0 | % |  | 100 | 1 | 1000
607 | 14280 | Prot: 4th CT | Mains > Protections > Power protections (4th CT) | 4th CT -P> 2 | 4th CT Reverse power protection level 2 | -5 | -200 | 0 | % |  | 100 | 1 | 1000
608 | 14290 | Prot: 4th CT | Mains > Protections > Power protections (4th CT) | 4th CT P> 1 | 4th CT overload protection level 1 | 100 | -200 | 200 | % |  | 100 | 1 | 32000
609 | 14300 | Prot: 4th CT | Mains > Protections > Power protections (4th CT) | 4th CT P> 2 | 4th CT overload protection level 2 | 110 | -200 | 200 | % |  | 50 | 1 | 32000