## Information
AGC 150 PMS lite M-Logic descriptions
Software version
The information contained in this spreadsheet (Revision A of document 4189341497) is applicable to software version 1.38.0 of AGC 150.
Monitoring M-Logic
You can use Modbus to see the state of each M-Logic line (function code 04, Modbus addresses 1150 to 1174).
More information
AGC 150 PMS lite Designer's handbook: This document has more information about some of the M-Logic functions.
Application notes, M-Logic AGC-4 Mk II: This document has a general introduction to M-Logic.
It also contains information and examples for generic M-Logic functions. You can download this document from:
https://www.deif.com/documentation/agc-4-mk-ii/
AGC 150 Modbus server tables: Some of the M-Logic functions are also available over Modbus.

## PMS_lite_M-Logic_Events
Category | Name | Options | From SW | To SW | The controller activates the event when …
PMS lite Event | Min number to run alarm |  |  |  | The Minimum number to run alarm is activated.
PMS lite Event | Min number of units alarm |  |  |  | The Minimum number of units alarm is activated.
PMS lite Event | Available power alarm |  |  |  | The Available power alarm is activated.
PMS lite Event | Next to start |  |  |  | The controller is the next to start its genset if this is required by PMS lite.
PMS lite Event | Next to stop |  |  |  | The controller is the next to stop its genset if this is required by PMS lite.
PMS lite Event | Multi start enabled |  |  |  | Multi start config (parameter 8521) is Enabled.
PMS lite Event | LDSS control active |  |  |  | The controller decides the load-dependent starts and stops, and PLC control is not active for the controller.
PMS lite Event | PLC control active |  |  |  | PLC control is active for the controller.
PMS lite Event | First priority |  |  |  | The controller's generator has first priority.
Alarms | Unacknowledged alarm(s) |  |  |  | One or more alarms are unacknowledged.
Alarms | Crank failure |  |  |  | There is a crank failure.
Alarms | Start failure failure |  |  |  | There is a start failure
Alarms | Phase seq. error GEN |  |  |  | A phase sequence error alarm is activated on the genset side of the GB.
Alarms | Phase seq. error BB |  |  |  | A phase sequence error alarm is activated on the busbar side of the GB.
Alarms | Mains sync. inhibit |  |  |  | Mains synchronisation is inhibited.
Alarms | M-Logic alarm 1 |  |  |  | M-Logic alarm 1 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 2 |  |  |  | M-Logic alarm 2 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 3 |  |  |  | M-Logic alarm 3 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 4 |  |  |  | M-Logic alarm 4 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 5 |  |  |  | M-Logic alarm 5 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 10 |  | 1180 |  | M-Logic alarm 10 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 11 |  | 1180 |  | M-Logic alarm 11 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 12 |  | 1180 |  | M-Logic alarm 12 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 13 |  | 1180 |  | M-Logic alarm 13 is activated (by the corresponding M-Logic output).
Alarms | M-Logic alarm 14 |  | 1180 |  | M-Logic alarm 14 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 1 |  | 1060 |  | M-Logic extended timer alarm 1 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 2 |  | 1060 |  | M-Logic extended timer alarm 2 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 3 |  | 1060 |  | M-Logic extended timer alarm 3 is activated (by the corresponding M-Logic output).
Alarms | M-Logic ext alarm 4 |  | 1060 |  | M-Logic extended timer alarm 4 is activated (by the corresponding M-Logic output).
Alarms - AC | BUS high-volt 1 |  |  |  | Busbar high voltage high alarm 1 is activated.
Alarms - AC | BUS high-volt 2 |  |  |  | Busbar high voltage high alarm 2 is activated.
Alarms - AC | BUS high-volt 3 |  |  |  | Busbar high voltage high alarm 3 is activated.
Alarms - AC | BUS low-volt 1 |  |  |  | Busbar voltage low alarm 1 is activated.
Alarms - AC | BUS low-volt 2 |  |  |  | Busbar voltage low alarm 2 is activated.
Alarms - AC | BUS low-volt 3 |  |  |  | Busbar voltage low alarm 3 is activated.
Alarms - AC | BUS low-volt 4 |  |  |  | Busbar voltage low alarm 4 is activated.
Alarms - AC | BUS high-freq 1 |  |  |  | Busbar frequency high alarm 1 is activated.
Alarms - AC | BUS high-freq 2 |  |  |  | Busbar frequency high alarm 2 is activated.
Alarms - AC | BUS high-freq 3 |  |  |  | Busbar frequency high alarm 3 is activated.
Alarms - AC | BUS high-freq 4 |  |  |  | Busbar frequency high alarm 4 is activated.
Alarms - AC | BUS low-freq 1 |  |  |  | Busbar frequency low alarm 1 is activated.
Alarms - AC | BUS low-freq 2 |  |  |  | Busbar frequency low alarm 2 is activated.
Alarms - AC | BUS low-freq 3 |  |  |  | Busbar frequency low alarm 3 is activated.
Alarms - AC | BUS low-freq 4 |  |  |  | Busbar frequency low alarm 4 is activated.
Alarms - AC | BUS low-freq 5 |  |  |  | Busbar frequency low alarm 5 is activated.
Alarms - AC | Over Current 1 |  |  |  | Generator current high alarm 1 is activated.
Alarms - AC | Over Current 2 |  |  |  | Generator current high alarm 2 is activated.
Alarms - AC | Over Current 3 |  |  |  | Generator current high alarm 3 is activated.
Alarms - AC | Over Current 4 |  |  |  | Generator current high alarm 4 is activated.
Alarms - AC | Volt dep Over Current |  |  |  | Generator voltage-dependent over-current alarm is activated.
Alarms - AC | Over load 1 |  |  |  | Generator active power alarm 1 is activated.
Alarms - AC | Over load 2 |  |  |  | Generator active power alarm 2 is activated.
Alarms - AC | Over load 3 |  |  |  | Generator active power alarm 3 is activated.
Alarms - AC | Over load 4 |  |  |  | Generator active power alarm 4 is activated.
Alarms - AC | Over load 5 |  |  |  | Generator active power alarm 5 is activated.
Alarms - AC | Reverse power 1 |  |  |  | Generator reverse power alarm 1 is activated.
Alarms - AC | Reverse power 2 |  |  |  | Generator reverse power alarm 2 is activated.
Alarms - AC | Reverse power 3 |  | 1070 |  | Generator reverse power alarm 3 is activated.
Alarms - AC | 4th CT Busbar Over Current 1 |  | 1120 |  | Busbar over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Busbar Over Current 2 |  | 1120 |  | Busbar over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Neutral Over Current 1 |  | 1200 |  | Neutral (N) over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Neutral Over Current 2 |  | 1200 |  | Neutral (N) over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Earth Over Current 1 |  | 1200 |  | Earth over-current alarm 1 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th CT Earth Over Current 2 |  | 1200 |  | Earth over-current alarm 2 (measured by the 4th current transformer) is activated.
Alarms - AC | 4th Over load 1 |  |  |  | 4th busbar current-based active power alarm 1 is activated.
Alarms - AC | 4th Over load 2 |  |  |  | 4th busbar current-based active power alarm 2 is activated.
Alarms - AC | 4th Reverse power 1 |  |  |  | 4th busbar current-based reverse power alarm 1 is activated.
Alarms - AC | 4th Reverse power 2 |  |  |  | 4th busbar current-based reverse power alarm 2 is activated.
Alarms - AC | Gen Unbalance current 1 |  |  |  | Generator unbalance current alarm 1 is activated.
Alarms - AC | Gen Unbalance current 2 |  |  |  | Generator unbalance current alarm 2 is activated.
Alarms - AC | Gen Unbalance voltage |  |  |  | Generator unbalance voltage alarm is activated.
Alarms - AC | Gen high-volt 1 |  |  |  | Generator voltage high alarm 1 is activated.
Alarms - AC | Gen high-volt 2 |  |  |  | Generator voltage high alarm 2 is activated.
Alarms - AC | Gen low-volt 1 |  |  |  | Generator voltage low alarm 1 is activated.
Alarms - AC | Gen low-volt 2 |  |  |  | Generator voltage low alarm 2 is activated.
Alarms - AC | Gen low-volt 3 |  |  |  | Generator voltage low alarm 3 is activated.
Alarms - AC | Gen high-freq 1 |  |  |  | Generator frequency high alarm 1 is activated.
Alarms - AC | Gen high-freq 2 |  |  |  | Generator frequency high alarm 2 is activated.
Alarms - AC | Gen high-freq 3 |  |  |  | Generator frequency high alarm 3 is activated.
Alarms - AC | Gen low-freq 1 |  |  |  | Generator frequency low alarm 1 is activated.
Alarms - AC | Gen low-freq 2 |  |  |  | Generator frequency low alarm 2 is activated.
Alarms - AC | Gen low-freq 3 |  |  |  | Generator frequency low alarm 3 is activated.
Alarms - AC | Fast over current 1 |  |  |  | Generator current fast high alarm 1 is activated.
Alarms - AC | Fast over current 2 |  |  |  | Generator current fast high alarm 2 is activated.
Alarms - AC | Var import |  |  |  | Generator reactive power import high alarm is activated.
Alarms - AC | Var export |  |  |  | Generator reactive power export high alarm is activated.
Alarms - AC | BB Unbalance U |  |  |  | Busbar unbalance voltage alarm is activated.
Alarms - Digital inputs | Emergency Stop |  |  |  | The emergency stop is active.
Alarms - Digital inputs | Digital input 20 |  |  |  | The alarm configured for digital input 20 is active.
Alarms - Digital inputs | Digital input 21 |  |  |  | The alarm configured for digital input 21 is active.
Alarms - Digital inputs | Digital input 22 |  |  |  | The alarm configured for digital input 22 is active.
Alarms - Digital inputs | Digital input 23 |  |  |  | The alarm configured for digital input 23 is active.
Alarms - Digital inputs | Digital input 39 |  |  |  | The alarm configured for digital input 39 is active.
Alarms - Digital inputs | Digital input 40 |  |  |  | The alarm configured for digital input 40 is active.
Alarms - Digital inputs | Digital input 41 |  |  |  | The alarm configured for digital input 41 is active.
Alarms - Digital inputs | Digital input 42 |  |  |  | The alarm configured for digital input 42 is active.
Alarms - Digital inputs | Digital input 43 |  |  |  | The alarm configured for digital input 43 is active.
Alarms - Digital inputs | Digital input 44 |  |  |  | The alarm configured for digital input 44 is active.
Alarms - Digital inputs | Digital input 45 |  |  |  | The alarm configured for digital input 45 is active.
Alarms - Digital inputs | Digital input 46 |  |  |  | The alarm configured for digital input 46 is active.
Alarms - Digital inputs | Digital input 47 |  |  |  | The alarm configured for digital input 47 is active.
Alarms - Digital inputs | Digital input 48 |  |  |  | The alarm configured for digital input 48 is active.
Alarms - Digital inputs | Digital input 49 |  |  |  | The alarm configured for digital input 49 is active.
Alarms - Digital inputs | Digital input 50 |  |  |  | The alarm configured for digital input 50 is active.
Alarms - Digital inputs | Digital input 20 wire fail |  |  |  | A wire failure was detected for digital input 20.
Alarms - Digital inputs | Digital input 21 wire fail |  |  |  | A wire failure was detected for digital input 21.
Alarms - Digital inputs | Digital input 22 wire fail |  |  |  | A wire failure was detected for digital input 22.
Alarms - Digital inputs | Digital input 23 wire fail |  |  |  | A wire failure was detected for digital input 23.
Alarms - Analogue inputs | Overspeed 2 |  |  |  | Overspeed 2 alarm is activated.
Alarms - Analogue inputs | Supply low terminal 1 |  |  |  | Low auxiliary supply voltage alarm.
Alarms - Analogue inputs | Supply High terminal 1 |  |  |  | High auxiliary supply voltage alarm.
Alarms - Analogue inputs | Multi input 20 1 |  |  |  | Alarm 1 for multi-input 20 is active.
Alarms - Analogue inputs | Multi input 21 1 |  |  |  | Alarm 1 for multi-input 21 is active.
Alarms - Analogue inputs | Multi input 22 1 |  |  |  | Alarm 1 for multi-input 22 is active.
Alarms - Analogue inputs | Multi input 23 1 |  |  |  | Alarm 1 for multi-input 23 is active.
Alarms - Analogue inputs | Multi input 20 2 |  |  |  | Alarm 2 for multi-input 20 is active.
Alarms - Analogue inputs | Multi input 21 2 |  |  |  | Alarm 2 for multi-input 21 is active.
Alarms - Analogue inputs | Multi input 22 2 |  |  |  | Alarm 2 for multi-input 22 is active.
Alarms - Analogue inputs | Multi input 23 2 |  |  |  | Alarm 2 for multi-input 23 is active.
Alarms - Analogue inputs | Analogue input 20 wire fail |  |  |  | A wire failure was detected for analogue input 20.
Alarms - Analogue inputs | Analogue input 21 wire fail |  |  |  | A wire failure was detected for analogue input 21.
Alarms - Analogue inputs | Analogue input 22 wire fail |  |  |  | A wire failure was detected for analogue input 22.
Alarms - Analogue inputs | Analogue input 23 wire fail |  |  |  | A wire failure was detected for analogue input 23.
Alarms - Analogue inputs | Delta analogue1 1 |  |  |  | Delta analogue1 1 (menu 4610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue1 2 |  |  |  | Delta analogue1 2 (menu 4620) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue2 1 |  |  |  | Delta analogue2 1 (menu 4630) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue2 2 |  |  |  | Delta analogue2 2 (menu 4640) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue3 1 |  |  |  | Delta analogue3 1 (menu 4650) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue3 2 |  |  |  | Delta analogue3 2 (menu 4660) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue4 1 |  |  |  | Delta analogue4 1 (menu 4680) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue4 2 |  |  |  | Delta analogue4 2 (menu 4690) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue5 1 |  |  |  | Delta analogue5 1 (menu 4700) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue5 2 |  |  |  | Delta analogue5 2 (menu 4710) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue6 1 |  |  |  | Delta analogue6 1 (menu 4720) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Analogue inputs | Delta analogue6 2 |  |  |  | Delta analogue6 2 (menu 4730) outputs A and/or B are set to Limits, and the alarm conditions are met.
Alarms - Breakers | GB open failure |  |  |  | GB open failure alarm is activated.
Alarms - Breakers | GB close failure |  |  |  | GB close failure alarm is activated.
Alarms - Breakers | GB pos. failure |  |  |  | GB position failure alarm is activated.
Alarms - Breakers | GB sync. failure |  |  |  | GB synchronisation failure alarm is activated.
Alarms - Breakers | MB open failure |  |  |  | MB open failure alarm is activated.
Alarms - Breakers | MB close failure |  |  |  | MB close failure alarm is activated.
Alarms - Breakers | MB pos. failure |  |  |  | MB position failure alarm is activated.
Alarms - Breakers | MB sync. failure |  |  |  | MB synchronisation failure alarm is activated.
Alarms - Breakers | GB Ext. Tripped |  |  |  | GB externally tripped alarm is activated.
Alarms - Breakers | MB Ext. Tripped |  |  |  | MB externally tripped alarm is activated.
Alarms - IOM and DAVR and CANShare | DAVR comm. error |  |  |  | DAVR communication error alarm is activated.
Alarms - IOM and DAVR and CANShare | DAVR Warning |  |  |  | DAVR warning alarm is activated.
Alarms - IOM and DAVR and CANShare | DAVR Trip |  |  |  | DAVR trip alarm is activated.
Alarms - IOM and DAVR and CANShare | CANShare failure |  |  |  | CANshare failure alarm is activated.
Alarms - IOM and DAVR and CANShare | IOM Comm. error |  |  |  | IOM communication error alarm is activated.
Alarms - EIC | EIC Comm. error |  |  |  | EIC communication error alarm is activated.
Alarms - EIC | EIC Warning |  |  |  | EIC warning alarm is activated.
Alarms - EIC | EIC Shutdown |  |  |  | EIC shutdown alarm is activated.
Alarms - EIC | EIC Overspeed |  |  |  | EIC overspeed alarm is activated.
Alarms - EIC | EIC Coolant Temp 1 |  |  |  | EIC cooling water temperature alarm is activated.
Alarms - EIC | EIC Coolant Temp 2 |  |  |  | EIC cooling water temperature alarm is activated.
Alarms - EIC | EIC Oil pressure 1 |  |  |  | EIC oil pressure alarm 1 is activated.
Alarms - EIC | EIC Oil pressure 2 |  |  |  | EIC oil pressure alarm 2 is activated.
Alarms - EIC | EIC Oil temperature 1 |  |  |  | EIC oil temperature alarm 1 is activated.
Alarms - EIC | EIC Oil temperature 2 |  |  |  | EIC oil temperature alarm 2 is activated.
Alarms - EIC | EIC Coolant Level 1 |  |  |  | EIC coolant level alarm 1 is activated.
Alarms - EIC | EIC Coolant Level 2 |  |  |  | EIC coolant level alarm 2 is activated.
Alarms - EIC | EIC Cylinder exhaust diff. temp. 1 |  |  |  | EIC cylinder exhaust differential temperature alarm 1 is activated.
Alarms - EIC | EIC Cylinder exhaust diff. temp. 2 |  |  |  | EIC cylinder exhaust differential temperature alarm 2 is activated.
Alarms - EIC | EIC high SOOT warning |  | 1020 |  | EIC high soot warning alarm is activated.
Alarms - EIC | EIC high SOOT shutdown |  | 1020 |  | EIC high soot shutdown alarm is activated.
Alarms - EIC | EIC Protection |  | 1160 |  | EIC protection alarm is activated.
Alarms - EIC | EIC Malfunction |  | 1160 |  | EIC malfunction alarm is activated.
Alarms - 3rd party loadshare | 3rd party LS - units missing |  |  |  | The number of detected units is dropping.
Alarms - 3rd party loadshare | 3rd party LS - error |  |  |  | Protocol error detected. See the event log for more info.
CIO Alarms | CIO 116 No. 1 In. 10 |  |  |  | CIO 116 No. 1 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 11 |  |  |  | CIO 116 No. 1 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 12 |  |  |  | CIO 116 No. 1 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 13 |  |  |  | CIO 116 No. 1 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 14 |  |  |  | CIO 116 No. 1 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 15 |  |  |  | CIO 116 No. 1 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 16 |  |  |  | CIO 116 No. 1 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 17 |  |  |  | CIO 116 No. 1 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 19 |  |  |  | CIO 116 No. 1 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 20 |  |  |  | CIO 116 No. 1 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 21 |  |  |  | CIO 116 No. 1 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 22 |  |  |  | CIO 116 No. 1 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 23 |  |  |  | CIO 116 No. 1 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 24 |  |  |  | CIO 116 No. 1 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 25 |  |  |  | CIO 116 No. 1 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 1 In. 26 |  |  |  | CIO 116 No. 1 In. 26 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 10 |  |  |  | CIO 116 No. 2 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 11 |  |  |  | CIO 116 No. 2 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 12 |  |  |  | CIO 116 No. 2 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 13 |  |  |  | CIO 116 No. 2 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 14 |  |  |  | CIO 116 No. 2 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 15 |  |  |  | CIO 116 No. 2 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 16 |  |  |  | CIO 116 No. 2 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 17 |  |  |  | CIO 116 No. 2 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 19 |  |  |  | CIO 116 No. 2 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 20 |  |  |  | CIO 116 No. 2 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 21 |  |  |  | CIO 116 No. 2 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 22 |  |  |  | CIO 116 No. 2 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 23 |  |  |  | CIO 116 No. 2 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 24 |  |  |  | CIO 116 No. 2 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 25 |  |  |  | CIO 116 No. 2 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 2 In. 26 |  |  |  | CIO 116 No. 2 In. 26 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 10 |  |  |  | CIO 116 No. 3 In. 10 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 11 |  |  |  | CIO 116 No. 3 In. 11 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 12 |  |  |  | CIO 116 No. 3 In. 12 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 13 |  |  |  | CIO 116 No. 3 In. 13 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 14 |  |  |  | CIO 116 No. 3 In. 14 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 15 |  |  |  | CIO 116 No. 3 In. 15 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 16 |  |  |  | CIO 116 No. 3 In. 16 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 17 |  |  |  | CIO 116 No. 3 In. 17 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 19 |  |  |  | CIO 116 No. 3 In. 19 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 20 |  |  |  | CIO 116 No. 3 In. 20 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 21 |  |  |  | CIO 116 No. 3 In. 21 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 22 |  |  |  | CIO 116 No. 3 In. 22 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 23 |  |  |  | CIO 116 No. 3 In. 23 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 24 |  |  |  | CIO 116 No. 3 In. 24 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 25 |  |  |  | CIO 116 No. 3 In. 25 alarm is active.
CIO Alarms | CIO 116 No. 3 In. 26 |  |  |  | CIO 116 No. 3 In. 26 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8.1 |  |  |  | CIO 308 No. 1 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8.2 |  |  |  | CIO 308 No. 1 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 11.1 |  |  |  | CIO 308 No. 1 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 11.2 |  |  |  | CIO 308 No. 1 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 14.1 |  |  |  | CIO 308 No. 1 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 14.2 |  |  |  | CIO 308 No. 1 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 17.1 |  |  |  | CIO 308 No. 1 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 17.2 |  |  |  | CIO 308 No. 1 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 20.1 |  |  |  | CIO 308 No. 1 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 20.2 |  |  |  | CIO 308 No. 1 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 23.1 |  |  |  | CIO 308 No. 1 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 23.2 |  |  |  | CIO 308 No. 1 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 26.1 |  |  |  | CIO 308 No. 1 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 26.2 |  |  |  | CIO 308 No. 1 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 29.1 |  |  |  | CIO 308 No. 1 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 29.2 |  |  |  | CIO 308 No. 1 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 8.1 |  |  |  | CIO 308 No. 2 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 8.2 |  |  |  | CIO 308 No. 2 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 11.1 |  |  |  | CIO 308 No. 2 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 11.2 |  |  |  | CIO 308 No. 2 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 14.1 |  |  |  | CIO 308 No. 2 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 14.2 |  |  |  | CIO 308 No. 2 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 17.1 |  |  |  | CIO 308 No. 2 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 17.2 |  |  |  | CIO 308 No. 2 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 20.1 |  |  |  | CIO 308 No. 2 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 20.2 |  |  |  | CIO 308 No. 2 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 23.1 |  |  |  | CIO 308 No. 2 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 23.2 |  |  |  | CIO 308 No. 2 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 26.1 |  |  |  | CIO 308 No. 2 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 26.2 |  |  |  | CIO 308 No. 2 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 29.1 |  |  |  | CIO 308 No. 2 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 2 In. 29.2 |  |  |  | CIO 308 No. 2 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 8.1 |  |  |  | CIO 308 No. 3 In. 8.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 8.2 |  |  |  | CIO 308 No. 3 In. 8.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 11.1 |  |  |  | CIO 308 No. 3 In. 11.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 11.2 |  |  |  | CIO 308 No. 3 In. 11.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 14.1 |  |  |  | CIO 308 No. 3 In. 14.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 14.2 |  |  |  | CIO 308 No. 3 In. 14.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 17.1 |  |  |  | CIO 308 No. 3 In. 17.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 17.2 |  |  |  | CIO 308 No. 3 In. 17.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 20.1 |  |  |  | CIO 308 No. 3 In. 20.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 20.2 |  |  |  | CIO 308 No. 3 In. 20.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 23.1 |  |  |  | CIO 308 No. 3 In. 23.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 23.2 |  |  |  | CIO 308 No. 3 In. 23.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 26.1 |  |  |  | CIO 308 No. 3 In. 26.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 26.2 |  |  |  | CIO 308 No. 3 In. 26.2 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 29.1 |  |  |  | CIO 308 No. 3 In. 29.1 alarm is active.
CIO Alarms | CIO 308 No. 3 In. 29.2 |  |  |  | CIO 308 No. 3 In. 29.2 alarm is active.
CIO Alarms | CIO 308 No. 1 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 8.
CIO Alarms | CIO 308 No. 1 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 11.
CIO Alarms | CIO 308 No. 1 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 14.
CIO Alarms | CIO 308 No. 1 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 17.
CIO Alarms | CIO 308 No. 1 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 20.
CIO Alarms | CIO 308 No. 1 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 23.
CIO Alarms | CIO 308 No. 1 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 26.
CIO Alarms | CIO 308 No. 1 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 29.
CIO Alarms | CIO 308 No. 2 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 8.
CIO Alarms | CIO 308 No. 2 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 11.
CIO Alarms | CIO 308 No. 2 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 14.
CIO Alarms | CIO 308 No. 2 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 17.
CIO Alarms | CIO 308 No. 2 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 20.
CIO Alarms | CIO 308 No. 2 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 23.
CIO Alarms | CIO 308 No. 2 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 26.
CIO Alarms | CIO 308 No. 2 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 29.
CIO Alarms | CIO 308 No. 3 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 8.
CIO Alarms | CIO 308 No. 3 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 11.
CIO Alarms | CIO 308 No. 3 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 14.
CIO Alarms | CIO 308 No. 3 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 17.
CIO Alarms | CIO 308 No. 3 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 20.
CIO Alarms | CIO 308 No. 3 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 23.
CIO Alarms | CIO 308 No. 3 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 26.
CIO Alarms | CIO 308 No. 3 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 29.
CIO Alarms | CIO 116 No. 1 module missing |  |  |  | The controller cannot communicate with CIO 116 No. 1.
CIO Alarms | CIO 116 No. 2 module missing |  |  |  | The controller cannot communicate with CIO 116 No. 2.
CIO Alarms | CIO 116 No. 3 module missing |  |  |  | The controller cannot communicate with CIO 116 No. 3.
CIO Alarms | CIO 208 No. 1 module missing |  |  |  | The controller cannot communicate with CIO 208 No. 1.
CIO Alarms | CIO 208 No. 2 module missing |  |  |  | The controller cannot communicate with CIO 208 No. 2.
CIO Alarms | CIO 208 No. 3 module missing |  |  |  | The controller cannot communicate with CIO 208 No. 3.
CIO Alarms | CIO 308 No. 1 module missing |  |  |  | The controller cannot communicate with CIO 308 No. 1.
CIO Alarms | CIO 308 No. 2 module missing |  |  |  | The controller cannot communicate with CIO 308 No. 2.
CIO Alarms | CIO 308 No. 3 module missing |  |  |  | The controller cannot communicate with CIO 308 No. 3.
Limits | BUS high-volt 1 |  |  |  | Busbar over-voltage alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-volt 2 |  |  |  | Busbar over-voltage alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-volt 3 |  |  |  | Busbar over-voltage alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-volt 1 |  |  |  | Busbar under-voltage alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-volt 2 |  |  |  | Busbar under-voltage alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-volt 3 |  |  |  | Busbar under-voltage alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-volt 4 |  |  |  | Busbar under-voltage alarm 4 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-freq 1 |  |  |  | Busbar high frequency alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-freq 2 |  |  |  | Busbar high frequency alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-freq 3 |  |  |  | Busbar high frequency alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS high-freq 4 |  |  |  | Busbar high frequency alarm 4 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-freq 1 |  |  |  | Busbar low frequency alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-freq 2 |  |  |  | Busbar low frequency alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-freq 3 |  |  |  | Busbar low frequency alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-freq 4 |  |  |  | Busbar low frequency alarm 4 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | BUS low-freq 5 |  |  |  | Busbar low frequency alarm 5 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over Current 1 |  |  |  | Over-current alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over Current 2 |  |  |  | Over-current alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over Current 3 |  |  |  | Over-current alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over Current 4 |  |  |  | Over-current alarm 4 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Busbar Over Current 1 |  | 1120 |  | Busbar over-current 1 (menu 14250) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Busbar Over Current 2 |  | 1120 |  | Busbar over-current 2 (menu 14260) (measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Neutral Over Current 1 |  | 1200 |  | Neutral over-current 1 (menu 14210) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Neutral Over Current 2 |  | 1200 |  | Neutral over-current 2 (menu 14220) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Earth Over Current 1 |  | 1200 |  | Earth over-current 1 (menu 14230) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Earth Over Current 2 |  | 1200 |  | Earth over-current 2 (menu 14240) (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over load 1 |  |  |  | Overload alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over load 2 |  |  |  | Overload alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over load 3 |  |  |  | Overload alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over load 4 |  |  |  | Overload alarm 4 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Over load 5 |  |  |  | Overload alarm 5 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Reverse power 1 |  |  |  | Reverse power alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Reverse power 2 |  |  |  | Reverse power alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Reverse power 3 |  | 1070 |  | Reverse power alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Over load 1 |  |  |  | Overload alarm 1 (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Over load 2 |  |  |  | Overload alarm 2 (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Reverse power 1 |  |  |  | Reverse power alarm 1 (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | 4th Reverse power 2 |  |  |  | Reverse power alarm 2 (as measured by the 4th current transformer) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen high-volt 1 |  |  |  | Generator over-voltage alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen high-volt 2 |  |  |  | Generator over-voltage alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-volt 1 |  |  |  | Generator under-voltage alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-volt 2 |  |  |  | Generator under-voltage alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-volt 3 |  |  |  | Generator under-voltage alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen high-freq 1 |  |  |  | Generator high frequency alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen high-freq 2 |  |  |  | Generator high frequency alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen high-freq 3 |  |  |  | Generator high frequency alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-freq 1 |  |  |  | Generator low frequency alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-freq 2 |  |  |  | Generator low frequency alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Gen low-freq 3 |  |  |  | Generator low frequency alarm 3 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 39 |  |  |  | Digital input 39 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 40 |  |  |  | Digital input 40 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 41 |  |  |  | Digital input 41 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 42 |  |  |  | Digital input 42 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 43 |  |  |  | Digital input 43 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 44 |  |  |  | Digital input 44 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 45 |  |  |  | Digital input 45 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 46 |  |  |  | Digital input 46 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 47 |  |  |  | Digital input 47 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 48 |  |  |  | Digital input 48 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 49 |  |  |  | Digital input 49 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Digital input 50 |  |  |  | Digital input 50 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 1 |  |  |  | Multi-input 20 alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 1 |  |  |  | Multi-input 21 alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 1 |  |  |  | Multi-input 22 alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 1 |  |  |  | Multi-input 23 alarm 1 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 2 |  |  |  | Multi-input 20 alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 2 |  |  |  | Multi-input 21 alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 2 |  |  |  | Multi-input 22 alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 2 |  |  |  | Multi-input 23 alarm 2 outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 20 wirefail |  |  |  | Multi-input 20 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 21 wirefail |  |  |  | Multi-input 21 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 22 wirefail |  |  |  | Multi-input 22 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Multi input 23 wirefail |  |  |  | Multi-input 23 wire break detection outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue1 1 |  |  |  | Delta analogue1 1 (menu 4610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue1 2 |  |  |  | Delta analogue1 2 (menu 4620) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue2 1 |  |  |  | Delta analogue2 1 (menu 4630) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue2 2 |  |  |  | Delta analogue2 2 (menu 4640) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue3 1 |  |  |  | Delta analogue3 1 (menu 4650) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue3 2 |  |  |  | Delta analogue3 2 (menu 4660) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue4 1 |  |  |  | Delta analogue4 1 (menu 4680) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue4 2 |  |  |  | Delta analogue4 2 (menu 4690) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue5 1 |  |  |  | Delta analogue5 1 (menu 4700) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue5 2 |  |  |  | Delta analogue5 2 (menu 4710) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue6 1 |  |  |  | Delta analogue6 1 (menu 4720) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | Delta analogue6 2 |  |  |  | Delta analogue6 2 (menu 4730) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 1 |  |  |  | M-Logic alarm 1 (menu 3570) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 2 |  |  |  | M-Logic alarm 2 (menu 3580) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 3 |  |  |  | M-Logic alarm 3 (menu 3590) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 4 |  |  |  | M-Logic alarm 4 (menu 3600) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 5 |  |  |  | M-Logic alarm 5 (menu 3610) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 10 |  | 1180 |  | M-Logic alarm 10 (menu 3660) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 11 |  | 1180 |  | M-Logic alarm 11 (menu 3670) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 12 |  | 1180 |  | M-Logic alarm 12 (menu 3680) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 13 |  | 1180 |  | M-Logic alarm 13 (menu 3690) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic alarm 14 |  | 1180 |  | M-Logic alarm 14 (menu 3700) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | GB sync. failure |  |  |  | GB synchronisation failure outputs A and/or B are set to Limits, and the alarm is activated.
Limits | MB sync. failure |  |  |  | MB synchronisation failure outputs A and/or B are set to Limits, and the alarm is activated.
Limits | BB meas failure |  |  |  | BB measurement failure outputs A and/or B are set to Limits, and the alarm is activated.
Limits | M-Logic ext alarm 1 |  | 1061 |  | M-Logic ext alarm 1 (menu 3621) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 2 |  | 1061 |  | M-Logic ext alarm 2 (menu 3631) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 3 |  | 1061 |  | M-Logic ext alarm 3 (menu 3641) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | M-Logic ext alarm 4 |  | 1061 |  | M-Logic ext alarm 4 (menu 3651) outputs A and/or B are set to Limits, and the alarm conditions are met.
Limits | EIC High SOOT warning |  | 1020 |  | EIC high soot warning outputs A and/or B are set to Limits, and the alarm is active.
Limits | EIC High SOOT shutdown |  | 1020 |  | EIC high soot shutdown outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 10 |  |  |  | CIO 116 No. 1 In. 10 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 11 |  |  |  | CIO 116 No. 1 In. 11 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 12 |  |  |  | CIO 116 No. 1 In. 12 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 13 |  |  |  | CIO 116 No. 1 In. 13 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 14 |  |  |  | CIO 116 No. 1 In. 14 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 15 |  |  |  | CIO 116 No. 1 In. 15 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 16 |  |  |  | CIO 116 No. 1 In. 16 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 17 |  |  |  | CIO 116 No. 1 In. 17 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 19 |  |  |  | CIO 116 No. 1 In. 19 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 20 |  |  |  | CIO 116 No. 1 In. 20 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 21 |  |  |  | CIO 116 No. 1 In. 21 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 22 |  |  |  | CIO 116 No. 1 In. 22 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 23 |  |  |  | CIO 116 No. 1 In. 23 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 24 |  |  |  | CIO 116 No. 1 In. 24 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 25 |  |  |  | CIO 116 No. 1 In. 25 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 1 In. 26 |  |  |  | CIO 116 No. 1 In. 26 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 10 |  |  |  | CIO 116 No. 2 In. 10 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 11 |  |  |  | CIO 116 No. 2 In. 11 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 12 |  |  |  | CIO 116 No. 2 In. 12 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 13 |  |  |  | CIO 116 No. 2 In. 13 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 14 |  |  |  | CIO 116 No. 2 In. 14 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 15 |  |  |  | CIO 116 No. 2 In. 15 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 16 |  |  |  | CIO 116 No. 2 In. 16 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 17 |  |  |  | CIO 116 No. 2 In. 17 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 19 |  |  |  | CIO 116 No. 2 In. 19 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 20 |  |  |  | CIO 116 No. 2 In. 20 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 21 |  |  |  | CIO 116 No. 2 In. 21 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 22 |  |  |  | CIO 116 No. 2 In. 22 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 23 |  |  |  | CIO 116 No. 2 In. 23 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 24 |  |  |  | CIO 116 No. 2 In. 24 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 25 |  |  |  | CIO 116 No. 2 In. 25 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 2 In. 26 |  |  |  | CIO 116 No. 2 In. 26 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 10 |  |  |  | CIO 116 No. 3 In. 10 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 11 |  |  |  | CIO 116 No. 3 In. 11 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 12 |  |  |  | CIO 116 No. 3 In. 12 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 13 |  |  |  | CIO 116 No. 3 In. 13 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 14 |  |  |  | CIO 116 No. 3 In. 14 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 15 |  |  |  | CIO 116 No. 3 In. 15 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 16 |  |  |  | CIO 116 No. 3 In. 16 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 17 |  |  |  | CIO 116 No. 3 In. 17 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 19 |  |  |  | CIO 116 No. 3 In. 19 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 20 |  |  |  | CIO 116 No. 3 In. 20 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 21 |  |  |  | CIO 116 No. 3 In. 21 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 22 |  |  |  | CIO 116 No. 3 In. 22 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 23 |  |  |  | CIO 116 No. 3 In. 23 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 24 |  |  |  | CIO 116 No. 3 In. 24 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 25 |  |  |  | CIO 116 No. 3 In. 25 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 116 No. 3 In. 26 |  |  |  | CIO 116 No. 3 In. 26 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 8.1 |  |  |  | CIO 308 No. 1 In. 8.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 8.2 |  |  |  | CIO 308 No. 1 In. 8.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 11.1 |  |  |  | CIO 308 No. 1 In. 11.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 11.2 |  |  |  | CIO 308 No. 1 In. 11.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 14.1 |  |  |  | CIO 308 No. 1 In. 14.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 14.2 |  |  |  | CIO 308 No. 1 In. 14.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 17.1 |  |  |  | CIO 308 No. 1 In. 17.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 17.2 |  |  |  | CIO 308 No. 1 In. 17.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 20.1 |  |  |  | CIO 308 No. 1 In. 20.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 20.2 |  |  |  | CIO 308 No. 1 In. 20.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 23.1 |  |  |  | CIO 308 No. 1 In. 23.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 23.2 |  |  |  | CIO 308 No. 1 In. 23.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 26.1 |  |  |  | CIO 308 No. 1 In. 26.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 26.2 |  |  |  | CIO 308 No. 1 In. 26.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 29.1 |  |  |  | CIO 308 No. 1 In. 29.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 29.2 |  |  |  | CIO 308 No. 1 In. 29.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 8.1 |  |  |  | CIO 308 No. 2 In. 8.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 8.2 |  |  |  | CIO 308 No. 2 In. 8.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 11.1 |  |  |  | CIO 308 No. 2 In. 11.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 11.2 |  |  |  | CIO 308 No. 2 In. 11.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 14.1 |  |  |  | CIO 308 No. 2 In. 14.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 14.2 |  |  |  | CIO 308 No. 2 In. 14.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 17.1 |  |  |  | CIO 308 No. 2 In. 17.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 17.2 |  |  |  | CIO 308 No. 2 In. 17.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 20.1 |  |  |  | CIO 308 No. 2 In. 20.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 20.2 |  |  |  | CIO 308 No. 2 In. 20.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 23.1 |  |  |  | CIO 308 No. 2 In. 23.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 23.2 |  |  |  | CIO 308 No. 2 In. 23.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 26.1 |  |  |  | CIO 308 No. 2 In. 26.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 26.2 |  |  |  | CIO 308 No. 2 In. 26.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 29.1 |  |  |  | CIO 308 No. 2 In. 29.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 2 In. 29.2 |  |  |  | CIO 308 No. 2 In. 29.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 8.1 |  |  |  | CIO 308 No. 3 In. 8.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 8.2 |  |  |  | CIO 308 No. 3 In. 8.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 11.1 |  |  |  | CIO 308 No. 3 In. 11.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 11.2 |  |  |  | CIO 308 No. 3 In. 11.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 14.1 |  |  |  | CIO 308 No. 3 In. 14.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 14.2 |  |  |  | CIO 308 No. 3 In. 14.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 17.1 |  |  |  | CIO 308 No. 3 In. 17.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 17.2 |  |  |  | CIO 308 No. 3 In. 17.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 20.1 |  |  |  | CIO 308 No. 3 In. 20.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 20.2 |  |  |  | CIO 308 No. 3 In. 20.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 23.1 |  |  |  | CIO 308 No. 3 In. 23.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 23.2 |  |  |  | CIO 308 No. 3 In. 23.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 26.1 |  |  |  | CIO 308 No. 3 In. 26.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 26.2 |  |  |  | CIO 308 No. 3 In. 26.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 29.1 |  |  |  | CIO 308 No. 3 In. 29.1 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 3 In. 29.2 |  |  |  | CIO 308 No. 3 In. 29.2 outputs A and/or B are set to Limits, and the alarm is active.
CIO Limits | CIO 308 No. 1 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 8.
CIO Limits | CIO 308 No. 1 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 11.
CIO Limits | CIO 308 No. 1 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 14.
CIO Limits | CIO 308 No. 1 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 17.
CIO Limits | CIO 308 No. 1 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 20.
CIO Limits | CIO 308 No. 1 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 23.
CIO Limits | CIO 308 No. 1 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 26.
CIO Limits | CIO 308 No. 1 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 1 In. 29.
CIO Limits | CIO 308 No. 2 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 8.
CIO Limits | CIO 308 No. 2 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 11.
CIO Limits | CIO 308 No. 2 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 14.
CIO Limits | CIO 308 No. 2 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 17.
CIO Limits | CIO 308 No. 2 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 20.
CIO Limits | CIO 308 No. 2 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 23.
CIO Limits | CIO 308 No. 2 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 26.
CIO Limits | CIO 308 No. 2 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 2 In. 29.
CIO Limits | CIO 308 No. 3 In. 8 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 8.
CIO Limits | CIO 308 No. 3 In. 11 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 11.
CIO Limits | CIO 308 No. 3 In. 14 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 14.
CIO Limits | CIO 308 No. 3 In. 17 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 17.
CIO Limits | CIO 308 No. 3 In. 20 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 20.
CIO Limits | CIO 308 No. 3 In. 23 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 23.
CIO Limits | CIO 308 No. 3 In. 26 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 26.
CIO Limits | CIO 308 No. 3 In. 29 wire fail |  |  |  | A wire failure was detected for CIO 308 No. 3 In. 29.
Events | Mains-Fail |  |  |  | There is an active mains failure.
Events | Peak shaving active |  |  |  | Peak sharing is active.
Events | G volt/freq Ok delay expired |  |  |  | The generator voltage and frequency OK timer has run out.
Events | Access lock |  |  |  | The access lock is active.
Events | Lamp test |  |  |  | The lamp test is active.
Events | Battery test active |  |  |  | The battery test is active.
Events | Shutdown override active |  | 1050 |  | Shutdown override is active.
Events | Test type simple selected |  |  |  | The simple test is selected.
Events | Test type load selected |  |  |  | The load test is selected.
Events | Test type full selected |  |  |  | The full test is selected.
Events | BB voltage ok |  |  |  | The voltage and frequency of the busbar are within the limits configured in parameters 2111 to 2114.
Events | G volt/freq Ok |  |  |  | The voltage and frequency of the generator are within the configured limits.
Events | Ack all alarms active |  |  |  | The controller acknowledges all alarms.
Events | Modeshift activated |  |  |  | Mode shift is activated.
Events | Modeshift deactivated |  |  |  | Mode shift is deactivated.
Events | Gov up pulse activated |  |  |  | The governor up pulse is activated.
Events | Gov down pulse activated |  |  |  | The governor down pulse is activated.
Events | AVR up pulse activated |  |  |  | The AVR up pulse is activated.
Events | AVR down pulse activated |  |  |  | The AVR down pulse is activated.
Events | Inductive reference selected |  |  |  | An inductive reference is selected.
Events | Capacitive reference selected |  |  |  | A capacitive reference is selected.
Events | Power offset 1 activated |  |  |  | Power offset 1 is activated.
Events | Power offset 2 activated |  |  |  | Power offset 2 is activated.
Events | Power offset 3 activated |  |  |  | Power offset 3 is activated.
Events | Cosphi offset 1 activated |  |  |  | Cosphi offset 1 is activated.
Events | Cosphi offset 2 activated |  |  |  | Cosphi offset 2 is activated.
Events | Cosphi offset 3 activated |  |  |  | Cosphi offset 3 is activated.
Events | Analogue offset set 1 active |  |  |  | The controller is using the analogue offset from set 1 of the nominal settings.
Events | Analogue offset set 2 active |  |  |  | The controller is using the analogue offset from set 2 of the nominal settings.
Events | Analogue offset set 3 active |  |  |  | The controller is using the analogue offset from set 3 of the nominal settings.
Events | Analogue offset set 4 active |  |  |  | The controller is using the analogue offset from set 4 of the nominal settings.
Events | Analogue offset set 5 active |  | 1210 |  | The controller is using the analogue offset from set 5 of the nominal settings.
Events | Analogue offset set 6 active |  | 1210 |  | The controller is using the analogue offset from set 6 of the nominal settings.
Events | Max ventilation activated |  |  |  | Maximum ventilation is activated.
Events | Max ventilation deactivated |  |  |  | Maximum ventilation is deactivated.
Events | Deload active |  |  |  | Deload is active.
Events | Power droop active |  |  |  | Power droop is active.
Events | Q droop active |  |  |  | Reactive power droop is active.
Events | Cosphi droop active |  |  |  | Cos phi droop is active.
Events | Any alarm active |  | 1190 |  | At least one alarm is active.
Events AC | Three phase system |  |  |  | The AC measurement setup is configured as a three-phase system.
Events AC | Split L1L3 phase system |  |  |  | The AC measurement setup is split-phase (L1-L3).
Events AC | Split L1L2 phase system |  |  |  | The AC measurement setup is split-phase (L1-L2).
Events AC | Single phase system |  |  |  | The AC measurement setup is single-phase.
Events AC | 60Hz system |  |  |  | The system has a nominal frequency of 60 Hz.
Events AC | L1L2L3 phase rotation active |  |  |  | The phase rotation used by the controller is L1L2L3.
Events AC | L1L3L2 phase rotation active |  |  |  | The phase rotation used by the controller is L1L3L2.
Events Parameter set | Parameter set 1 used |  |  |  | The controller is using nominal parameter set 1.
Events Parameter set | Parameter set 2 used |  |  |  | The controller is using nominal parameter set 2.
Events Parameter set | Parameter set 3 used |  |  |  | The controller is using nominal parameter set 3.
Events Parameter set | Parameter set 4 used |  |  |  | The controller is using nominal parameter set 4.
Events Parameter set | Parameter set 5 used |  | 1210 |  | The controller is using nominal parameter set 5.
Events Parameter set | Parameter set 6 used |  | 1210 |  | The controller is using nominal parameter set 6.
Events Parameter set | BB Parameter set 1 used |  |  |  | The controller is using busbar parameter set 1.
Events Parameter set | BB Parameter set 2 used |  |  |  | The controller is using busbar parameter set 2.
Events Parameter set | BB Unom = Gen Unom used |  |  |  | The busbar nominal voltage is equal to the generator nominal voltage.
Events Engine | Running |  |  |  | The engine is running.
Events Engine | Emergency stop |  |  |  | The emergency stop is active.
Events Engine | Gen ready for auto start |  |  |  | The generator is ready for an automatic start.
Events Engine | Cranking |  |  |  | The engine crank is active.
Events Engine | Start activated |  |  |  | The engine start is activated.
Events Engine | Cool down active |  |  |  | The engine cool down is activated.
Events Engine | Eng. heater in manual ctrl. |  |  |  | The engine heater is under manual control.
Events Engine | Alternative start activated |  |  |  | The engine alternative start is activated.
Events Engine | Idle run activated |  |  |  | The engine idle run is activated.
Events Engine | Idle run deactivated |  |  |  | The engine idle run is deactivated.
Events Breakers | MB-Closed |  |  |  | The mains breaker is closed.
Events Breakers | MB-Opened |  |  |  | The mains breaker is opened.
Events Breakers | GB-Closed |  |  |  | The generator breaker is closed.
Events Breakers | GB-Opened |  |  |  | The generator breaker is opened.
Events Breakers | GB synchronising |  |  |  | The generator breaker is synchronising.
Events Breakers | MB synchronising |  |  |  | The mains breaker is synchronising.
Events Breakers | GB direct in |  |  |  | The GB is being closed on a dead busbar.
Events Breakers | GB Black close request |  |  |  | There is a generator breaker black close request.
Events Breakers | Dynamic sync selected |  |  |  | Dynamic synchronisation is selected.
Events Breakers | Static sync selected |  |  |  | Static synchronisation is selected.
Events Breakers | MB synchronisation to Gen activated |  |  |  | Mains breaker synchronisation to the generator is activated.
Events Breakers | MB synchronisation to Gen deactivated |  |  |  | Mains breaker synchronisation to the generator is deactivated.
Events Breakers | GB synchronisation to mains activated |  |  |  | Generator breaker synchronisation to the generator is activated.
Events Breakers | GB synchronisation to mains deactivated |  |  |  | Generator breaker synchronisation to the generator is deactivated.
Events Breakers | Mains sync. inhibit activated |  |  |  | The mains synchronisation inhibit is activated.
Events Breakers | Mains sync. inhibited |  |  |  | The mains synchronisation is inhibited.
Events Plant | Test application selected with output cmd enabled |  |  |  | A test application is selected with output command enabled.
Events Plant | Test application selected with output cmd disabled |  |  |  | A test application is selected with output command disabled.
Cmd Timers | Cmd timer 01 active |  |  |  | Command timer 1 (parameters 6951, and 6961 to 6966) is active.
Cmd Timers | Cmd timer 02 active |  |  |  | Command timer 2 (parameters 6952, and 6971 to 6976) is active.
Cmd Timers | Cmd timer 03 active |  |  |  | Command timer 3 (parameters 6953, and 6981 to 6986) is active.
Cmd Timers | Cmd timer 04 active |  |  |  | Command timer 4 (parameters 6954, and 6991 to 6996) is active.
Cmd Timers | Any Cmd timer active |  |  |  | Any command timer (1 to 4) is active.
Cmd Schedulers | Cmd Scheduler 1 active |  |  |  | Scheduler 1 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 2 active |  |  |  | Scheduler 2 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 3 active |  |  |  | Scheduler 3 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 4 active |  |  |  | Scheduler 4 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 5 active |  |  |  | Scheduler 5 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 6 active |  |  |  | Scheduler 6 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 7 active |  |  |  | Scheduler 7 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 8 active |  |  |  | Scheduler 8 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 9 active |  |  |  | Scheduler 9 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 10 active |  |  |  | Scheduler 10 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 11 active |  |  |  | Scheduler 11 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 12 active |  |  |  | Scheduler 12 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 13 active |  |  |  | Scheduler 13 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 14 active |  |  |  | Scheduler 14 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 15 active |  |  |  | Scheduler 15 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 16 active |  |  |  | Scheduler 16 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 17 active |  |  |  | Scheduler 17 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 18 active |  |  |  | Scheduler 18 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 19 active |  |  |  | Scheduler 19 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 20 active |  |  |  | Scheduler 20 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 21 active |  |  |  | Scheduler 21 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 22 active |  |  |  | Scheduler 22 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 23 active |  |  |  | Scheduler 23 (configured in the utility software) is active.
Cmd Schedulers | Cmd Scheduler 24 active |  |  |  | Scheduler 24 (configured in the utility software) is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 1 |  |  |  | CANshare/PMS lite flag 1 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 2 |  |  |  | CANshare/PMS lite flag 2 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 3 |  |  |  | CANshare/PMS lite flag 3 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 4 |  |  |  | CANshare/PMS lite flag 4 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 5 |  |  |  | CANshare/PMS lite flag 5 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 6 |  |  |  | CANshare/PMS lite flag 6 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 7 |  |  |  | CANshare/PMS lite flag 7 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 8 |  |  |  | CANshare/PMS lite flag 8 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 9 |  |  |  | CANshare/PMS lite flag 9 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 10 |  |  |  | CANshare/PMS lite flag 10 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 11 |  |  |  | CANshare/PMS lite flag 11 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 12 |  |  |  | CANshare/PMS lite flag 12 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 13 |  |  |  | CANshare/PMS lite flag 13 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 14 |  |  |  | CANshare/PMS lite flag 14 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 15 |  |  |  | CANshare/PMS lite flag 15 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 16 |  |  |  | CANshare/PMS lite flag 16 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 17 |  |  |  | CANshare/PMS lite flag 17 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 18 |  |  |  | CANshare/PMS lite flag 18 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 19 |  |  |  | CANshare/PMS lite flag 19 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 20 |  |  |  | CANshare/PMS lite flag 20 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 21 |  |  |  | CANshare/PMS lite flag 21 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 22 |  |  |  | CANshare/PMS lite flag 22 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 23 |  |  |  | CANshare/PMS lite flag 23 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 24 |  |  |  | CANshare/PMS lite flag 24 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 25 |  |  |  | CANshare/PMS lite flag 25 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 26 |  |  |  | CANshare/PMS lite flag 26 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 27 |  |  |  | CANshare/PMS lite flag 27 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 28 |  |  |  | CANshare/PMS lite flag 28 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 29 |  |  |  | CANshare/PMS lite flag 29 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 30 |  |  |  | CANshare/PMS lite flag 30 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 31 |  |  |  | CANshare/PMS lite flag 31 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 32 |  |  |  | CANshare/PMS lite flag 32 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 33 |  |  |  | CANshare/PMS lite flag 33 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 34 |  |  |  | CANshare/PMS lite flag 34 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 35 |  |  |  | CANshare/PMS lite flag 35 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 36 |  |  |  | CANshare/PMS lite flag 36 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 37 |  |  |  | CANshare/PMS lite flag 37 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 38 |  |  |  | CANshare/PMS lite flag 38 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 39 |  |  |  | CANshare/PMS lite flag 39 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 40 |  |  |  | CANshare/PMS lite flag 40 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 41 |  |  |  | CANshare/PMS lite flag 41 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 42 |  |  |  | CANshare/PMS lite flag 42 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 43 |  |  |  | CANshare/PMS lite flag 43 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 44 |  |  |  | CANshare/PMS lite flag 44 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 45 |  |  |  | CANshare/PMS lite flag 45 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 46 |  |  |  | CANshare/PMS lite flag 46 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 47 |  |  |  | CANshare/PMS lite flag 47 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 48 |  |  |  | CANshare/PMS lite flag 48 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 49 |  |  |  | CANshare/PMS lite flag 49 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 50 |  |  |  | CANshare/PMS lite flag 50 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 51 |  |  |  | CANshare/PMS lite flag 51 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 52 |  |  |  | CANshare/PMS lite flag 52 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 53 |  |  |  | CANshare/PMS lite flag 53 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 54 |  |  |  | CANshare/PMS lite flag 54 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 55 |  |  |  | CANshare/PMS lite flag 55 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 56 |  |  |  | CANshare/PMS lite flag 56 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 57 |  |  |  | CANshare/PMS lite flag 57 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 58 |  |  |  | CANshare/PMS lite flag 58 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 59 |  |  |  | CANshare/PMS lite flag 59 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 60 |  |  |  | CANshare/PMS lite flag 60 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 61 |  |  |  | CANshare/PMS lite flag 61 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 62 |  |  |  | CANshare/PMS lite flag 62 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 63 |  |  |  | CANshare/PMS lite flag 63 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 64 |  |  |  | CANshare/PMS lite flag 64 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 65 |  |  |  | CANshare/PMS lite flag 65 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 66 |  |  |  | CANshare/PMS lite flag 66 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 67 |  |  |  | CANshare/PMS lite flag 67 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 68 |  |  |  | CANshare/PMS lite flag 68 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 69 |  |  |  | CANshare/PMS lite flag 69 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 70 |  |  |  | CANshare/PMS lite flag 70 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 71 |  |  |  | CANshare/PMS lite flag 71 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 72 |  |  |  | CANshare/PMS lite flag 72 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 73 |  |  |  | CANshare/PMS lite flag 73 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 74 |  |  |  | CANshare/PMS lite flag 74 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 75 |  |  |  | CANshare/PMS lite flag 75 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 76 |  |  |  | CANshare/PMS lite flag 76 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 77 |  |  |  | CANshare/PMS lite flag 77 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 78 |  |  |  | CANshare/PMS lite flag 78 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 79 |  |  |  | CANshare/PMS lite flag 79 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 80 |  |  |  | CANshare/PMS lite flag 80 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 81 |  |  |  | CANshare/PMS lite flag 81 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 82 |  |  |  | CANshare/PMS lite flag 82 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 83 |  |  |  | CANshare/PMS lite flag 83 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 84 |  |  |  | CANshare/PMS lite flag 84 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 85 |  |  |  | CANshare/PMS lite flag 85 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 86 |  |  |  | CANshare/PMS lite flag 86 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 87 |  |  |  | CANshare/PMS lite flag 87 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 88 |  |  |  | CANshare/PMS lite flag 88 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 89 |  |  |  | CANshare/PMS lite flag 89 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 90 |  |  |  | CANshare/PMS lite flag 90 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 91 |  |  |  | CANshare/PMS lite flag 91 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 92 |  |  |  | CANshare/PMS lite flag 92 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 93 |  |  |  | CANshare/PMS lite flag 93 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 94 |  |  |  | CANshare/PMS lite flag 94 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 95 |  |  |  | CANshare/PMS lite flag 95 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 96 |  |  |  | CANshare/PMS lite flag 96 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 97 |  |  |  | CANshare/PMS lite flag 97 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 98 |  |  |  | CANshare/PMS lite flag 98 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 99 |  |  |  | CANshare/PMS lite flag 99 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 100 |  |  |  | CANshare/PMS lite flag 100 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 101 |  |  |  | CANshare/PMS lite flag 101 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 102 |  |  |  | CANshare/PMS lite flag 102 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 103 |  |  |  | CANshare/PMS lite flag 103 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 104 |  |  |  | CANshare/PMS lite flag 104 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 105 |  |  |  | CANshare/PMS lite flag 105 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 106 |  |  |  | CANshare/PMS lite flag 106 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 107 |  |  |  | CANshare/PMS lite flag 107 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 108 |  |  |  | CANshare/PMS lite flag 108 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 109 |  |  |  | CANshare/PMS lite flag 109 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 110 |  |  |  | CANshare/PMS lite flag 110 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 111 |  |  |  | CANshare/PMS lite flag 111 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 112 |  |  |  | CANshare/PMS lite flag 112 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 113 |  |  |  | CANshare/PMS lite flag 113 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 114 |  |  |  | CANshare/PMS lite flag 114 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 115 |  |  |  | CANshare/PMS lite flag 115 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 116 |  |  |  | CANshare/PMS lite flag 116 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 117 |  |  |  | CANshare/PMS lite flag 117 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 118 |  |  |  | CANshare/PMS lite flag 118 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 119 |  |  |  | CANshare/PMS lite flag 119 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 120 |  |  |  | CANshare/PMS lite flag 120 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 121 |  |  |  | CANshare/PMS lite flag 121 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 122 |  |  |  | CANshare/PMS lite flag 122 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 123 |  |  |  | CANshare/PMS lite flag 123 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 124 |  |  |  | CANshare/PMS lite flag 124 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 125 |  |  |  | CANshare/PMS lite flag 125 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 126 |  |  |  | CANshare/PMS lite flag 126 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 127 |  |  |  | CANshare/PMS lite flag 127 is active.
CANshare/PMS lite flags | CANshare/PMS lite flag 128 |  |  |  | CANshare/PMS lite flag 128 is active.
Static sync. type | GB: Breaker
Static sync. type | GB: Infinite
Static sync. type | MB: Breaker
Static sync. type | MB: Infinite
Logic | Not used |  |  |  | -
Logic | TRUE |  |  |  | This event is always TRUE.
Logic | FALSE |  |  |  | This event is always FALSE.
Inputs | Dig. Input 39 |  |  |  | Digital input 39 is active.
Inputs | Dig. Input 40 |  |  |  | Digital input 40 is active.
Inputs | Dig. Input 41 |  |  |  | Digital input 41 is active.
Inputs | Dig. Input 42 |  |  |  | Digital input 42 is active.
Inputs | Dig. Input 43 |  |  |  | Digital input 43 is active.
Inputs | Dig. Input 44 |  |  |  | Digital input 44 is active.
Inputs | Dig. Input 45 |  |  |  | Digital input 45 is active.
Inputs | Dig. Input 46 |  |  |  | Digital input 46 is active.
Inputs | Dig. Input 47 |  |  |  | Digital input 47 is active.
Inputs | Dig. Input 48 |  |  |  | Digital input 48 is active.
Inputs | Dig. Input 49 |  |  |  | Digital input 49 is active.
Inputs | Dig. Input 50 |  |  |  | Digital input 50 is active.
Inputs | Dig. Input 20 |  |  |  | Digital input 20 is active.
Inputs | Dig. Input 21 |  |  |  | Digital input 21 is active.
Inputs | Dig. Input 22 |  |  |  | Digital input 22 is active.
Inputs | Dig. Input 23 |  |  |  | Digital input 23 is active.
Inputs | Emergency stop |  |  |  | The emergency stop is active.
CIO dig. inputs | CIO 116 no.1 In. 10 |  |  |  | CIO 116 no.1 In. 10 is active.
CIO dig. inputs | CIO 116 no.1 In. 11 |  |  |  | CIO 116 no.1 In. 11 is active.
CIO dig. inputs | CIO 116 no.1 In. 12 |  |  |  | CIO 116 no.1 In. 12 is active.
CIO dig. inputs | CIO 116 no.1 In. 13 |  |  |  | CIO 116 no.1 In. 13 is active.
CIO dig. inputs | CIO 116 no.1 In. 14 |  |  |  | CIO 116 no.1 In. 14 is active.
CIO dig. inputs | CIO 116 no.1 In. 15 |  |  |  | CIO 116 no.1 In. 15 is active.
CIO dig. inputs | CIO 116 no.1 In. 16 |  |  |  | CIO 116 no.1 In. 16 is active.
CIO dig. inputs | CIO 116 no.1 In. 17 |  |  |  | CIO 116 no.1 In. 17 is active.
CIO dig. inputs | CIO 116 no.1 In. 19 |  |  |  | CIO 116 no.1 In. 19 is active.
CIO dig. inputs | CIO 116 no.1 In. 20 |  |  |  | CIO 116 no.1 In. 20 is active.
CIO dig. inputs | CIO 116 no.1 In. 21 |  |  |  | CIO 116 no.1 In. 21 is active.
CIO dig. inputs | CIO 116 no.1 In. 22 |  |  |  | CIO 116 no.1 In. 22 is active.
CIO dig. inputs | CIO 116 no.1 In. 23 |  |  |  | CIO 116 no.1 In. 23 is active.
CIO dig. inputs | CIO 116 no.1 In. 24 |  |  |  | CIO 116 no.1 In. 24 is active.
CIO dig. inputs | CIO 116 no.1 In. 25 |  |  |  | CIO 116 no.1 In. 25 is active.
CIO dig. inputs | CIO 116 no.1 In. 26 |  |  |  | CIO 116 no.1 In. 26 is active.
CIO dig. inputs | CIO 116 no.2 In. 10 |  |  |  | CIO 116 no.2 In. 10 is active.
CIO dig. inputs | CIO 116 no.2 In. 11 |  |  |  | CIO 116 no.2 In. 11 is active.
CIO dig. inputs | CIO 116 no.2 In. 12 |  |  |  | CIO 116 no.2 In. 12 is active.
CIO dig. inputs | CIO 116 no.2 In. 13 |  |  |  | CIO 116 no.2 In. 13 is active.
CIO dig. inputs | CIO 116 no.2 In. 14 |  |  |  | CIO 116 no.2 In. 14 is active.
CIO dig. inputs | CIO 116 no.2 In. 15 |  |  |  | CIO 116 no.2 In. 15 is active.
CIO dig. inputs | CIO 116 no.2 In. 16 |  |  |  | CIO 116 no.2 In. 16 is active.
CIO dig. inputs | CIO 116 no.2 In. 17 |  |  |  | CIO 116 no.2 In. 17 is active.
CIO dig. inputs | CIO 116 no.2 In. 19 |  |  |  | CIO 116 no.2 In. 19 is active.
CIO dig. inputs | CIO 116 no.2 In. 20 |  |  |  | CIO 116 no.2 In. 20 is active.
CIO dig. inputs | CIO 116 no.2 In. 21 |  |  |  | CIO 116 no.2 In. 21 is active.
CIO dig. inputs | CIO 116 no.2 In. 22 |  |  |  | CIO 116 no.2 In. 22 is active.
CIO dig. inputs | CIO 116 no.2 In. 23 |  |  |  | CIO 116 no.2 In. 23 is active.
CIO dig. inputs | CIO 116 no.2 In. 24 |  |  |  | CIO 116 no.2 In. 24 is active.
CIO dig. inputs | CIO 116 no.2 In. 25 |  |  |  | CIO 116 no.2 In. 25 is active.
CIO dig. inputs | CIO 116 no.2 In. 26 |  |  |  | CIO 116 no.2 In. 26 is active.
CIO dig. inputs | CIO 116 no.3 In. 10 |  |  |  | CIO 116 no.3 In. 10 is active.
CIO dig. inputs | CIO 116 no.3 In. 11 |  |  |  | CIO 116 no.3 In. 11 is active.
CIO dig. inputs | CIO 116 no.3 In. 12 |  |  |  | CIO 116 no.3 In. 12 is active.
CIO dig. inputs | CIO 116 no.3 In. 13 |  |  |  | CIO 116 no.3 In. 13 is active.
CIO dig. inputs | CIO 116 no.3 In. 14 |  |  |  | CIO 116 no.3 In. 14 is active.
CIO dig. inputs | CIO 116 no.3 In. 15 |  |  |  | CIO 116 no.3 In. 15 is active.
CIO dig. inputs | CIO 116 no.3 In. 16 |  |  |  | CIO 116 no.3 In. 16 is active.
CIO dig. inputs | CIO 116 no.3 In. 17 |  |  |  | CIO 116 no.3 In. 17 is active.
CIO dig. inputs | CIO 116 no.3 In. 19 |  |  |  | CIO 116 no.3 In. 19 is active.
CIO dig. inputs | CIO 116 no.3 In. 20 |  |  |  | CIO 116 no.3 In. 20 is active.
CIO dig. inputs | CIO 116 no.3 In. 21 |  |  |  | CIO 116 no.3 In. 21 is active.
CIO dig. inputs | CIO 116 no.3 In. 22 |  |  |  | CIO 116 no.3 In. 22 is active.
CIO dig. inputs | CIO 116 no.3 In. 23 |  |  |  | CIO 116 no.3 In. 23 is active.
CIO dig. inputs | CIO 116 no.3 In. 24 |  |  |  | CIO 116 no.3 In. 24 is active.
CIO dig. inputs | CIO 116 no.3 In. 25 |  |  |  | CIO 116 no.3 In. 25 is active.
CIO dig. inputs | CIO 116 no.3 In. 26 |  |  |  | CIO 116 no.3 In. 26 is active.
CIO dig. inputs | CIO 308 no.1 In. 8 |  | 1220 |  | CIO 308 no.1 In. 8 is active.
CIO dig. inputs | CIO 308 no.1 In. 11 |  | 1220 |  | CIO 308 no.1 In. 11 is active.
CIO dig. inputs | CIO 308 no.1 In. 14 |  | 1220 |  | CIO 308 no.1 In. 14 is active.
CIO dig. inputs | CIO 308 no.1 In. 17 |  | 1220 |  | CIO 308 no.1 In. 17 is active.
CIO dig. inputs | CIO 308 no.1 In. 20 |  | 1220 |  | CIO 308 no.1 In. 20 is active.
CIO dig. inputs | CIO 308 no.1 In. 23 |  | 1220 |  | CIO 308 no.1 In. 23 is active.
CIO dig. inputs | CIO 308 no.1 In. 26 |  | 1220 |  | CIO 308 no.1 In. 26 is active.
CIO dig. inputs | CIO 308 no.1 In. 29 |  | 1220 |  | CIO 308 no.1 In. 29 is active.
CIO dig. inputs | CIO 308 no.2 In. 8 |  | 1220 |  | CIO 308 no.2 In. 8 is active.
CIO dig. inputs | CIO 308 no.2 In. 11 |  | 1220 |  | CIO 308 no.2 In. 11 is active.
CIO dig. inputs | CIO 308 no.2 In. 14 |  | 1220 |  | CIO 308 no.2 In. 14 is active.
CIO dig. inputs | CIO 308 no.2 In. 17 |  | 1220 |  | CIO 308 no.2 In. 17 is active.
CIO dig. inputs | CIO 308 no.2 In. 20 |  | 1220 |  | CIO 308 no.2 In. 20 is active.
CIO dig. inputs | CIO 308 no.2 In. 23 |  | 1220 |  | CIO 308 no.2 In. 23 is active.
CIO dig. inputs | CIO 308 no.2 In. 26 |  | 1220 |  | CIO 308 no.2 In. 26 is active.
CIO dig. inputs | CIO 308 no.2 In. 29 |  | 1220 |  | CIO 308 no.2 In. 29 is active.
CIO dig. inputs | CIO 308 no.3 In. 8 |  | 1220 |  | CIO 308 no.3 In. 8 is active.
CIO dig. inputs | CIO 308 no.3 In. 11 |  | 1220 |  | CIO 308 no.3 In. 11 is active.
CIO dig. inputs | CIO 308 no.3 In. 14 |  | 1220 |  | CIO 308 no.3 In. 14 is active.
CIO dig. inputs | CIO 308 no.3 In. 17 |  | 1220 |  | CIO 308 no.3 In. 17 is active.
CIO dig. inputs | CIO 308 no.3 In. 20 |  | 1220 |  | CIO 308 no.3 In. 20 is active.
CIO dig. inputs | CIO 308 no.3 In. 23 |  | 1220 |  | CIO 308 no.3 In. 23 is active.
CIO dig. inputs | CIO 308 no.3 In. 26 |  | 1220 |  | CIO 308 no.3 In. 26 is active.
CIO dig. inputs | CIO 308 no.3 In. 29 |  | 1220 |  | CIO 308 no.3 In. 29 is active.
Modes | Island |  |  |  | The controller is in island operation.
Modes | AMF |  |  |  | The controller is in automatic mains failure operation.
Modes | Peak shaving |  |  |  | The controller is in peak shaving operation.
Modes | Fixed power |  |  |  | The controller is in fixed power operation.
Modes | Mains power export |  |  |  | The controller is in mains power export operation.
Modes | Load take over |  |  |  | The controller is in load take over operation.
Modes | SEMI mode |  |  | 1299 | The controller is in semi-auto mode (only up to SW version 1.29).
Modes | MANUAL mode |  | 1300 |  | The controller is in manual mode (called semi-auto before SW version 1.30).
Modes | TEST mode |  |  |  | The controller is in test mode.
Modes | AUTO mode |  |  |  | The controller is in automatic mode.
Modes | MANUAL mode |  |  | 1299 | The controller is in manual mode (only up to SW version 1.29).
Modes | NoReg mode |  | 1300 |  | The controller is in no regulation mode (called manual before SW version 1.30).
Modes | BLOCK mode |  |  |  | The controller is in block mode.
Modes | DI SEMI mode used |  |  | 1299 | The semi-auto mode digital input is active (only up to SW version 1.29).
Modes | DI MANUAL mode used |  | 1300 |  | The manual mode digital input is active.
Modes | DI TEST mode used |  |  |  | The test mode digital input is active.
Modes | DI AUTO mode used |  |  |  | The auto mode digital input is active.
Modes | DI MANUAL mode used |  |  | 1299 | The manual mode digital input is active (only up to SW version 1.29).
Modes | DI NoReg mode used |  | 1300 |  | The no regulation mode digital input is active.
Modes | DI BLOCK mode used |  |  |  | The block mode digital input is active.
Modes | Modeshift or AMF act. |  |  |  | A mains failure sequence is active.
Relays | Not used |  |  |  | -
Relays | Relay 5 |  |  |  | Relay 5 is activated.
Relays | Relay 6 |  |  |  | Relay 6 is activated.
Relays | Relay 9 |  |  |  | Relay 9 is activated.
Relays | Relay 10 |  |  |  | Relay 10 is activated.
Relays | Relay 11 |  |  |  | Relay 11 is activated.
Relays | Relay 12 |  |  |  | Relay 12 is activated.
Relays | Relay 13 |  |  |  | Relay 13 is activated.
Relays | Relay 14 |  |  |  | Relay 14 is activated.
Relays | Relay 15 |  |  |  | Relay 15 is activated.
Relays | Relay 16 |  |  |  | Relay 16 is activated.
Relays | Relay 17 |  |  |  | Relay 17 is activated.
Relays | Relay 18 |  |  |  | Relay 18 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 9 |  |  |  | CIO 208 no.1 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 11 |  |  |  | CIO 208 no.1 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 13 |  |  |  | CIO 208 no.1 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 15 |  |  |  | CIO 208 no.1 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 18 |  |  |  | CIO 208 no.1 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 21 |  |  |  | CIO 208 no.1 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 24 |  |  |  | CIO 208 no.1 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.1 Out. 27 |  |  |  | CIO 208 no.1 Out. 27 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 9 |  |  |  | CIO 208 no.2 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 11 |  |  |  | CIO 208 no.2 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 13 |  |  |  | CIO 208 no.2 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 15 |  |  |  | CIO 208 no.2 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 18 |  |  |  | CIO 208 no.2 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 21 |  |  |  | CIO 208 no.2 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 24 |  |  |  | CIO 208 no.2 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.2 Out. 27 |  |  |  | CIO 208 no.2 Out. 27 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 9 |  |  |  | CIO 208 no.3 Out. 9 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 11 |  |  |  | CIO 208 no.3 Out. 11 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 13 |  |  |  | CIO 208 no.3 Out. 13 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 15 |  |  |  | CIO 208 no.3 Out. 15 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 18 |  |  |  | CIO 208 no.3 Out. 18 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 21 |  |  |  | CIO 208 no.3 Out. 21 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 24 |  |  |  | CIO 208 no.3 Out. 24 is activated.
CIO dig. outputs | CIO 208 no.3 Out. 27 |  |  |  | CIO 208 no.3 Out. 27 is activated.
CIO dig. outputs | CIO 116 no.1 conf. status output |  |  |  | The CIO 116 no.1 conf. status output is activated.
CIO dig. outputs | CIO 116 no.2 conf. status output |  |  |  | The CIO 116 no.2 conf. status output is activated.
CIO dig. outputs | CIO 116 no.3 conf. status output |  |  |  | The CIO 116 no.3 conf. status output is activated.
CIO dig. outputs | CIO 208 no.1 conf. status output |  |  |  | The CIO 208 no.1 conf. status output is activated.
CIO dig. outputs | CIO 208 no.2 conf. status output |  |  |  | The CIO 208 no.2 conf. status output is activated.
CIO dig. outputs | CIO 208 no.3 conf. status output |  |  |  | The CIO 208 no.3 conf. status output is activated.
CIO dig. outputs | CIO 308 no.1 conf. status output |  |  |  | The CIO 308 no.1 conf. status output is activated.
CIO dig. outputs | CIO 308 no.2 conf. status output |  |  |  | The CIO 308 no.2 conf. status output is activated.
CIO dig. outputs | CIO 308 no.3 conf. status output |  |  |  | The CIO 308 no.3 conf. status output is activated.
Virtual toggle events | Virtual toggle event 1 |  |  |  | Virtual toggle event 1 is active.
Virtual toggle events | Virtual toggle event 2 |  |  |  | Virtual toggle event 2 is active.
Virtual toggle events | Virtual toggle event 3 |  |  |  | Virtual toggle event 3 is active.
Virtual toggle events | Virtual toggle event 4 |  |  |  | Virtual toggle event 4 is active.
Virtual toggle events | Virtual toggle event 5 |  |  |  | Virtual toggle event 5 is active.
Virtual toggle events | Virtual toggle event 6 |  |  |  | Virtual toggle event 6 is active.
Virtual toggle events | Virtual toggle event 7 |  |  |  | Virtual toggle event 7 is active.
Virtual toggle events | Virtual toggle event 8 |  |  |  | Virtual toggle event 8 is active.
Virtual toggle events | Virtual toggle event 9 |  |  |  | Virtual toggle event 9 is active.
Virtual toggle events | Virtual toggle event 10 |  |  |  | Virtual toggle event 10 is active.
Virtual toggle events | Virtual toggle event 11 |  |  |  | Virtual toggle event 11 is active.
Virtual toggle events | Virtual toggle event 12 |  |  |  | Virtual toggle event 12 is active.
Virtual toggle events | Virtual toggle event 13 |  |  |  | Virtual toggle event 13 is active.
Virtual toggle events | Virtual toggle event 14 |  |  |  | Virtual toggle event 14 is active.
Virtual toggle events | Virtual toggle event 15 |  |  |  | Virtual toggle event 15 is active.
Virtual toggle events | Virtual toggle event 16 |  |  |  | Virtual toggle event 16 is active.
Virtual toggle events | Virtual toggle event 17 |  |  |  | Virtual toggle event 17 is active.
Virtual toggle events | Virtual toggle event 18 |  |  |  | Virtual toggle event 18 is active.
Virtual toggle events | Virtual toggle event 19 |  |  |  | Virtual toggle event 19 is active.
Virtual toggle events | Virtual toggle event 20 |  |  |  | Virtual toggle event 20 is active.
Virtual toggle events | Virtual toggle event 21 |  |  |  | Virtual toggle event 21 is active.
Virtual toggle events | Virtual toggle event 22 |  |  |  | Virtual toggle event 22 is active.
Virtual toggle events | Virtual toggle event 23 |  |  |  | Virtual toggle event 23 is active.
Virtual toggle events | Virtual toggle event 24 |  |  |  | Virtual toggle event 24 is active.
Virtual toggle events | Virtual toggle event 25 |  |  |  | Virtual toggle event 25 is active.
Virtual toggle events | Virtual toggle event 26 |  |  |  | Virtual toggle event 26 is active.
Virtual toggle events | Virtual toggle event 27 |  |  |  | Virtual toggle event 27 is active.
Virtual toggle events | Virtual toggle event 28 |  |  |  | Virtual toggle event 28 is active.
Virtual toggle events | Virtual toggle event 29 |  |  |  | Virtual toggle event 29 is active.
Virtual toggle events | Virtual toggle event 30 |  |  |  | Virtual toggle event 30 is active.
Virtual toggle events | Virtual toggle event 31 |  |  |  | Virtual toggle event 31 is active.
Virtual toggle events | Virtual toggle event 32 |  |  |  | Virtual toggle event 32 is active.
Virtual toggle events | Virtual toggle event 33 |  |  |  | Virtual toggle event 33 is active.
Virtual toggle events | Virtual toggle event 34 |  |  |  | Virtual toggle event 34 is active.
Virtual toggle events | Virtual toggle event 35 |  |  |  | Virtual toggle event 35 is active.
Virtual toggle events | Virtual toggle event 36 |  |  |  | Virtual toggle event 36 is active.
Virtual toggle events | Virtual toggle event 37 |  |  |  | Virtual toggle event 37 is active.
Virtual toggle events | Virtual toggle event 38 |  |  |  | Virtual toggle event 38 is active.
Virtual toggle events | Virtual toggle event 39 |  |  |  | Virtual toggle event 39 is active.
Virtual toggle events | Virtual toggle event 40 |  |  |  | Virtual toggle event 40 is active.
Virtual toggle events | Virtual toggle event 41 |  |  |  | Virtual toggle event 41 is active.
Virtual toggle events | Virtual toggle event 42 |  |  |  | Virtual toggle event 42 is active.
Virtual toggle events | Virtual toggle event 43 |  |  |  | Virtual toggle event 43 is active.
Virtual toggle events | Virtual toggle event 44 |  |  |  | Virtual toggle event 44 is active.
Virtual toggle events | Virtual toggle event 45 |  |  |  | Virtual toggle event 45 is active.
Virtual toggle events | Virtual toggle event 46 |  |  |  | Virtual toggle event 46 is active.
Virtual toggle events | Virtual toggle event 47 |  |  |  | Virtual toggle event 47 is active.
Virtual toggle events | Virtual toggle event 48 |  |  |  | Virtual toggle event 48 is active.
Virtual toggle events | Virtual toggle event 49 |  |  |  | Virtual toggle event 49 is active.
Virtual toggle events | Virtual toggle event 50 |  |  |  | Virtual toggle event 50 is active.
Virtual toggle events | Virtual toggle event 51 |  |  |  | Virtual toggle event 51 is active.
Virtual toggle events | Virtual toggle event 52 |  |  |  | Virtual toggle event 52 is active.
Virtual toggle events | Virtual toggle event 53 |  |  |  | Virtual toggle event 53 is active.
Virtual toggle events | Virtual toggle event 54 |  |  |  | Virtual toggle event 54 is active.
Virtual toggle events | Virtual toggle event 55 |  |  |  | Virtual toggle event 55 is active.
Virtual toggle events | Virtual toggle event 56 |  |  |  | Virtual toggle event 56 is active.
Virtual toggle events | Virtual toggle event 57 |  |  |  | Virtual toggle event 57 is active.
Virtual toggle events | Virtual toggle event 58 |  |  |  | Virtual toggle event 58 is active.
Virtual toggle events | Virtual toggle event 59 |  |  |  | Virtual toggle event 59 is active.
Virtual toggle events | Virtual toggle event 60 |  |  |  | Virtual toggle event 60 is active.
Virtual toggle events | Virtual toggle event 61 |  |  |  | Virtual toggle event 61 is active.
Virtual toggle events | Virtual toggle event 62 |  |  |  | Virtual toggle event 62 is active.
Virtual toggle events | Virtual toggle event 63 |  |  |  | Virtual toggle event 63 is active.
Virtual toggle events | Virtual toggle event 64 |  |  |  | Virtual toggle event 64 is active.
Virtual toggle events | Virtual toggle event 65 |  |  |  | Virtual toggle event 65 is active.
Virtual toggle events | Virtual toggle event 66 |  |  |  | Virtual toggle event 66 is active.
Virtual toggle events | Virtual toggle event 67 |  |  |  | Virtual toggle event 67 is active.
Virtual toggle events | Virtual toggle event 68 |  |  |  | Virtual toggle event 68 is active.
Virtual toggle events | Virtual toggle event 69 |  |  |  | Virtual toggle event 69 is active.
Virtual toggle events | Virtual toggle event 70 |  |  |  | Virtual toggle event 70 is active.
Virtual toggle events | Virtual toggle event 71 |  |  |  | Virtual toggle event 71 is active.
Virtual toggle events | Virtual toggle event 72 |  |  |  | Virtual toggle event 72 is active.
Virtual toggle events | Virtual toggle event 73 |  |  |  | Virtual toggle event 73 is active.
Virtual toggle events | Virtual toggle event 74 |  |  |  | Virtual toggle event 74 is active.
Virtual toggle events | Virtual toggle event 75 |  |  |  | Virtual toggle event 75 is active.
Virtual toggle events | Virtual toggle event 76 |  |  |  | Virtual toggle event 76 is active.
Virtual toggle events | Virtual toggle event 77 |  |  |  | Virtual toggle event 77 is active.
Virtual toggle events | Virtual toggle event 78 |  |  |  | Virtual toggle event 78 is active.
Virtual toggle events | Virtual toggle event 79 |  |  |  | Virtual toggle event 79 is active.
Virtual toggle events | Virtual toggle event 80 |  |  |  | Virtual toggle event 80 is active.
Virtual toggle events | Virtual toggle event 81 |  |  |  | Virtual toggle event 81 is active.
Virtual toggle events | Virtual toggle event 82 |  |  |  | Virtual toggle event 82 is active.
Virtual toggle events | Virtual toggle event 83 |  |  |  | Virtual toggle event 83 is active.
Virtual toggle events | Virtual toggle event 84 |  |  |  | Virtual toggle event 84 is active.
Virtual toggle events | Virtual toggle event 85 |  |  |  | Virtual toggle event 85 is active.
Virtual toggle events | Virtual toggle event 86 |  |  |  | Virtual toggle event 86 is active.
Virtual toggle events | Virtual toggle event 87 |  |  |  | Virtual toggle event 87 is active.
Virtual toggle events | Virtual toggle event 88 |  |  |  | Virtual toggle event 88 is active.
Virtual toggle events | Virtual toggle event 89 |  |  |  | Virtual toggle event 89 is active.
Virtual toggle events | Virtual toggle event 90 |  |  |  | Virtual toggle event 90 is active.
Virtual toggle events | Virtual toggle event 91 |  |  |  | Virtual toggle event 91 is active.
Virtual toggle events | Virtual toggle event 92 |  |  |  | Virtual toggle event 92 is active.
Virtual toggle events | Virtual toggle event 93 |  |  |  | Virtual toggle event 93 is active.
Virtual toggle events | Virtual toggle event 94 |  |  |  | Virtual toggle event 94 is active.
Virtual toggle events | Virtual toggle event 95 |  |  |  | Virtual toggle event 95 is active.
Virtual toggle events | Virtual toggle event 96 |  |  |  | Virtual toggle event 96 is active.
Virtual switch events | Virtual switch event 1 |  |  |  | Virtual switch event 1 is active.
Virtual switch events | Virtual switch event 2 |  |  |  | Virtual switch event 2 is active.
Virtual switch events | Virtual switch event 3 |  |  |  | Virtual switch event 3 is active.
Virtual switch events | Virtual switch event 4 |  |  |  | Virtual switch event 4 is active.
Virtual switch events | Virtual switch event 5 |  |  |  | Virtual switch event 5 is active.
Virtual switch events | Virtual switch event 6 |  |  |  | Virtual switch event 6 is active.
Virtual switch events | Virtual switch event 7 |  |  |  | Virtual switch event 7 is active.
Virtual switch events | Virtual switch event 8 |  |  |  | Virtual switch event 8 is active.
Virtual switch events | Virtual switch event 9 |  |  |  | Virtual switch event 9 is active.
Virtual switch events | Virtual switch event 10 |  |  |  | Virtual switch event 10 is active.
Virtual switch events | Virtual switch event 11 |  |  |  | Virtual switch event 11 is active.
Virtual switch events | Virtual switch event 12 |  |  |  | Virtual switch event 12 is active.
Virtual switch events | Virtual switch event 13 |  |  |  | Virtual switch event 13 is active.
Virtual switch events | Virtual switch event 14 |  |  |  | Virtual switch event 14 is active.
Virtual switch events | Virtual switch event 15 |  |  |  | Virtual switch event 15 is active.
Virtual switch events | Virtual switch event 16 |  |  |  | Virtual switch event 16 is active.
Virtual switch events | Virtual switch event 17 |  |  |  | Virtual switch event 17 is active.
Virtual switch events | Virtual switch event 18 |  |  |  | Virtual switch event 18 is active.
Virtual switch events | Virtual switch event 19 |  |  |  | Virtual switch event 19 is active.
Virtual switch events | Virtual switch event 20 |  |  |  | Virtual switch event 20 is active.
Virtual switch events | Virtual switch event 21 |  |  |  | Virtual switch event 21 is active.
Virtual switch events | Virtual switch event 22 |  |  |  | Virtual switch event 22 is active.
Virtual switch events | Virtual switch event 23 |  |  |  | Virtual switch event 23 is active.
Virtual switch events | Virtual switch event 24 |  |  |  | Virtual switch event 24 is active.
Virtual switch events | Virtual switch event 25 |  |  |  | Virtual switch event 25 is active.
Virtual switch events | Virtual switch event 26 |  |  |  | Virtual switch event 26 is active.
Virtual switch events | Virtual switch event 27 |  |  |  | Virtual switch event 27 is active.
Virtual switch events | Virtual switch event 28 |  |  |  | Virtual switch event 28 is active.
Virtual switch events | Virtual switch event 29 |  |  |  | Virtual switch event 29 is active.
Virtual switch events | Virtual switch event 30 |  |  |  | Virtual switch event 30 is active.
Virtual switch events | Virtual switch event 31 |  |  |  | Virtual switch event 31 is active.
Virtual switch events | Virtual switch event 32 |  |  |  | Virtual switch event 32 is active.
AOP Buttons | Button 01 |  |  |  | AOP button 01 is pushed.
AOP Buttons | Button 02 |  |  |  | AOP button 02 is pushed.
AOP Buttons | Button 03 |  |  |  | AOP button 03 is pushed.
AOP Buttons | Button 04 |  |  |  | AOP button 04 is pushed.
AOP Buttons | Button 05 |  |  |  | AOP button 05 is pushed.
AOP Buttons | Button 06 |  |  |  | AOP button 06 is pushed.
AOP Buttons | Button 07 |  |  |  | AOP button 07 is pushed.
AOP Buttons | Button 08 |  |  |  | AOP button 08 is pushed.
Fail class | Block |  |  |  | There is an active alarm that has the alarm action "Block".
Fail class | Warning |  |  |  | At least one alarm with the fail class Warning is active.
Fail class | Trip GB |  |  |  | There is an active alarm that has the alarm action "Trip GB".
Fail class | Trip+stop |  |  |  | There is an active alarm that has the alarm action "Trip+stop".
Fail class | Shutdown |  |  |  | At least one alarm with the fail class Shutdown is active.
Fail class | Trip MB |  |  |  | There is an active alarm that has the alarm action "Trip MB".
Fail class | Safety stop |  |  |  | There is an active alarm that has the alarm action "Safety stop".
Fail class | Trip MB/GB |  |  |  | There is an active alarm that has the alarm action "Trip MB/GB".
Fail class | Controlled stop |  |  |  | There is an active alarm that has the alarm action "Controlled stop".
EIC event | DPF Lamp OFF |  |  |  | The Diesel Particular Filter does not need regeneration.
EIC event | DPF Lamp ON (solid) |  |  |  | The Diesel Particular Filter needs regeneration.
EIC event | DPF Lamp ON (blink) |  |  |  | The Diesel Particular Filter needs regeneration soon.
EIC event | DPF Active Regeneration not activated (status) |  |  |  | The Diesel Particular Filter is not being regenerated.
EIC event | DPF Active Regeneration activated (status) |  |  |  | The Diesel Particular Filter is being regenerated.
EIC event | DPF Active Regeneration needed (status) |  |  |  | The Diesel Particular Filter needs active regeneration.
EIC event | DPF Regen not needed (status) |  |  |  | The Diesel Particular Filter does not need regeneration.
EIC event | DPF Regen needed - lowest level (status) |  |  |  | The Diesel Particular Filter needs regeneration, but not urgently.
EIC event | DPF Regen needed - moderate level (status) |  |  |  | The Diesel Particular Filter needs regeneration soon.
EIC event | DPF Regen needed - highest level (status) |  |  |  | The Diesel Particular Filter urgently needs regeneration.
EIC event | DPF Regen not inhibited (lamp) |  |  |  | The EIC event is active. See the EIC documentation.
EIC event | DPF Regen inhibited (lamp) |  |  |  | The EIC event is active. See the EIC documentation.
EIC event | High Exh Syst Temp OFF (lamp) |  |  |  | The exhaust gas has no high temperature alarm.
EIC event | High Exh Syst Temp ON (lamp) |  |  |  | The exhaust gas has a high temperature alarm.
EIC event | MTU LIMIT LAMP OFF (lamp) |  |  |  | Proprietary event.
EIC event | MTU LIMIT LAMP ON (solid) |  |  |  | Proprietary event.
EIC event | MTU LIMIT LAMP ON (blink) |  |  |  | Proprietary event.
EIC event | MTU Limit Lamp ON Blink 2Hz (status) |  |  |  | Proprietary event.
EIC event | DEF Level LOW ICON OFF (lamp) |  |  |  | No active alarm.
EIC event | DEF Level LOW ICON ON (solid) |  |  |  | Alarm active.
EIC event | DEF Level LOW ICON ON (blink) |  |  |  | Alarm active (higher severity than solid).
EIC event | Purge Active ON (status) |  |  |  | Proprietary event.
EIC event | Inducement not active (status) |  |  |  | Proprietary event.
EIC event | Inducements warning (status) |  |  |  | Proprietary event.
EIC event | Derate active (status) |  |  |  | Proprietary event.
EIC event | Pre severe derate warning (status) |  |  |  | Proprietary event.
EIC event | Severe derate (status) |  |  |  | Proprietary event.
EIC event | Temporate override of derate (status) |  |  |  | Proprietary event.
EIC event | Scr Inducement Reason OK (status) |  |  |  | Proprietary event.
EIC event | Reagent tank low (status) |  |  |  | Proprietary event.
EIC event | Incorrect reagent quality (status) |  |  |  | Proprietary event.
EIC event | Absence of reagent dosing (status) |  |  |  | Proprietary event.
EIC event | MTU TIER4 Lamp ON Blink 2Hz (status) |  |  |  | Proprietary event.
EIC event | MTU Buzzer Lamp OFF (status) |  |  |  | Proprietary event.
EIC event | MTU Buzzer Lamp ON Solid (status) |  |  |  | Proprietary event.
EIC event | MTU Buzzer Lamp ON Blink 1Hz (status) |  |  |  | Proprietary event.
EIC event | MTU Buzzer Lamp ON Blink 2Hz (status) |  |  |  | Proprietary event (2 Hz is more severe than 1 Hz).
EIC event | AT Yellow Lamp OFF (status) |  |  |  | No after treatment warning.
EIC event | AT Yellow Lamp ON (status) |  |  |  | There is an after treatment warning.
EIC event | AT Red Lamp OFF (status) |  |  |  | No after treatment shutdown.
EIC event | AT Red Lamp ON (status) |  |  |  | There is an after treatment shutdown.
EIC event | Engine Fuel Leakage 1 (status) |  |  |  | Activated by the J1939 object EngineFuelLeak1
EIC event | Engine Wait to Start (status) |  |  |  | Activated by the J1939 object EngineWaitToStart
EIC event | Engine Protect Sys Shutdown (status) |  |  |  | Activated by the J1939 object EngineProtectSysShutdown
EIC event | Engine Protect Sys Appro Shutdown (status) |  |  |  | Activated by the J1939 object EngineProtectSysApproShutdown
EIC event | Engine Alarm Acknowledge (status) |  |  |  | Activated by the J1939 object EngineAlarmAcknowledge
EIC event | Engine Air Shutoff Command Status (status) |  |  |  | Activated by the J1939 object EngineAirShutoffCommandStatus
EIC event | Engine Overspeed Test (status) |  |  |  | Activated by the J1939 object EngineOverspeedTest
EIC event | Engine Shutoff Status (status) |  |  |  | Activated by the J1939 object EngineShutoffStatus
EIC event | DPF Regen not inhibited due to parking brake |  |  |  | The Diesel Particular Filter regeneration is not inhibited due to the parking brake.
EIC event | DPF Regen inhibited due to parking brake |  |  |  | The Diesel Particular Filter regeneration is inhibited due to the parking brake.
EIC event | DPF Regen not inhibited due to neutral gear switch |  |  |  | The Diesel Particular Filter regeneration is not inhibited due to the neutral gear switch.
EIC event | DPF Regen inhibited due to neutral gear switch |  |  |  | The Diesel Particular Filter regeneration is inhibited due to the neutral gear switch.
EIC event | Isuzu Manual Purge ECU activated (status) |  | 1060 |  | A manual purge is active in the ECU.
EIC event | Isuzu Manual Purge E-IDSS activated (status) |  | 1060 |  | E-IDSS (an Isuzu service PC tool) activated a manual purge.
EIC event | Isuzu Force Purge activated (status) |  | 1060 |  | A force purge is active.
EIC event | Kubota oil switch |  | 1110 |  | Proprietary event.
EIC event | Scania S8 - Evaporation not required |  | 1110 |  | Proprietary event.
EIC event | Scania S8 - Evaporation required - less urgent |  | 1110 |  | Proprietary event.
EIC event | Scania S8 - Evaporation required - urgent |  | 1110 |  | Proprietary event.
EIC event | Scania S8 - Evaporation is in progress |  | 1110 |  | Proprietary event.
EIC event | KWG ISO5 - Isolation fault |  | 1120 |  | The EIC event is active. See the EIC documentation.
EIC event | KWG ISO5 - Isolation warning |  | 1120 |  | The EIC event is active. See the EIC documentation.
EIC event | KWG ISO5 - Isolation timeout |  | 1120 |  | The EIC event is active. See the EIC documentation.
EIC event | Doosan stage 5 ash lamp status < 100% |  | 1120 |  | Proprietary event.
EIC event | Doosan stage 5 ash lamp status 100%-105% |  | 1120 |  | Proprietary event.
EIC event | Doosan stage 5 ash lamp status 106%-110% |  | 1120 |  | Proprietary event.
EIC event | Doosan stage 5 ash lamp status 111%-120% |  | 1120 |  | Proprietary event.
EIC event | Doosan stage 5 ash lamp status > 121% |  | 1120 |  | Proprietary event.
EIC event | FPT - Turbo heat protection |  | 1150 |  | Proprietary event. Activated when turbo heat protection is activated.
EIC event | Safe regeneration (status) |  | 1150 |  | For all protocols that support safe regeneration. The event is active if the command is sent to the ECU.
EIC event | FPT - High coolant pre-warning |  | 1150 |  | Proprietary event.
EIC event | FPT - High coolant warning |  | 1150 |  | Proprietary event.
EIC event | FPT - Engine overspeed |  | 1150 |  | Proprietary event.
EIC event | FPT - Engine high oil temperature |  | 1150 |  | Proprietary event.
EIC event | FPT - Engine oil low pressure |  | 1150 |  | Proprietary event.
EIC event | Water in fuel 1 (SPN 97) |  | 1150 |  | There is water accumulation in the fuel.
EIC event | Deutz EMR5 Standstill request from SCR system |  | 1150 |  | Proprietary event.
EIC event | Deutz EMR5 Standstill request due to maintenance |  | 1150 |  | Proprietary event.
EIC event | Deutz EMR5 Standstill request due to time in headmode 2 |  | 1150 |  | Proprietary event.
EIC event | Deutz EMR5 Standstill request due to high filter soot load |  | 1150 |  | Proprietary event.
EIC event | Deutz EMR5 Standstill no request |  | 1150 |  | Proprietary event.
EIC event | Yanmar Stage V Accelerator Interlock Switch feedback |  | 1150 |  | Proprietary event.
EIC event | Yanmar Stage V DPF regeneration acknowledge lamp |  | 1150 |  | Proprietary event.
EIC event | FPT DEF technical failure mild inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF technical failure moderate inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF technical failure severe inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF quality driver warning |  | 1160 |  | Proprietary event.
EIC event | FPT DEF quality moderate inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF quality severe inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF level driver warning |  | 1160 |  | Proprietary event.
EIC event | FPT DEF level moderate inducement |  | 1160 |  | Proprietary event.
EIC event | FPT DEF level severe inducement |  | 1160 |  | Proprietary event.
EIC event | John Deere DPF regeneration in-active |  | 1180 |  | Proprietary event.
EIC event | John Deere DPF normal regeneration in progress |  | 1180 |  | Proprietary event.
EIC event | John Deere DPF deep clean in progress |  | 1180 |  | Proprietary event.
EIC event | John Deere DPF regeneration aborted |  | 1180 |  | Proprietary event.
EIC event | Kohler KDI3404 Power On and engine not running |  | 1190 |  | Power On and engine not running (CASRS)
EIC event | Kohler KDI3404 Pedal Input Delay active no idle |  | 1190 |  | Pedal Input Delay active (engine run at no idle condition) (CASRS)
EIC event | Kohler KDI3404 Pedal Input Delay active time elapsed too short |  | 1190 |  | Pedal Input Delay active (time elapsed too short) (CASRS)
EIC event | Kohler KDI3404 Pedal Input Delay NOT active |  | 1190 |  | Pedal Input Delay NOT active (CASRS)
EIC event | John Deere force regeneration not needed |  | 1210 |  | DM1 with SPN 3719, FMI 15 is active (John Deere Stage V).
EIC event | John Deere force regeneration needed |  | 1210 |  | DM1 with SPN 3719, FMI 16 is active (John Deere Stage V).
EIC event | John Deere service regeneration needed |  | 1210 |  | DM1 with SPN 3719, FMI 0 is active (John Deere Stage V).
EIC event | John Deere DPF regeneration state very high |  | 1210 |  | SPN3701 is set to 4 (John Deere Stage V).
EIC event | John Deere DPF regeneration state service only |  | 1210 |  | SPN3701 is set to 5 (John Deere Stage V).
EIC event | DPF force state not active |  | 1210 |  | SPN4175 is set to 0.
EIC event | DPF forced by switch |  | 1210 |  | SPN4175 is set to 1.
EIC event | DPF forced by service tool |  | 1210 |  | SPN4175 is set to 2 (4 for John Deere Stage V).
EIC event | CVT yellow lamp active |  | 1300 |  | DM1 yellow lamp is received from CVT.
EIC event | CVT red lamp active |  | 1300 |  | DM1 red lamp is received from CVT.
EIC event | CVT timeout |  | 1300 |  | CVT timeout because ETC7 is not received
EIC event | CVT crank enabled |  | 1300 |  | CVT crank is enabled (SPN 2900)
EIC event | CVT shift inhibit active |  | 1300 |  | CVT shift inhibit active is enabled (SPN 1851)
EIC event | CVT TVSI active |  | 1300 |  | CVT TVSI mode active
EIC event | Guascor fluxing start active |  | 1320 |  | Active on start for fluxing start part
DVC 310 events | LED: Power On |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: U=U |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: PFkVAR |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Manual |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Fault |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Exc. |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Exc. blink |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Volt |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | LED: Hz |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | General trip |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Short circuit |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Loss of voltage sensing |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Under excitation |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Over excitation (level) |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Over excitation (curve) |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Over voltage |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | High temperature PT100_1 |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | High temperature PT100_2 |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | High temperature PT100_3 |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | High temperature PTC |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator over current |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator over current U |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator over current V |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator over current W |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Imbalance Stator current |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Diode fault |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Shutdown diodes |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator current limitation off |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator current limitation TM |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator current limitation IM |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 310 events | Stator current limitation Active |  |  |  | The DVC 310 event is active. See the DVC 310 documentation.
DVC 550 events | Stator current limitation off |  | 1110 |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Stator current limitation TM |  | 1110 |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Stator current limitation IM |  | 1110 |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Stator current limitation Active |  | 1110 |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: USB |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: Power ON |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: U=U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: PF kVAR |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: I Exc. |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: Diode fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: Exc. |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: Volt |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | LED: Hz |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Any D550 warning alarms present |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Any D550 trip alarms present |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Over voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Under voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Over frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Under freq. |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Open diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Shorted diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Reverse P |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Reverse Q |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 1 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 1 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 2 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 2 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 3 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 3 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 4 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 4 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 5 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 5 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PTC 1 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PTC 2 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PTC 3 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PTC 4 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PTC 5 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Sensing lost |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Unbalanced U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Unbalanced I |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Short circuit |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Excitat. chain |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Motor start |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Power bridge |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): Batt supply low |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): CAN supply low |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 1 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 2 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 3 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 4 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): PT100 5 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AIN1 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AIN2 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AIN3 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AIN4 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AOUT1 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AOUT2 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AOUT3 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): AOUT4 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Warning): DOUT overload |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Over voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Under voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Over frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Under freq. |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Open diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Shorted diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Reverse P |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Reverse Q |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 1 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 1 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 2 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 2 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 3 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 3 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 4 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 4 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 5 alarm |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 5 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PTC 1 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PTC 2 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PTC 3 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PTC 4 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PTC 5 fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Sensing lost |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Unbalanced U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Unbalanced I |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Short circuit |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Excitat. chain |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Motor start |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Power bridge |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): Batt supply low |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): CAN supply low |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 1 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 2 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 3 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 4 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): PT100 5 open/short |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AIN1 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AIN2 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AIN3 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AIN4 wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AOUT1 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AOUT2 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AOUT3 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): AOUT4 overload/wirebreak |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 550 events | Alarm(Trip): DOUT overload |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | LED: Power ON |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | LED: Excitation fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | LED: Frequency fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Any DVC350 warning alarms present |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Any DVC350 trip alarms present |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Over voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Under voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Over frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Under frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Open diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Shorted diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Reverse kW |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Reverse kVar |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Loss of sensing |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Unbalance voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Unbalance current |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Short circuit |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): IGBT |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Motor start |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Power bridge overload |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): VBat supply |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): DOUT overload fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Phase rotation direction fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Stator overcurrent U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Stator overcurrent V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Stator overcurrent W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding active power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding active power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding active power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding active power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): I^2T stator fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding apparent power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding apparent power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding apparent power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding apparent power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding reactive power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding reactive power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding reactive power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Warning): Exceeding reactive power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Over voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Under voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Over frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Under frequency |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Open diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Shorted diode |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Reverse kW |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Reverse kVar |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Loss of sensing |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Unbalance voltage |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Unbalance current |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Short circuit |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): IGBT |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Motor start |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Power bridge overload |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): VBat supply |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): DOUT overload fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Phase rotation direction fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Stator overcurrent U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Stator overcurrent V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Stator overcurrent W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding active power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding active power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding active power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding active power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): I^2T stator fault |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding apparent power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding apparent power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding apparent power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding apparent power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding reactive power |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding reactive power U |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding reactive power V |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
DVC 350 events | Alarm(Trip): Exceeding reactive power W |  |  |  | The DVC 550 event is active. See the DVC 550 documentation.
Virtual event output | Virtual event output 1 |  |  |  | Virtual event 1 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 2 |  |  |  | Virtual event 2 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 3 |  |  |  | Virtual event 3 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 4 |  |  |  | Virtual event 4 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 5 |  |  |  | Virtual event 5 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 6 |  |  |  | Virtual event 6 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 7 |  |  |  | Virtual event 7 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 8 |  |  |  | Virtual event 8 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 9 |  |  |  | Virtual event 9 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 10 |  |  |  | Virtual event 10 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 11 |  |  |  | Virtual event 11 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 12 |  |  |  | Virtual event 12 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 13 |  |  |  | Virtual event 13 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 14 |  |  |  | Virtual event 14 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 15 |  |  |  | Virtual event 15 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 16 |  |  |  | Virtual event 16 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 17 |  |  |  | Virtual event 17 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 18 |  |  |  | Virtual event 18 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 19 |  |  |  | Virtual event 19 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 20 |  |  |  | Virtual event 20 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 21 |  |  |  | Virtual event 21 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 22 |  |  |  | Virtual event 22 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 23 |  |  |  | Virtual event 23 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 24 |  |  |  | Virtual event 24 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 25 |  |  |  | Virtual event 25 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 26 |  |  |  | Virtual event 26 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 27 |  |  |  | Virtual event 27 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 28 |  |  |  | Virtual event 28 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 29 |  |  |  | Virtual event 29 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 30 |  |  |  | Virtual event 30 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 31 |  |  |  | Virtual event 31 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 32 |  |  |  | Virtual event 32 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 33 |  |  |  | Virtual event 33 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 34 |  |  |  | Virtual event 34 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 35 |  |  |  | Virtual event 35 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 36 |  |  |  | Virtual event 36 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 37 |  |  |  | Virtual event 37 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 38 |  |  |  | Virtual event 38 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 39 |  |  |  | Virtual event 39 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 40 |  |  |  | Virtual event 40 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 41 |  |  |  | Virtual event 41 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 42 |  |  |  | Virtual event 42 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 43 |  |  |  | Virtual event 43 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 44 |  |  |  | Virtual event 44 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 45 |  |  |  | Virtual event 45 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 46 |  |  |  | Virtual event 46 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 47 |  |  |  | Virtual event 47 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 48 |  |  |  | Virtual event 48 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 49 |  |  |  | Virtual event 49 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 50 |  |  |  | Virtual event 50 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 51 |  |  |  | Virtual event 51 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 52 |  |  |  | Virtual event 52 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 53 |  |  |  | Virtual event 53 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 54 |  |  |  | Virtual event 54 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 55 |  |  |  | Virtual event 55 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 56 |  |  |  | Virtual event 56 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 57 |  |  |  | Virtual event 57 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 58 |  |  |  | Virtual event 58 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 59 |  |  |  | Virtual event 59 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 60 |  |  |  | Virtual event 60 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 61 |  |  |  | Virtual event 61 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 62 |  |  |  | Virtual event 62 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 63 |  |  |  | Virtual event 63 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 64 |  |  |  | Virtual event 64 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 65 |  |  |  | Virtual event 65 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 66 |  |  |  | Virtual event 66 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 67 |  |  |  | Virtual event 67 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 68 |  |  |  | Virtual event 68 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 69 |  |  |  | Virtual event 69 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 70 |  |  |  | Virtual event 70 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 71 |  |  |  | Virtual event 71 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 72 |  |  |  | Virtual event 72 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 73 |  |  |  | Virtual event 73 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 74 |  |  |  | Virtual event 74 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 75 |  |  |  | Virtual event 75 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 76 |  |  |  | Virtual event 76 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 77 |  |  |  | Virtual event 77 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 78 |  |  |  | Virtual event 78 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 79 |  |  |  | Virtual event 79 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 80 |  |  |  | Virtual event 80 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 81 |  |  |  | Virtual event 81 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 82 |  |  |  | Virtual event 82 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 83 |  |  |  | Virtual event 83 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 84 |  |  |  | Virtual event 84 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 85 |  |  |  | Virtual event 85 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 86 |  |  |  | Virtual event 86 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 87 |  |  |  | Virtual event 87 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 88 |  |  |  | Virtual event 88 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 89 |  |  |  | Virtual event 89 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 90 |  |  |  | Virtual event 90 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 91 |  |  |  | Virtual event 91 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 92 |  |  |  | Virtual event 92 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 93 |  |  |  | Virtual event 93 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 94 |  |  |  | Virtual event 94 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 95 |  |  |  | Virtual event 95 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual event output | Virtual event output 96 |  |  |  | Virtual event 96 is activated by M-Logic or Modbus. Virtual events can be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 1 |  |  |  | Virtual toggle 1 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 2 |  |  |  | Virtual toggle 2 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 3 |  |  |  | Virtual toggle 3 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 4 |  |  |  | Virtual toggle 4 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 5 |  |  |  | Virtual toggle 5 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 6 |  |  |  | Virtual toggle 6 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 7 |  |  |  | Virtual toggle 7 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 8 |  |  |  | Virtual toggle 8 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 9 |  |  |  | Virtual toggle 9 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 10 |  |  |  | Virtual toggle 10 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 11 |  |  |  | Virtual toggle 11 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 12 |  |  |  | Virtual toggle 12 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 13 |  |  |  | Virtual toggle 13 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 14 |  |  |  | Virtual toggle 14 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 15 |  |  |  | Virtual toggle 15 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 16 |  |  |  | Virtual toggle 16 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 17 |  |  |  | Virtual toggle 17 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 18 |  |  |  | Virtual toggle 18 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 19 |  |  |  | Virtual toggle 19 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 20 |  |  |  | Virtual toggle 20 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 21 |  |  |  | Virtual toggle 21 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 22 |  |  |  | Virtual toggle 22 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 23 |  |  |  | Virtual toggle 23 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 24 |  |  |  | Virtual toggle 24 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 25 |  |  |  | Virtual toggle 25 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 26 |  |  |  | Virtual toggle 26 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 27 |  |  |  | Virtual toggle 27 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 28 |  |  |  | Virtual toggle 28 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 29 |  |  |  | Virtual toggle 29 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 30 |  |  |  | Virtual toggle 30 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 31 |  |  |  | Virtual toggle 31 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Virtual toggle output | Virtual toggle output 32 |  |  |  | Virtual toggle 32 is activated by M-Logic or Modbus. Virtual toggles can also be used in multiple lines of logic to increase the number of events possible in one sequence.
Flip flops | Flip flop output 1 |  |  |  | M-Logic flip flop 1 is High.
Flip flops | Flip flop output 2 |  |  |  | M-Logic flip flop 2 is High.
Flip flops | Flip flop output 3 |  |  |  | M-Logic flip flop 3 is High.
Flip flops | Flip flop output 4 |  |  |  | M-Logic flip flop 4 is High.
Flip flops | Flip flop output 5 |  |  |  | M-Logic flip flop 5 is High.
Flip flops | Flip flop output 6 |  |  |  | M-Logic flip flop 6 is High.
Flip flops | Flip flop output 7 |  |  |  | M-Logic flip flop 7 is High.
Flip flops | Flip flop output 8 |  |  |  | M-Logic flip flop 8 is High.
Flip flops | Flip flop output 9 |  |  |  | M-Logic flip flop 9 is High.
Flip flops | Flip flop output 10 |  |  |  | M-Logic flip flop 10 is High.
Flip flops | Flip flop output 11 |  |  |  | M-Logic flip flop 11 is High.
Flip flops | Flip flop output 12 |  |  |  | M-Logic flip flop 12 is High.
Flip flops | Flip flop output 13 |  |  |  | M-Logic flip flop 13 is High.
Flip flops | Flip flop output 14 |  |  |  | M-Logic flip flop 14 is High.
Flip flops | Flip flop output 15 |  |  |  | M-Logic flip flop 15 is High.
Flip flops | Flip flop output 16 |  |  |  | M-Logic flip flop 16 is High.
Oneshots | Oneshot output 1 |  | 1120 |  | M-Logic Oneshot 1 is activated.
Oneshots | Oneshot output 2 |  | 1120 |  | M-Logic Oneshot 2 is activated.
Oneshots | Oneshot output 3 |  | 1120 |  | M-Logic Oneshot 3 is activated.
Oneshots | Oneshot output 4 |  | 1120 |  | M-Logic Oneshot 4 is activated.
Oneshots | Oneshot output 5 |  | 1120 |  | M-Logic Oneshot 5 is activated.
Oneshots | Oneshot output 6 |  | 1120 |  | M-Logic Oneshot 6 is activated.
Oneshots | Oneshot output 7 |  | 1120 |  | M-Logic Oneshot 7 is activated.
Oneshots | Oneshot output 8 |  | 1120 |  | M-Logic Oneshot 8 is activated.
Oneshots | Oneshot output 9 |  | 1120 |  | M-Logic Oneshot 9 is activated.
Oneshots | Oneshot output 10 |  | 1120 |  | M-Logic Oneshot 10 is activated.
Oneshots | Oneshot output 11 |  | 1120 |  | M-Logic Oneshot 11 is activated.
Oneshots | Oneshot output 12 |  | 1120 |  | M-Logic Oneshot 12 is activated.
Oneshots | Oneshot output 13 |  | 1120 |  | M-Logic Oneshot 13 is activated.
Oneshots | Oneshot output 14 |  | 1120 |  | M-Logic Oneshot 14 is activated.
Oneshots | Oneshot output 15 |  | 1120 |  | M-Logic Oneshot 15 is activated.
Oneshots | Oneshot output 16 |  | 1120 |  | M-Logic Oneshot 16 is activated.
General Purpose PID | PID1 active |  |  |  | PID1 is active.
General Purpose PID | PID1 at min output |  |  |  | PID1 is at its minimum output.
General Purpose PID | PID1 at max output |  |  |  | PID1 is at its maximum output.
General Purpose PID | PID1 output frozen |  |  |  | The PID1 output is frozen.
General Purpose PID | PID2 active |  |  |  | PID2 is active.
General Purpose PID | PID2 at min output |  |  |  | PID2 is at its minimum output.
General Purpose PID | PID2 at max output |  |  |  | PID2 is at its maximum output.
General Purpose PID | PID2 output frozen |  |  |  | The PID2 output is frozen.
General Purpose PID | PID3 active |  |  |  | PID3 is active.
General Purpose PID | PID3 at min output |  |  |  | PID3 is at its minimum output.
General Purpose PID | PID3 at max output |  |  |  | PID3 is at its maximum output.
General Purpose PID | PID3 output frozen |  |  |  | The PID3 output is frozen.
General Purpose PID | PID4 active |  |  |  | PID4 is active.
General Purpose PID | PID4 at min output |  |  |  | PID4 is at its minimum output.
General Purpose PID | PID4 at max output |  |  |  | PID4 is at its maximum output.
General Purpose PID | PID4 output frozen |  |  |  | The PID4 output is frozen.
General Purpose PID | PID1 using input 1 |  |  |  | PID1 is using input 1.
General Purpose PID | PID1 using input 2 |  |  |  | PID1 is using input 2.
General Purpose PID | PID1 using input 3 |  |  |  | PID1 is using input 3.
General Purpose PID | PID2 using input 1 |  |  |  | PID2 is using input 1.
General Purpose PID | PID2 using input 2 |  |  |  | PID2 is using input 2.
General Purpose PID | PID2 using input 3 |  |  |  | PID2 is using input 3.
General Purpose PID | PID3 using input 1 |  |  |  | PID3 is using input 1.
General Purpose PID | PID3 using input 2 |  |  |  | PID3 is using input 2.
General Purpose PID | PID3 using input 3 |  |  |  | PID3 is using input 3.
General Purpose PID | PID4 using input 1 |  |  |  | PID4 is using input 1.
General Purpose PID | PID4 using input 2 |  |  |  | PID4 is using input 2.
General Purpose PID | PID4 using input 3 |  |  |  | PID4 is using input 3.
General Purpose PID | PID1 modbus control |  |  |  | General purpose PID1 is under Modbus control.
General Purpose PID | PID2 modbus control |  |  |  | General purpose PID2 is under Modbus control.
General Purpose PID | PID3 modbus control |  |  |  | General purpose PID3 is under Modbus control.
General Purpose PID | PID4 modbus control |  |  |  | General purpose PID4 is under Modbus control.
Shortcut - Switch | Shortcut - Switch 1 |  |  |  | M-Logic Shortcut - Switch 1 is active.
Shortcut - Switch | Shortcut - Switch 2 |  |  |  | M-Logic Shortcut - Switch 2 is active.
Shortcut - Switch | Shortcut - Switch 3 |  |  |  | M-Logic Shortcut - Switch 3 is active.
Shortcut - Switch | Shortcut - Switch 4 |  |  |  | M-Logic Shortcut - Switch 4 is active.
Shortcut - Switch | Shortcut - Switch 5 |  |  |  | M-Logic Shortcut - Switch 5 is active.
Shortcut - Switch | Shortcut - Switch 6 |  |  |  | M-Logic Shortcut - Switch 6 is active.
Shortcut - Pulse | Shortcut - Pulse 1 |  |  |  | M-Logic Shortcut - Pulse 1 is active.
Shortcut - Pulse | Shortcut - Pulse 2 |  |  |  | M-Logic Shortcut - Pulse 2 is active.
Shortcut - Pulse | Shortcut - Pulse 3 |  |  |  | M-Logic Shortcut - Pulse 3 is active.
Shortcut - Pulse | Shortcut - Pulse 4 |  |  |  | M-Logic Shortcut - Pulse 4 is active.
Shortcut - Pulse | Shortcut - Pulse 5 |  |  |  | M-Logic Shortcut - Pulse 5 is active.
Shortcut - Pulse | Shortcut - Pulse 6 |  |  |  | M-Logic Shortcut - Pulse 6 is active.
Engine Shortcut - Switch | Engine Shortcut - Switch 1 |  |  |  | Engine Shortcut Switch 1 is active.
Engine Shortcut - Switch | Engine Shortcut - Switch 2 |  |  |  | Engine Shortcut Switch 2 is active.
Engine Shortcut - Pulse | Engine Shortcut - Pulse 1 |  |  |  | Engine Shortcut Pulse 1 is active.
Engine Shortcut - Pulse | Engine Shortcut - Pulse 2 |  |  |  | Engine Shortcut Pulse 2 is active.
M-Logic event counters | M-logic event counter limit 1 |  |  |  | M-Logic event counter 1 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 2 |  |  |  | M-Logic event counter 2 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 3 |  |  |  | M-Logic event counter 3 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 4 |  |  |  | M-Logic event counter 4 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 5 |  |  |  | M-Logic event counter 5 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 6 |  |  |  | M-Logic event counter 6 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 7 |  |  |  | M-Logic event counter 7 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter limit 8 |  |  |  | M-Logic event counter 8 has reached its limit (Counters > M-Logic event counters).
M-Logic event counters | M-logic event reset counter 1 |  |  |  | M-Logic event counter 1 is reset.
M-Logic event counters | M-logic event reset counter 2 |  |  |  | M-Logic event counter 2 is reset.
M-Logic event counters | M-logic event reset counter 3 |  |  |  | M-Logic event counter 3 is reset.
M-Logic event counters | M-logic event reset counter 4 |  |  |  | M-Logic event counter 4 is reset.
M-Logic event counters | M-logic event reset counter 5 |  |  |  | M-Logic event counter 5 is reset.
M-Logic event counters | M-logic event reset counter 6 |  |  |  | M-Logic event counter 6 is reset.
M-Logic event counters | M-logic event reset counter 7 |  |  |  | M-Logic event counter 7 is reset.
M-Logic event counters | M-logic event reset counter 8 |  |  |  | M-Logic event counter 8 is reset.
Display keypress events | Up |  |  |  | The Up button on the display folio is pushed.
Display keypress events | Down |  |  |  | The Down button on the display folio is pushed.
Display keypress events | Left |  |  |  | The Left button on the display folio is pushed.
Display keypress events | Right |  |  |  | The Right button on the display folio is pushed.
Display keypress events | Escape |  |  |  | The Back button on the display folio is pushed.
Display keypress events | Select |  |  |  | The OK button on the display folio is pushed.
Display keypress events | Start |  |  |  | The Start button on the display mimic is pushed.
Display keypress events | Stop |  |  |  | The Stop button on the display mimic is pushed.
Display keypress events | GB close |  |  |  | The GB close button on the display mimic is pushed.
Display keypress events | GB open |  |  |  | The GB open button on the display mimic is pushed.
Display keypress events | MB close |  |  |  | The MB close button on the display mimic is pushed.
Display keypress events | MB open |  |  |  | The MB open button on the display mimic is pushed.
Display keypress events | AUTO mode |  |  |  | The controller is in automatic mode.
Display keypress events | MANUAL mode |  |  |  | The controller is in manual mode (called semi-auto before SW version 1.30).
Display keypress events | Alarm list |  |  |  | The Alarm button on the display folio is pushed.
Display keypress events | Command menu |  |  |  | The Menu button on the display folio is pushed.

## PMS_lite_M-Logic_Outputs
Category | Name | Option | From SW | To SW | Controller action when the output is activated
PMS lite commands | PLC control start |  |  |  | If PLC control is active, start the genset.
PMS lite commands | PLC control stop |  |  |  | If PLC control is active, stop the genset.
PMS lite commands | Enable multi start |  |  |  | Change Multi start config (parameter 8521) to Enabled.
PMS lite commands | Disable multi start |  |  |  | Change Multi start config (parameter 8521) to Not enabled.
PMS lite commands | Share PMS lite setpoints |  |  |  | Share the PMS lite parameters. This corresponds to selecting On in Share parameters (parameter 8514).
PMS lite commands | Set LDSS control |  |  |  | Use the controller's PMS lite load-dependent start and stop settings, and ignore the start and stop commands from a PLC. This corresponds to selecting Load dependent start/stop in PMS lite start/stop (parameter 8505).
PMS lite commands | Set PLC control |  |  |  | Use start and stop commands from a PLC, and ignore the PMS lite load-dependent start and stop settings. This corresponds to selecting PLC start/stop in PMS lite start/stop (parameter 8505).
PMS lite commands | Set multi start failure mode to no action |  |  |  | Change Multi start config (parameter 8521) to No action on fail.
PMS lite commands | Set multi start failure mode to start all DGs |  |  |  | Change Multi start config (parameter 8521) to Start all other DGs.
PMS lite commands | Start all available DGs |  | 1190 |  | Start all avaliable (AUTO and ready to start) DGs.
PMS lite commands | Genset on DUTY (force to run) |  | 1190 |  | Genset on DUTY (force to run)
Application config commands | Apply configuration |  |  |  | Applies the configuration.
Application config commands | Set pulse MB |  |  |  | Sets the mains breaker type to pulse.
Application config commands | Set no MB |  |  |  | Sets the mains breaker type to no mains breaker.
Application config commands | Set continuous MB |  |  |  | Sets the mains breaker type to continuous.
Application config commands | Set compact MB |  |  |  | Sets the mains breaker type to compact.
Application config commands | Set pulse GB |  |  |  | Sets the generator breaker type to pulse.
Application config commands | Set continuous GB |  |  |  | Sets the generator breaker type to continuous.
Application config commands | Set compact GB |  |  |  | Sets the generator breaker type to compact.
Application config commands | Set mains present |  |  |  | Configures an application with a mains connection.
Application config commands | Set no mains present |  |  |  | Configures an application with no mains connection.
Application config commands | No mains present + CAN B PMS lite + Apply config |  | 1180 |  | Sets the CAN B protocol to PMS lite, configures an application with no mains connection, and applies the configuration.
Application config commands | Mains present + CAN B OFF + Apply config |  | 1180 |  | Sets the CAN B protocol to Off, configures an application with a mains connection, and applies the configuration.
Command | Lamp test |  |  |  | Runs a lamp test.
Command | Force backlight and LEDs OFF |  | 1090 |  | Turn off the display backlight and LEDs.
Command | Ack. all alarms |  |  |  | Acknowledge all alarms.
Command | Set clock to 4 AM |  |  |  | Set the controller clock to 04h00.
Command | Derate Pnom 1 |  |  |  | Derates the power.
Command | Derate Pnom 2 |  |  |  | Derates the power.
Command | Derate Pnom 3 |  |  |  | Derates the power.
Command | Select test type to simple |  |  |  | Changes the test type to simple.
Command | Select test type to load |  |  |  | Changes the test type to load.
Command | Select test type to full |  |  |  | Changes the test type to full.
Command | Freeze ramp |  |  |  | Freezes the ramp.
Command | Inductive reference |  |  |  | Changes the cos phi type (7053) to inductive.
Command | Capacitive reference |  |  |  | Changes the cos phi type (7053) to capacitive.
Command | Enable analog LS via IOM |  |  |  | Enables analogue load sharing using an IOM.
Command | Fan A running |  |  |  | Regards Fan A as running.
Command | Fan B running |  |  |  | Regards Fan B as running.
Command | Fan C running |  |  |  | Regards Fan C as running.
Command | Fan D running |  |  |  | Regards Fan D as running.
Command | Act. power offset 1 |  |  |  | Activates power offset 1.
Command | Act. power offset 2 |  |  |  | Activates power offset 2.
Command | Act. power offset 3 |  |  |  | Activates power offset 3.
Command | Deact. power offset 1 |  |  |  | Deactivates power offset 1.
Command | Deact. power offset 2 |  |  |  | Deactivates power offset 2.
Command | Deact. power offset 3 |  |  |  | Deactivates power offset 3.
Command | Act. cosphi offset 1 |  |  |  | Activates cos phi offset 1.
Command | Act. cosphi offset 2 |  |  |  | Activates cos phi offset 2.
Command | Act. cosphi offset 3 |  |  |  | Activates cos phi offset 3.
Command | Deact. cosphi offset 1 |  |  |  | Deactivates cos phi offset 1.
Command | Deact. cosphi offset 2 |  |  |  | Deactivates cos phi offset 2.
Command | Deact. cosphi offset 3 |  |  |  | Deactivates cos phi offset 3.
Command | Activate Fuel pump |  |  |  | Activates the fuel pump relay.
Command | Activate DEF pump |  | 1130 |  | Activates the DEF pump relay.
Command | Activate Generic pump |  | 1130 |  | Activates the generic pump relay.
Command | Inhibit Fuel pump |  | 1370 |  | Inhibit Fuel pump operation.
Command | Inhibit DEF pump |  | 1370 |  | Inhibit DEF pump operation.
Command | Inhibit Generic pump |  | 1370 |  | Inhibit Generic pump operation.
Command | Reset horn |  |  |  | Reset the alarm horn function.
Command | Reset rel. counter |  |  |  | Reset the relative counter.
Command | Reset I max demand |  |  |  | Reset the maximum current demand counter.
Command | Reset I thermal demand |  |  |  | Reset the current thermal demand counter.
Command | Pulse counter 1 |  |  |  | Adds 1 to pulse counter 1.
Command | Pulse counter 2 |  |  |  | Adds 1 to pulse counter 2.
Command | Reset pulse counter 1 |  |  |  | Resets pulse counter 1.
Command | Reset pulse counter 2 |  |  |  | Resets pulse counter 2.
Command | Force use of analogue offset set 1 |  |  |  | This command forces the selected analogue offset 1 to be active.
Command | Force use of analogue offset set 2 |  |  |  | This command forces the selected analogue offset 2 to be active.
Command | Force use of analogue offset set 3 |  |  |  | This command forces the selected analogue offset 3 to be active.
Command | Force use of analogue offset set 4 |  |  |  | This command forces the selected analogue offset 4 to be active.
Command | Force use of analogue offset set 5 |  | 1210 |  | This command forces the selected analogue offset 5 to be active.
Command | Force use of analogue offset set 6 |  | 1210 |  | This command forces the selected analogue offset 6 to be active.
Command | Ack Mains protection alarms |  |  |  | Acknowledges all mains alarms.
Command | Act. max ventilation |  |  |  | Activates maximum ventilation.
Command | Deact. max ventilation |  |  |  | Deactivates maximum ventilation.
Command | Mains Okay |  |  |  | If an input has been configured to Mains Okay, the command Mains Okay is given. This command is sometimes called External Mains Okay.
Command | Access lock |  |  |  | Display button access is locked.
Command | Reset Service Timer 1 |  |  |  | Resets Service Timer 1.
Command | Reset Service Timer 2 |  |  |  | Resets Service Timer 2.
Command | Activate Ramp Speed 1 |  |  |  | Activates Ramp Speed 1.
Command | Activate Ramp Speed 2 |  |  |  | Activates Ramp Speed 2.
Command | Activate Warm Up Ramp |  |  |  | Activates a warm up ramp.
Command | Activate active power control via comm |  | 1220 |  | Activate active power control via communication
Command | Activate frequency control via comm |  | 1220 |  | Activate frequency control via communication
Command | Activate voltage control via comm |  | 1220 |  | Activate voltage control via communication
Command | Activate cosphi control via comm |  | 1220 |  | Activate cosphi control via communication
Command | Activate reactive power control via comm |  | 1220 |  | Activate reactive power control via communication
Command | Deactivate active power control via comm |  | 1220 |  | Deactivate active power control via communication
Command | Deactivate frequency control via comm |  | 1220 |  | Deactivate frequency control via communication
Command | Deactivate voltage control via comm |  | 1220 |  | Deactivate voltage control via communication
Command | Deactivate cosphi control via comm |  | 1220 |  | Deactivate cosphi control via communication
Command | Deactivate reactive power control via comm |  | 1220 |  | Deactivate reactive power control via communication
Command AC | Select three phase system |  |  |  | Select 3-phase system (parameter 9131).
Command AC | Select split L1L3 phase system |  |  |  | Select split-phase (L1L3) system (parameter 9131).
Command AC | Select split L1L2 phase system |  |  |  | Select split-phase (L1L2) system (parameter 9131).
Command AC | Select single phase system |  |  |  | Select single-phase system (parameter 9131).
Command AC | Select L1L2L3 phase rotation |  |  |  | Select L1L2L3 phase rotation (parameter 2154).
Command AC | Select L1L3L2 phase rotation |  |  |  | Select L1L3L2 phase rotation (parameter 2154).
Command Parameter set | Set parameter 1 |  |  |  | Choose the parameter set for nominal settings 1
Command Parameter set | Set parameter 2 |  |  |  | Choose the parameter set for nominal settings 2
Command Parameter set | Set parameter 3 |  |  |  | Choose the parameter set for nominal settings 3
Command Parameter set | Set parameter 4 |  |  |  | Choose the parameter set for nominal settings 4
Command Parameter set | Set parameter 5 |  | 1210 |  | Choose the parameter set for nominal settings 5
Command Parameter set | Set parameter 6 |  | 1210 |  | Choose the parameter set for nominal settings 6
Command Parameter set | Set BB parameter 1 |  |  |  | Select the parameter set for busbar nominal settings 1
Command Parameter set | Set BB parameter 2 |  |  |  | Select the parameter set for busbar nominal settings 2
Command Parameter set | Set BB Unom = Gen Unom |  |  |  | Busbar nominal voltage is equal to the generator nominal voltage.
Command Engine | Battery test |  |  |  | Activates a battery test.
Command Engine | Eng. heater manual ctrl. |  |  |  | Enables or disables the engine heater function.
Command Engine | Auto start/stop |  |  |  | Activates auto start/stop.
Command Engine | Force Gen Start in AUTO |  | 1050 |  | Forces the genset to start, even if the controller mode is auto.
Command Engine | Remote start |  |  |  | Activates a pulse signal for remote start.
Command Engine | Remote stop |  |  |  | Activates a pulse signal for remote stop.
Command Engine | Idle run low speed |  |  |  | Starts low speed idle running.
Command Engine | Idle run temp control |  |  |  | Starts temperature controlled idle running.
Command Engine | Cool down threshold |  |  |  | Interrupts the cool down sequence.
Command Engine | Shutdown override |  |  |  | The shutdown override input is activated.
Command Engine | Alternative start |  |  |  | Activates alternative start.
Command Engine | Activate Idle run |  |  |  | Activates idle run.
Command Engine | Deactivate Idle run |  |  |  | Deactivates idle run.
Command Breakers | GB close inhibit |  |  |  | The controller does not allow the GB to close.
Command Breakers | Open GB |  |  |  | Open the GB breaker.
Command Breakers | Close GB |  |  |  | Close the GB breaker.
Command Breakers | Open MB |  |  |  | Close the mains breaker.
Command Breakers | Close MB |  |  |  | Open the mains breaker.
Command Breakers | Force GB ON in AUTO |  | 1050 |  | Forces the GB to close, even if the controller mode is auto.
Command Breakers | MB close inhibit |  |  |  | The controller does not allow the MB to close.
Command Breakers | Mains sync. inhibit activate |  |  |  | The controller does not allow the MB to synchronise.
Command Breakers | Mains sync. inhibit deactivate |  |  |  | The controller allows the MB to synchronise.
Command M-Logic and AOP | M-Logic alarm 1 |  |  |  | Activate M-Logic alarm 1.
Command M-Logic and AOP | M-Logic alarm 2 |  |  |  | Activate M-Logic alarm 2.
Command M-Logic and AOP | M-Logic alarm 3 |  |  |  | Activate M-Logic alarm 3.
Command M-Logic and AOP | M-Logic alarm 4 |  |  |  | Activate M-Logic alarm 4.
Command M-Logic and AOP | M-Logic alarm 5 |  |  |  | Activate M-Logic alarm 5.
Command M-Logic and AOP | M-Logic alarm 10 |  | 1180 |  | Activate M-Logic alarm 10.
Command M-Logic and AOP | M-Logic alarm 11 |  | 1180 |  | Activate M-Logic alarm 11.
Command M-Logic and AOP | M-Logic alarm 12 |  | 1180 |  | Activate M-Logic alarm 12.
Command M-Logic and AOP | M-Logic alarm 13 |  | 1180 |  | Activate M-Logic alarm 13.
Command M-Logic and AOP | M-Logic alarm 14 |  | 1180 |  | Activate M-Logic alarm 14.
Command M-Logic and AOP | M-Logic ext alarm 1: Start extended timer |  | 1060 |  | Starts the extended timer for M-Logic ext alarm 1.
Command M-Logic and AOP | M-Logic ext alarm 2: Start extended timer |  | 1060 |  | Starts the extended timer for M-Logic ext alarm 2.
Command M-Logic and AOP | M-Logic ext alarm 3: Start extended timer |  | 1060 |  | Starts the extended timer for M-Logic ext alarm 3.
Command M-Logic and AOP | M-Logic ext alarm 4: Start extended timer |  | 1060 |  | Starts the extended timer for M-Logic ext alarm 4.
Command M-Logic and AOP | M-Logic ext alarm 1: Reset extended timer |  | 1060 |  | Resets the extended timer for M-Logic ext alarm 1.
Command M-Logic and AOP | M-Logic ext alarm 2: Reset extended timer |  | 1060 |  | Resets the extended timer for M-Logic ext alarm 2.
Command M-Logic and AOP | M-Logic ext alarm 3: Reset extended timer |  | 1060 |  | Resets the extended timer for M-Logic ext alarm 3.
Command M-Logic and AOP | M-Logic ext alarm 4: Reset extended timer |  | 1060 |  | Resets the extended timer for M-Logic ext alarm 4.
Command M-Logic and AOP | Activate relay on AOP2 ID 1 |  |  |  | Activates the relay on AOP2 ID 1.
Command M-Logic and AOP | Activate relay on AOP2 ID 2 | S4 PREMIUM |  |  | Activates the relay on AOP2 ID 2.
Command M-Logic and AOP | Activate buzzer on AOP2 ID 1 |  |  |  | Activates the buzzer on AOP2 ID 1.
Command M-Logic and AOP | Activate buzzer on AOP2 ID 2 | S4 PREMIUM |  |  | Activates the buzzer on AOP2 ID 2.
Command M-Logic and AOP | Activate All AOP2 buzzers |  |  |  | Activates all AOP2 buzzers.
Command M-Logic and AOP | Activate All AOP2 relays |  |  |  | Activates all AOP2 relays.
Modes | Island |  |  |  | Change the controller mode to island.
Modes | AMF |  |  |  | Change the controller mode to automatic mains failure.
Modes | Peak shaving |  |  |  | Change the controller mode to peak shaving.
Modes | Fixed power |  |  |  | Change the controller mode to fixed power.
Modes | Mains power export |  |  |  | Change the controller mode to mains power export.
Modes | Load take over |  |  |  | Change the controller mode to load take over.
Modes | TEST mode |  |  |  | Change the controller mode to test mode.
Modes | AUTO mode |  |  |  | Change the controller mode to automatic (no manual control).
Modes | Semi-auto mode |  |  | 1299 | Change the controller mode to semi-auto (that is, as if the semi-auto button was pushed on the display) (only up to SW version 1.29).
Modes | MANUAL mode |  | 1300 |  | Change the controller mode to Manual (that is, as if the Manual button was pushed on the display) (called semi-auto before SW version 1.30).
Modes | MANUAL Mode |  |  | 1299 | Change the controller mode to Manual (that is, as if the Manual button was pushed on the display) (only up to SW version 1.29).
Modes | No reg mode |  | 1300 |  | Change the controller mode to no regulation (that is, as if the no regulation button was pushed on the display) (called manual before SW version 1.30).
Modes | BLOCK Mode |  |  |  | Change the controller mode to block.
Relays | Not used |  |  |  | -
Relays | Relay 5 |  |  |  | Activate Relay 5.
Relays | Relay 6 |  |  |  | Activate Relay 6.
Relays | Relay 9 |  |  |  | Activate Relay 9.
Relays | Relay 10 |  |  |  | Activate Relay 10.
Relays | Relay 11 |  |  |  | Activate Relay 11.
Relays | Relay 12 |  |  |  | Activate Relay 12.
Relays | Relay 13 |  |  |  | Activate Relay 13.
Relays | Relay 14 |  |  |  | Activate Relay 14.
Relays | Relay 15 |  |  |  | Activate Relay 15.
Relays | Relay 16 |  |  |  | Activate Relay 16.
Relays | Relay 17 |  |  |  | Activate Relay 17.
Relays | Relay 18 |  |  |  | Activate Relay 18.
CIO outputs | CIO 208 no.1 Out. 9 |  |  |  | Activate CIO 208 no.1 Out. 9.
CIO outputs | CIO 208 no.1 Out. 11 |  |  |  | Activate CIO 208 no.1 Out. 11.
CIO outputs | CIO 208 no.1 Out. 13 |  |  |  | Activate CIO 208 no.1 Out. 13.
CIO outputs | CIO 208 no.1 Out. 15 |  |  |  | Activate CIO 208 no.1 Out. 15.
CIO outputs | CIO 208 no.1 Out. 18 |  |  |  | Activate CIO 208 no.1 Out. 18.
CIO outputs | CIO 208 no.1 Out. 21 |  |  |  | Activate CIO 208 no.1 Out. 21.
CIO outputs | CIO 208 no.1 Out. 24 |  |  |  | Activate CIO 208 no.1 Out. 24.
CIO outputs | CIO 208 no.1 Out. 27 |  |  |  | Activate CIO 208 no.1 Out. 27.
CIO outputs | CIO 208 no.2 Out. 9 |  |  |  | Activate CIO 208 no.2 Out. 9.
CIO outputs | CIO 208 no.2 Out. 11 |  |  |  | Activate CIO 208 no.2 Out. 11.
CIO outputs | CIO 208 no.2 Out. 13 |  |  |  | Activate CIO 208 no.2 Out. 13.
CIO outputs | CIO 208 no.2 Out. 15 |  |  |  | Activate CIO 208 no.2 Out. 15.
CIO outputs | CIO 208 no.2 Out. 18 |  |  |  | Activate CIO 208 no.2 Out. 18.
CIO outputs | CIO 208 no.2 Out. 21 |  |  |  | Activate CIO 208 no.2 Out. 21.
CIO outputs | CIO 208 no.2 Out. 24 |  |  |  | Activate CIO 208 no.2 Out. 24.
CIO outputs | CIO 208 no.2 Out. 27 |  |  |  | Activate CIO 208 no.2 Out. 27.
CIO outputs | CIO 208 no.3 Out. 9 |  |  |  | Activate CIO 208 no.3 Out. 9.
CIO outputs | CIO 208 no.3 Out. 11 |  |  |  | Activate CIO 208 no.3 Out. 11.
CIO outputs | CIO 208 no.3 Out. 13 |  |  |  | Activate CIO 208 no.3 Out. 13.
CIO outputs | CIO 208 no.3 Out. 15 |  |  |  | Activate CIO 208 no.3 Out. 15.
CIO outputs | CIO 208 no.3 Out. 18 |  |  |  | Activate CIO 208 no.3 Out. 18.
CIO outputs | CIO 208 no.3 Out. 21 |  |  |  | Activate CIO 208 no.3 Out. 21.
CIO outputs | CIO 208 no.3 Out. 24 |  |  |  | Activate CIO 208 no.3 Out. 24.
CIO outputs | CIO 208 no.3 Out. 27 |  |  |  | Activate CIO 208 no.3 Out. 27.
CIO outputs | CIO 116 no.1 conf. status output |  |  |  | Activate CIO 116 no.1 conf. status output.
CIO outputs | CIO 116 no.2 conf. status output |  |  |  | Activate CIO 116 no.2 conf. status output.
CIO outputs | CIO 116 no.3 conf. status output |  |  |  | Activate CIO 116 no.3 conf. status output.
CIO outputs | CIO 208 no.1 conf. status output |  |  |  | Activate CIO 208 no.1 conf. status output.
CIO outputs | CIO 208 no.2 conf. status output |  |  |  | Activate CIO 208 no.2 conf. status output.
CIO outputs | CIO 208 no.3 conf. status output |  |  |  | Activate CIO 208 no.3 conf. status output.
CIO outputs | CIO 308 no.1 conf. status output |  |  |  | Activate CIO 308 no.1 conf. status output.
CIO outputs | CIO 308 no.2 conf. status output |  |  |  | Activate CIO 308 no.2 conf. status output.
CIO outputs | CIO 308 no.3 conf. status output |  |  |  | Activate CIO 308 no.3 conf. status output.
Inhibits/Activate/Deactivate | Not used |  |  |  | -
Inhibits/Activate/Deactivate | Deactivate Mode change via Mode Cmd |  |  |  | Deactivate the AUTO and MANUAL mode buttons on the display.
Inhibits/Activate/Deactivate | Deactivate OFF selection via Mode Cmd |  |  |  | Deactivate the OFF (block) selection from the display.
Inhibits/Activate/Deactivate | Inh. start button |  |  |  | Deactivate the start button on the display.
Inhibits/Activate/Deactivate | Inh. stop button |  |  |  | Deactivate the stop button on the display.
Inhibits/Activate/Deactivate | Inh. engine start |  |  |  | The controller does not allow the engine to start.
Inhibits/Activate/Deactivate | Inh. GB buttons |  |  |  | Deactivate the GB open and close buttons on the display.
Inhibits/Activate/Deactivate | Inh. MB buttons |  |  |  | Deactivate the MB open and close buttons on the display.
Inhibits/Activate/Deactivate | Inh. GB black close |  |  |  | The controller does not allow GB black close.
Inhibits/Activate/Deactivate | Inh. regulation |  |  |  | Deactivate regulation.
Inhibits/Activate/Deactivate | Inh. CANShare |  |  |  | The controller does not use CANShare load sharing.
Inhibits/Activate/Deactivate | Inh. analogue load share |  |  |  | The controller does not use analogue load sharing.
Inhibits/Activate/Deactivate | Inh. acknowledge in AUTO |  |  |  | Inhibit alarm acknowledge in AUTO mode.
Inhibits/Activate/Deactivate | Inh. modbus commands |  |  |  | Inhibit Modbus commands to this controller.
Inhibits/Activate/Deactivate | Inhibit 1 |  |  |  | Activate User configurable alarm inhibit 1 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inhibit 2 |  |  |  | Activate User configurable alarm inhibit 2 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inhibit 3 |  |  |  | Activate User configurable alarm inhibit 3 (to inhibit alarms with this inhibit).
Inhibits/Activate/Deactivate | Inh. AOP2_1 buttons |  |  |  | Deactivate all the buttons on AOP2 number 1.
Inhibits/Activate/Deactivate | Inh. AOP2_2 buttons | S4 PREMIUM |  |  | Deactivate all the buttons on AOP2 number 2.
Inhibits/Activate/Deactivate | Activate short time parallel |  |  |  | Activates short time parallel.
Inhibits/Activate/Deactivate | Deactivate short time parallel |  |  |  | Deactivates short time parallel.
Inhibits/Activate/Deactivate | Activate modeshift |  |  |  | Activate AMF mode automatically.
Inhibits/Activate/Deactivate | Deactivate modeshift |  |  |  | Deactivate AMF mode automatically.
CAN B Set | OFF |  |  |  | Change the selection for CAN B to Off.
CAN B Set | Canshare |  |  |  | Changes the CAN B protocol (7842) to Canshare.
CAN B Set | PMS Lite |  |  |  | Changes the CAN B protocol (7842) to PMS Lite.
CANshare/PMS lite flags | CANshare/PMS lite flag 1 |  |  |  | Activates CANshare/PMS lite flag 1.
CANshare/PMS lite flags | CANshare/PMS lite flag 2 |  |  |  | Activates CANshare/PMS lite flag 2.
CANshare/PMS lite flags | CANshare/PMS lite flag 3 |  |  |  | Activates CANshare/PMS lite flag 3.
CANshare/PMS lite flags | CANshare/PMS lite flag 4 |  |  |  | Activates CANshare/PMS lite flag 4.
CANshare/PMS lite flags | CANshare/PMS lite flag 5 |  |  |  | Activates CANshare/PMS lite flag 5.
CANshare/PMS lite flags | CANshare/PMS lite flag 6 |  |  |  | Activates CANshare/PMS lite flag 6.
CANshare/PMS lite flags | CANshare/PMS lite flag 7 |  |  |  | Activates CANshare/PMS lite flag 7.
CANshare/PMS lite flags | CANshare/PMS lite flag 8 |  |  |  | Activates CANshare/PMS lite flag 8.
CANshare/PMS lite flags | CANshare/PMS lite flag 9 |  |  |  | Activates CANshare/PMS lite flag 9.
CANshare/PMS lite flags | CANshare/PMS lite flag 10 |  |  |  | Activates CANshare/PMS lite flag 10.
CANshare/PMS lite flags | CANshare/PMS lite flag 11 |  |  |  | Activates CANshare/PMS lite flag 11.
CANshare/PMS lite flags | CANshare/PMS lite flag 12 |  |  |  | Activates CANshare/PMS lite flag 12.
CANshare/PMS lite flags | CANshare/PMS lite flag 13 |  |  |  | Activates CANshare/PMS lite flag 13.
CANshare/PMS lite flags | CANshare/PMS lite flag 14 |  |  |  | Activates CANshare/PMS lite flag 14.
CANshare/PMS lite flags | CANshare/PMS lite flag 15 |  |  |  | Activates CANshare/PMS lite flag 15.
CANshare/PMS lite flags | CANshare/PMS lite flag 16 |  |  |  | Activates CANshare/PMS lite flag 16.
CANshare/PMS lite flags | CANshare/PMS lite flag 17 |  |  |  | Activates CANshare/PMS lite flag 17.
CANshare/PMS lite flags | CANshare/PMS lite flag 18 |  |  |  | Activates CANshare/PMS lite flag 18.
CANshare/PMS lite flags | CANshare/PMS lite flag 19 |  |  |  | Activates CANshare/PMS lite flag 19.
CANshare/PMS lite flags | CANshare/PMS lite flag 20 |  |  |  | Activates CANshare/PMS lite flag 20.
CANshare/PMS lite flags | CANshare/PMS lite flag 21 |  |  |  | Activates CANshare/PMS lite flag 21.
CANshare/PMS lite flags | CANshare/PMS lite flag 22 |  |  |  | Activates CANshare/PMS lite flag 22.
CANshare/PMS lite flags | CANshare/PMS lite flag 23 |  |  |  | Activates CANshare/PMS lite flag 23.
CANshare/PMS lite flags | CANshare/PMS lite flag 24 |  |  |  | Activates CANshare/PMS lite flag 24.
CANshare/PMS lite flags | CANshare/PMS lite flag 25 |  |  |  | Activates CANshare/PMS lite flag 25.
CANshare/PMS lite flags | CANshare/PMS lite flag 26 |  |  |  | Activates CANshare/PMS lite flag 26.
CANshare/PMS lite flags | CANshare/PMS lite flag 27 |  |  |  | Activates CANshare/PMS lite flag 27.
CANshare/PMS lite flags | CANshare/PMS lite flag 28 |  |  |  | Activates CANshare/PMS lite flag 28.
CANshare/PMS lite flags | CANshare/PMS lite flag 29 |  |  |  | Activates CANshare/PMS lite flag 29.
CANshare/PMS lite flags | CANshare/PMS lite flag 30 |  |  |  | Activates CANshare/PMS lite flag 30.
CANshare/PMS lite flags | CANshare/PMS lite flag 31 |  |  |  | Activates CANshare/PMS lite flag 31.
CANshare/PMS lite flags | CANshare/PMS lite flag 32 |  |  |  | Activates CANshare/PMS lite flag 32.
CANshare/PMS lite flags | CANshare/PMS lite flag 33 |  |  |  | Activates CANshare/PMS lite flag 33.
CANshare/PMS lite flags | CANshare/PMS lite flag 34 |  |  |  | Activates CANshare/PMS lite flag 34.
CANshare/PMS lite flags | CANshare/PMS lite flag 35 |  |  |  | Activates CANshare/PMS lite flag 35.
CANshare/PMS lite flags | CANshare/PMS lite flag 36 |  |  |  | Activates CANshare/PMS lite flag 36.
CANshare/PMS lite flags | CANshare/PMS lite flag 37 |  |  |  | Activates CANshare/PMS lite flag 37.
CANshare/PMS lite flags | CANshare/PMS lite flag 38 |  |  |  | Activates CANshare/PMS lite flag 38.
CANshare/PMS lite flags | CANshare/PMS lite flag 39 |  |  |  | Activates CANshare/PMS lite flag 39.
CANshare/PMS lite flags | CANshare/PMS lite flag 40 |  |  |  | Activates CANshare/PMS lite flag 40.
CANshare/PMS lite flags | CANshare/PMS lite flag 41 |  |  |  | Activates CANshare/PMS lite flag 41.
CANshare/PMS lite flags | CANshare/PMS lite flag 42 |  |  |  | Activates CANshare/PMS lite flag 42.
CANshare/PMS lite flags | CANshare/PMS lite flag 43 |  |  |  | Activates CANshare/PMS lite flag 43.
CANshare/PMS lite flags | CANshare/PMS lite flag 44 |  |  |  | Activates CANshare/PMS lite flag 44.
CANshare/PMS lite flags | CANshare/PMS lite flag 45 |  |  |  | Activates CANshare/PMS lite flag 45.
CANshare/PMS lite flags | CANshare/PMS lite flag 46 |  |  |  | Activates CANshare/PMS lite flag 46.
CANshare/PMS lite flags | CANshare/PMS lite flag 47 |  |  |  | Activates CANshare/PMS lite flag 47.
CANshare/PMS lite flags | CANshare/PMS lite flag 48 |  |  |  | Activates CANshare/PMS lite flag 48.
CANshare/PMS lite flags | CANshare/PMS lite flag 49 |  |  |  | Activates CANshare/PMS lite flag 49.
CANshare/PMS lite flags | CANshare/PMS lite flag 50 |  |  |  | Activates CANshare/PMS lite flag 50.
CANshare/PMS lite flags | CANshare/PMS lite flag 51 |  |  |  | Activates CANshare/PMS lite flag 51.
CANshare/PMS lite flags | CANshare/PMS lite flag 52 |  |  |  | Activates CANshare/PMS lite flag 52.
CANshare/PMS lite flags | CANshare/PMS lite flag 53 |  |  |  | Activates CANshare/PMS lite flag 53.
CANshare/PMS lite flags | CANshare/PMS lite flag 54 |  |  |  | Activates CANshare/PMS lite flag 54.
CANshare/PMS lite flags | CANshare/PMS lite flag 55 |  |  |  | Activates CANshare/PMS lite flag 55.
CANshare/PMS lite flags | CANshare/PMS lite flag 56 |  |  |  | Activates CANshare/PMS lite flag 56.
CANshare/PMS lite flags | CANshare/PMS lite flag 57 |  |  |  | Activates CANshare/PMS lite flag 57.
CANshare/PMS lite flags | CANshare/PMS lite flag 58 |  |  |  | Activates CANshare/PMS lite flag 58.
CANshare/PMS lite flags | CANshare/PMS lite flag 59 |  |  |  | Activates CANshare/PMS lite flag 59.
CANshare/PMS lite flags | CANshare/PMS lite flag 60 |  |  |  | Activates CANshare/PMS lite flag 60.
CANshare/PMS lite flags | CANshare/PMS lite flag 61 |  |  |  | Activates CANshare/PMS lite flag 61.
CANshare/PMS lite flags | CANshare/PMS lite flag 62 |  |  |  | Activates CANshare/PMS lite flag 62.
CANshare/PMS lite flags | CANshare/PMS lite flag 63 |  |  |  | Activates CANshare/PMS lite flag 63.
CANshare/PMS lite flags | CANshare/PMS lite flag 64 |  |  |  | Activates CANshare/PMS lite flag 64.
CANshare/PMS lite flags | CANshare/PMS lite flag 65 |  |  |  | Activates CANshare/PMS lite flag 65.
CANshare/PMS lite flags | CANshare/PMS lite flag 66 |  |  |  | Activates CANshare/PMS lite flag 66.
CANshare/PMS lite flags | CANshare/PMS lite flag 67 |  |  |  | Activates CANshare/PMS lite flag 67.
CANshare/PMS lite flags | CANshare/PMS lite flag 68 |  |  |  | Activates CANshare/PMS lite flag 68.
CANshare/PMS lite flags | CANshare/PMS lite flag 69 |  |  |  | Activates CANshare/PMS lite flag 69.
CANshare/PMS lite flags | CANshare/PMS lite flag 70 |  |  |  | Activates CANshare/PMS lite flag 70.
CANshare/PMS lite flags | CANshare/PMS lite flag 71 |  |  |  | Activates CANshare/PMS lite flag 71.
CANshare/PMS lite flags | CANshare/PMS lite flag 72 |  |  |  | Activates CANshare/PMS lite flag 72.
CANshare/PMS lite flags | CANshare/PMS lite flag 73 |  |  |  | Activates CANshare/PMS lite flag 73.
CANshare/PMS lite flags | CANshare/PMS lite flag 74 |  |  |  | Activates CANshare/PMS lite flag 74.
CANshare/PMS lite flags | CANshare/PMS lite flag 75 |  |  |  | Activates CANshare/PMS lite flag 75.
CANshare/PMS lite flags | CANshare/PMS lite flag 76 |  |  |  | Activates CANshare/PMS lite flag 76.
CANshare/PMS lite flags | CANshare/PMS lite flag 77 |  |  |  | Activates CANshare/PMS lite flag 77.
CANshare/PMS lite flags | CANshare/PMS lite flag 78 |  |  |  | Activates CANshare/PMS lite flag 78.
CANshare/PMS lite flags | CANshare/PMS lite flag 79 |  |  |  | Activates CANshare/PMS lite flag 79.
CANshare/PMS lite flags | CANshare/PMS lite flag 80 |  |  |  | Activates CANshare/PMS lite flag 80.
CANshare/PMS lite flags | CANshare/PMS lite flag 81 |  |  |  | Activates CANshare/PMS lite flag 81.
CANshare/PMS lite flags | CANshare/PMS lite flag 82 |  |  |  | Activates CANshare/PMS lite flag 82.
CANshare/PMS lite flags | CANshare/PMS lite flag 83 |  |  |  | Activates CANshare/PMS lite flag 83.
CANshare/PMS lite flags | CANshare/PMS lite flag 84 |  |  |  | Activates CANshare/PMS lite flag 84.
CANshare/PMS lite flags | CANshare/PMS lite flag 85 |  |  |  | Activates CANshare/PMS lite flag 85.
CANshare/PMS lite flags | CANshare/PMS lite flag 86 |  |  |  | Activates CANshare/PMS lite flag 86.
CANshare/PMS lite flags | CANshare/PMS lite flag 87 |  |  |  | Activates CANshare/PMS lite flag 87.
CANshare/PMS lite flags | CANshare/PMS lite flag 88 |  |  |  | Activates CANshare/PMS lite flag 88.
CANshare/PMS lite flags | CANshare/PMS lite flag 89 |  |  |  | Activates CANshare/PMS lite flag 89.
CANshare/PMS lite flags | CANshare/PMS lite flag 90 |  |  |  | Activates CANshare/PMS lite flag 90.
CANshare/PMS lite flags | CANshare/PMS lite flag 91 |  |  |  | Activates CANshare/PMS lite flag 91.
CANshare/PMS lite flags | CANshare/PMS lite flag 92 |  |  |  | Activates CANshare/PMS lite flag 92.
CANshare/PMS lite flags | CANshare/PMS lite flag 93 |  |  |  | Activates CANshare/PMS lite flag 93.
CANshare/PMS lite flags | CANshare/PMS lite flag 94 |  |  |  | Activates CANshare/PMS lite flag 94.
CANshare/PMS lite flags | CANshare/PMS lite flag 95 |  |  |  | Activates CANshare/PMS lite flag 95.
CANshare/PMS lite flags | CANshare/PMS lite flag 96 |  |  |  | Activates CANshare/PMS lite flag 96.
CANshare/PMS lite flags | CANshare/PMS lite flag 97 |  |  |  | Activates CANshare/PMS lite flag 97.
CANshare/PMS lite flags | CANshare/PMS lite flag 98 |  |  |  | Activates CANshare/PMS lite flag 98.
CANshare/PMS lite flags | CANshare/PMS lite flag 99 |  |  |  | Activates CANshare/PMS lite flag 99.
CANshare/PMS lite flags | CANshare/PMS lite flag 100 |  |  |  | Activates CANshare/PMS lite flag 100.
CANshare/PMS lite flags | CANshare/PMS lite flag 101 |  |  |  | Activates CANshare/PMS lite flag 101.
CANshare/PMS lite flags | CANshare/PMS lite flag 102 |  |  |  | Activates CANshare/PMS lite flag 102.
CANshare/PMS lite flags | CANshare/PMS lite flag 103 |  |  |  | Activates CANshare/PMS lite flag 103.
CANshare/PMS lite flags | CANshare/PMS lite flag 104 |  |  |  | Activates CANshare/PMS lite flag 104.
CANshare/PMS lite flags | CANshare/PMS lite flag 105 |  |  |  | Activates CANshare/PMS lite flag 105.
CANshare/PMS lite flags | CANshare/PMS lite flag 106 |  |  |  | Activates CANshare/PMS lite flag 106.
CANshare/PMS lite flags | CANshare/PMS lite flag 107 |  |  |  | Activates CANshare/PMS lite flag 107.
CANshare/PMS lite flags | CANshare/PMS lite flag 108 |  |  |  | Activates CANshare/PMS lite flag 108.
CANshare/PMS lite flags | CANshare/PMS lite flag 109 |  |  |  | Activates CANshare/PMS lite flag 109.
CANshare/PMS lite flags | CANshare/PMS lite flag 110 |  |  |  | Activates CANshare/PMS lite flag 110.
CANshare/PMS lite flags | CANshare/PMS lite flag 111 |  |  |  | Activates CANshare/PMS lite flag 111.
CANshare/PMS lite flags | CANshare/PMS lite flag 112 |  |  |  | Activates CANshare/PMS lite flag 112.
CANshare/PMS lite flags | CANshare/PMS lite flag 113 |  |  |  | Activates CANshare/PMS lite flag 113.
CANshare/PMS lite flags | CANshare/PMS lite flag 114 |  |  |  | Activates CANshare/PMS lite flag 114.
CANshare/PMS lite flags | CANshare/PMS lite flag 115 |  |  |  | Activates CANshare/PMS lite flag 115.
CANshare/PMS lite flags | CANshare/PMS lite flag 116 |  |  |  | Activates CANshare/PMS lite flag 116.
CANshare/PMS lite flags | CANshare/PMS lite flag 117 |  |  |  | Activates CANshare/PMS lite flag 117.
CANshare/PMS lite flags | CANshare/PMS lite flag 118 |  |  |  | Activates CANshare/PMS lite flag 118.
CANshare/PMS lite flags | CANshare/PMS lite flag 119 |  |  |  | Activates CANshare/PMS lite flag 119.
CANshare/PMS lite flags | CANshare/PMS lite flag 120 |  |  |  | Activates CANshare/PMS lite flag 120.
CANshare/PMS lite flags | CANshare/PMS lite flag 121 |  |  |  | Activates CANshare/PMS lite flag 121.
CANshare/PMS lite flags | CANshare/PMS lite flag 122 |  |  |  | Activates CANshare/PMS lite flag 122.
CANshare/PMS lite flags | CANshare/PMS lite flag 123 |  |  |  | Activates CANshare/PMS lite flag 123.
CANshare/PMS lite flags | CANshare/PMS lite flag 124 |  |  |  | Activates CANshare/PMS lite flag 124.
CANshare/PMS lite flags | CANshare/PMS lite flag 125 |  |  |  | Activates CANshare/PMS lite flag 125.
CANshare/PMS lite flags | CANshare/PMS lite flag 126 |  |  |  | Activates CANshare/PMS lite flag 126.
CANshare/PMS lite flags | CANshare/PMS lite flag 127 |  |  |  | Activates CANshare/PMS lite flag 127.
CANshare/PMS lite flags | CANshare/PMS lite flag 128 |  |  |  | Activates CANshare/PMS lite flag 128.
CANshare/PMS lite flags | BB 1 |  |  |  | Activates BB 1.
CANshare/PMS lite flags | BB 2 |  |  |  | Activates BB 2.
CANshare/PMS lite flags | BB 3 |  |  |  | Activates BB 3.
CANshare/PMS lite flags | BB 4 |  |  |  | Activates BB 4.
CANshare/PMS lite flags | BB 5 |  |  |  | Activates BB 5.
CANshare/PMS lite flags | BB 6 |  |  |  | Activates BB 6.
CANshare/PMS lite flags | BB 7 |  |  |  | Activates BB 7.
CANshare/PMS lite flags | BB 8 |  |  |  | Activates BB 8.
CANshare/PMS lite flags | BB 9 |  |  |  | Activates BB 9.
CANshare/PMS lite flags | BB 10 |  |  |  | Activates BB 10.
CANshare/PMS lite flags | BB 11 |  |  |  | Activates BB 11.
CANshare/PMS lite flags | BB 12 |  |  |  | Activates BB 12.
CANshare/PMS lite flags | BB 13 |  |  |  | Activates BB 13.
CANshare/PMS lite flags | BB 14 |  |  |  | Activates BB 14.
CANshare/PMS lite flags | BB 15 |  |  |  | Activates BB 15.
CANshare/PMS lite flags | BB 16 |  |  |  | Activates BB 16.
CANshare/PMS lite flags | BB 17 |  |  |  | Activates BB 17.
CANshare/PMS lite flags | BB 18 |  |  |  | Activates BB 18.
CANshare/PMS lite flags | BB 19 |  |  |  | Activates BB 19.
CANshare/PMS lite flags | BB 20 |  |  |  | Activates BB 20.
CANshare/PMS lite flags | BB 21 |  |  |  | Activates BB 21.
CANshare/PMS lite flags | BB 22 |  |  |  | Activates BB 22.
CANshare/PMS lite flags | BB 23 |  |  |  | Activates BB 23.
CANshare/PMS lite flags | BB 24 |  |  |  | Activates BB 24.
CANshare/PMS lite flags | BB 25 |  |  |  | Activates BB 25.
CANshare/PMS lite flags | BB 26 |  |  |  | Activates BB 26.
CANshare/PMS lite flags | BB 27 |  |  |  | Activates BB 27.
CANshare/PMS lite flags | BB 28 |  |  |  | Activates BB 28.
CANshare/PMS lite flags | BB 29 |  |  |  | Activates BB 29.
CANshare/PMS lite flags | BB 30 |  |  |  | Activates BB 30.
CANshare/PMS lite flags | BB 31 |  |  |  | Activates BB 31.
CANshare/PMS lite flags | BB 32 |  |  |  | Activates BB 32.
CANshare/PMS lite flags | BB 33 |  |  |  | Activates BB 33.
CANshare/PMS lite flags | BB 34 |  |  |  | Activates BB 34.
CANshare/PMS lite flags | BB 35 |  |  |  | Activates BB 35.
CANshare/PMS lite flags | BB 36 |  |  |  | Activates BB 36.
CANshare/PMS lite flags | BB 37 |  |  |  | Activates BB 37.
CANshare/PMS lite flags | BB 38 |  |  |  | Activates BB 38.
CANshare/PMS lite flags | BB 39 |  |  |  | Activates BB 39.
CANshare/PMS lite flags | BB 40 |  |  |  | Activates BB 40.
CANshare/PMS lite flags | BB 41 |  |  |  | Activates BB 41.
CANshare/PMS lite flags | BB 42 |  |  |  | Activates BB 42.
CANshare/PMS lite flags | BB 43 |  |  |  | Activates BB 43.
CANshare/PMS lite flags | BB 44 |  |  |  | Activates BB 44.
CANshare/PMS lite flags | BB 45 |  |  |  | Activates BB 45.
CANshare/PMS lite flags | BB 46 |  |  |  | Activates BB 46.
CANshare/PMS lite flags | BB 47 |  |  |  | Activates BB 47.
CANshare/PMS lite flags | BB 48 |  |  |  | Activates BB 48.
CANshare/PMS lite flags | BB 49 |  |  |  | Activates BB 49.
CANshare/PMS lite flags | BB 50 |  |  |  | Activates BB 50.
CANshare/PMS lite flags | BB 51 |  |  |  | Activates BB 51.
CANshare/PMS lite flags | BB 52 |  |  |  | Activates BB 52.
CANshare/PMS lite flags | BB 53 |  |  |  | Activates BB 53.
CANshare/PMS lite flags | BB 54 |  |  |  | Activates BB 54.
CANshare/PMS lite flags | BB 55 |  |  |  | Activates BB 55.
CANshare/PMS lite flags | BB 56 |  |  |  | Activates BB 56.
CANshare/PMS lite flags | BB 57 |  |  |  | Activates BB 57.
CANshare/PMS lite flags | BB 58 |  |  |  | Activates BB 58.
CANshare/PMS lite flags | BB 59 |  |  |  | Activates BB 59.
CANshare/PMS lite flags | BB 60 |  |  |  | Activates BB 60.
CANshare/PMS lite flags | BB 61 |  |  |  | Activates BB 61.
CANshare/PMS lite flags | BB 62 |  |  |  | Activates BB 62.
CANshare/PMS lite flags | BB 63 |  |  |  | Activates BB 63.
CANshare/PMS lite flags | BB 64 |  |  |  | Activates BB 64.
Display - View control | Act. view 1 on display |  |  |  | Activates view 1 on the display.
Display - View control | Act. view 2 on display |  |  |  | Activates view 2 on the display.
Display - View control | Act. view 3 on display |  |  |  | Activates view 3 on the display.
Display - View control | Act. view 4 on display |  |  |  | Activates view 4 on the display.
Display - View control | Act. view 5 on display |  |  |  | Activates view 5 on the display.
Display - View control | Act. view 6 on display |  |  |  | Activates view 6 on the display.
Display - View control | Act. view 7 on display |  |  |  | Activates view 7 on the display.
Display - View control | Act. view 8 on display |  |  |  | Activates view 8 on the display.
Display - View control | Act. view 9 on display |  |  |  | Activates view 9 on the display.
Display - View control | Act. view 10 on display |  |  |  | Activates view 10 on the display.
Display - View control | Act. view 11 on display |  |  |  | Activates view 11 on the display.
Display - View control | Act. view 12 on display |  |  |  | Activates view 12 on the display.
Display - View control | Act. view 13 on display |  |  |  | Activates view 13 on the display.
Display - View control | Act. view 14 on display |  |  |  | Activates view 14 on the display.
Display - View control | Act. view 15 on display |  |  |  | Activates view 15 on the display.
Display - View control | Act. view 16 on display |  |  |  | Activates view 16 on the display.
Display - View control | Act. view 17 on display |  |  |  | Activates view 17 on the display.
Display - View control | Act. view 18 on display |  |  |  | Activates view 18 on the display.
Display - View control | Act. view 19 on display |  |  |  | Activates view 19 on the display.
Display - View control | Act. view 20 on display |  |  |  | Activates view 20 on the display.
Display - View control | Act. power reference menu on display 1 |  |  |  | Activate the power reference menu on display 1.
Display - View control | Act. test power reference menu on display 1 |  |  |  | Activate the test power reference menu on display 1.
Display - View control | Act. cosphi reference menu on display 1 |  |  |  | Activate the cos phi reference menu on display 1.
Display - View-line control | Activate view-line 1_1 |  |  |  | Activates view-line 1_1.
Display - View-line control | Activate view-line 1_2 |  |  |  | Activates view-line 1_2.
Display - View-line control | Activate view-line 1_3 |  |  |  | Activates view-line 1_3.
Display - View-line control | Activate view-line 1_4 |  |  |  | Activates view-line 1_4.
Display - View-line control | Activate view-line 1_5 |  |  |  | Activates view-line 1_5.
Display - View-line control | Activate view-line 2_1 |  |  |  | Activates view-line 2_1.
Display - View-line control | Activate view-line 2_2 |  |  |  | Activates view-line 2_2.
Display - View-line control | Activate view-line 2_3 |  |  |  | Activates view-line 2_3.
Display - View-line control | Activate view-line 2_4 |  |  |  | Activates view-line 2_4.
Display - View-line control | Activate view-line 2_5 |  |  |  | Activates view-line 2_5.
Display - View-line control | Activate view-line 3_1 |  |  |  | Activates view-line 3_1.
Display - View-line control | Activate view-line 3_2 |  |  |  | Activates view-line 3_2.
Display - View-line control | Activate view-line 3_3 |  |  |  | Activates view-line 3_3.
Display - View-line control | Activate view-line 3_4 |  |  |  | Activates view-line 3_4.
Display - View-line control | Activate view-line 3_5 |  |  |  | Activates view-line 3_5.
Display - View-line control | Activate view-line 4_1 |  |  |  | Activates view-line 4_1.
Display - View-line control | Activate view-line 4_2 |  |  |  | Activates view-line 4_2.
Display - View-line control | Activate view-line 4_3 |  |  |  | Activates view-line 4_3.
Display - View-line control | Activate view-line 4_4 |  |  |  | Activates view-line 4_4.
Display - View-line control | Activate view-line 4_5 |  |  |  | Activates view-line 4_5.
Display - View-line control | Activate view-line 5_1 |  |  |  | Activates view-line 5_1.
Display - View-line control | Activate view-line 5_2 |  |  |  | Activates view-line 5_2.
Display - View-line control | Activate view-line 5_3 |  |  |  | Activates view-line 5_3.
Display - View-line control | Activate view-line 5_4 |  |  |  | Activates view-line 5_4.
Display - View-line control | Activate view-line 5_5 |  |  |  | Activates view-line 5_5.
Display - Remote display setup | OFF |  |  |  | Select the function of the remote display: OFF (non-functional, no alarms from remote display).
Display - Remote display setup | ON: View only |  |  |  | Select the function of the remote display: ON: View only.
Display - Remote display setup | ON: View and control |  |  |  | Select the function of the remote display: ON: View and control.
Display - Keyboard commands | Start |  |  |  | Start the genset (that is, as if the Start button was pushed on the display).
Display - Keyboard commands | Stop |  |  |  | Stop the genset (that is, as if the Stop button was pushed on the display).
Display - Keyboard commands | GB close |  |  |  | Close the GB (that is, as if the GB close button was pushed on the display).
Display - Keyboard commands | GB open |  |  |  | Open the GB (that is, as if the GB open button was pushed on the display).
Display - Keyboard commands | MB close |  |  |  | Close the MB (that is, as if the MB close button was pushed on the display).
Display - Keyboard commands | MB open |  |  |  | Open the MB (that is, as if the MB open button was pushed on the display).
Display - Keyboard commands | AUTO mode |  |  |  | Change the controller mode to Auto (that is, as if the Auto button was pushed on the display).
Display - Keyboard commands | MANUAL mode |  |  |  | Change the controller mode to Manual (that is, as if the Manual button was pushed on the display).
Display - Keyboard commands | Alarm list |  |  |  | Show the alarm list on the display (that is, as if the Alarm button was pushed on the display).
Gov/AVR control | Gov increase pulse |  |  |  | Increases the governor reference by a small amount.
Gov/AVR control | Gov decrease pulse |  |  |  | Decreases the governor reference by a small amount.
Gov/AVR control | Freeze Gov regulation |  |  |  | Freezes the governor regulation.
Gov/AVR control | AVR increase pulse |  |  |  | Increases the AVR reference by a small amount.
Gov/AVR control | AVR decrease pulse |  |  |  | Decreases the AVR reference by a small amount.
Gov/AVR control | Freeze AVR regulation |  |  |  | Freezes the AVR regulation.
Gov/AVR control | Ext Frequency (Gov): Input 20 |  |  |  | Uses Input 20 as the external frequency set point for the governor.
Gov/AVR control | Ext Frequency (Gov): Input 21 |  |  |  | Uses Input 21 as the external frequency set point for the governor.
Gov/AVR control | Ext Frequency (Gov): Input 22 |  |  |  | Uses Input 22 as the external frequency set point for the governor.
Gov/AVR control | Ext Frequency (Gov): Input 23 |  |  |  | Uses Input 23 as the external frequency set point for the governor.
Gov/AVR control | Ext Power (Gov): Input 20 |  |  |  | Uses Input 20 as the external power set point for the governor.
Gov/AVR control | Ext Power (Gov): Input 21 |  |  |  | Uses Input 21 as the external power set point for the governor.
Gov/AVR control | Ext Power (Gov): Input 22 |  |  |  | Uses Input 22 as the external power set point for the governor.
Gov/AVR control | Ext Power (Gov): Input 23 |  |  |  | Uses Input 23 as the external power set point for the governor.
Gov/AVR control | Ext Voltage (AVR): Input 20 |  |  |  | Uses Input 20 as the external voltage set point for the AVR.
Gov/AVR control | Ext Voltage (AVR): Input 21 |  |  |  | Uses Input 21 as the external voltage set point for the AVR.
Gov/AVR control | Ext Voltage (AVR): Input 22 |  |  |  | Uses Input 22 as the external voltage set point for the AVR.
Gov/AVR control | Ext Voltage (AVR): Input 23 |  |  |  | Uses Input 23 as the external voltage set point for the AVR.
Gov/AVR control | Ext Cos Phi (AVR): Input 20 |  |  |  | Uses Input 20 as the external cos phi set point for the AVR.
Gov/AVR control | Ext Cos Phi (AVR): Input 21 |  |  |  | Uses Input 21 as the external cos phi set point for the AVR.
Gov/AVR control | Ext Cos Phi (AVR): Input 22 |  |  |  | Uses Input 22 as the external cos phi set point for the AVR.
Gov/AVR control | Ext Cos Phi (AVR): Input 23 |  |  |  | Uses Input 23 as the external cos phi set point for the AVR.
Gov/AVR control | Ext Var (AVR): Input 20 |  |  |  | Uses Input 20 as the external reactive power set point for the AVR.
Gov/AVR control | Ext Var (AVR): Input 21 |  |  |  | Uses Input 21 as the external reactive power set point for the AVR.
Gov/AVR control | Ext Var (AVR): Input 22 |  |  |  | Uses Input 22 as the external reactive power set point for the AVR.
Gov/AVR control | Ext Var (AVR): Input 23 |  |  |  | Uses Input 23 as the external reactive power set point for the AVR.
Gov/AVR control | Act. Frequency droop regulation |  |  |  | Activates frequency droop regulation.
Gov/AVR control | Act. Voltage droop regulation |  |  |  | Activates voltage droop regulation.
Gov/AVR control | Reset analog output (Gov & AVR) |  |  |  | Resets the analogue output for the governor and AVR.
Static sync. type | GB: Breaker
Static sync. type | GB: Infinite
Static sync. type | MB: Breaker
Static sync. type | MB Infinite
EIC commands | EIC droop |  |  |  | If the droop parameters are enabled in the iE 150, the iE 150 commands the ECU to activate the droop function. Cummins: The iE 150 sends the droop set point to the ECU. Scania and Volvo Penta: The iE 150 sends an enable to the ECU.
EIC commands | EIC droop emulation |  |  |  | The iE 150 uses the droop setting in parameter 2771. The iE 150 adjusts the speed set point to emulate droop. This is useful if a droop set point cannot be sent to the ECU.
EIC commands | EIC Reset trip fuel |  |  |  | The iE 150 commands the ECU to reset the trip counter for fuel.
EIC commands | EIC Enable Cylinder Cutout |  |  |  | The ECU is allowed to use cylinder cut-out.
EIC commands | EIC Engine overspeed test |  |  |  | The iE 150 makes the ECU perform a overspeed test. Instead of raising the RPM, the overspeed alarms limits are lowered.
EIC commands | EIC Intermittent oil priming |  |  |  | Engage the pre-lubrication oil pump (if installed). The command is activated through M-Logic (Output, EIC commands, EIC Intermittent oil priming).
EIC commands | EIC Engine opr mode command |  |  |  | Switches the operating mode of the engine. The command is activated through M-Logic (Output, EIC commands, EIC Engine opr mode command).
EIC commands | EIC Engine speed gov param command |  |  |  | Parameter switch for selection between: Default and Variant 1. M-Logic is used to select variant 1 parameters (Output, EIC Commands, EIC Engine speed gov param command). The function is MTU-specific
EIC commands | EIC DPF Regeneration Inhibit |  |  |  | The iE 150 commands the ECU to inhibit the regeneration of the Diesel Particulate Filter.
EIC commands | EIC DPF Regeneration Force |  |  |  | The iE 150 commands the ECU to regenerate the Diesel Particulate Filter.
EIC commands | Inh. ECU alarms |  |  |  | When this command is active, the iE 150 will not shutdown the engine based on EIC alarms. This is typically necessary while the engine is stopping. The following alarms are inhibited: 1. EIC red alarm. 2. EIC yellow alarm. 3. EIC malfunction. 4. EIC protection.
EIC commands | EIC Select Cummins PCC1301 |  |  |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Start/Stop enable |  |  |  | The iE 150 transmits PGN65223, SPN 786 (2 bits) to control start and stop. Engine start command: The iE 150 transmits 00: Injection enable. Engine stop command: The iE 150 transmits 01: Injection disable. The default transmission is 01. The iE 150 also transmits PGN65223, SPN 3542 (4 bits) to control start and stop: 0000: Normal engine shutdown on engine stop command. 0001: Rapid engine shutdown on engine stop command. 0100: Rapid engine start on engine start command. If EIC normal engine start is activated at the same time, the iE 150 replaces 0100: Rapid engine start with 0011: Normal engine start. Alternatively, you can use EIC Start/Stop, parameter 15090.
EIC commands | EIC Speed Control Inhibit (TSC1) |  |  |  | The iE 150 will not send a speed set point to the ECU.
EIC commands | EIC Interval Priming |  |  |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Priming On Engine Start |  |  |  | The iE 150 commands the ECU to activate priming on engine start.
EIC commands | EIC Speed Increase |  |  |  | This command increases the speed of the engine by a small amount. The command is activated through M-Logic (Output, EIC commands, EIC Speed Increase).
EIC commands | EIC Speed Decrease |  |  |  | This command decreases the speed of the engine by a small amount. The command is activated through M-Logic (Output, EIC commands, EIC Speed Decrease).
EIC commands | EIC binary Speed IncrDecr Enable |  |  |  | The ECU uses (or does not use) EIC binary speed for the speed bias. The command is activated through M-Logic (Output, EIC commands, EIC binary Speed In-De Enable). The function is MTU-specific.
EIC commands | EIC MTU Alternate Droop Setting |  |  |  | If the M-Logic command (Output, EIC Commands, EIC MTU Alternate Droop Setting) is activated, the ACG commands the ECU to activate droop, using the setting in parameter 2771. The function is MTU-specific.
EIC commands | EIC MTU inhibit AL speed demand |  |  |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC MTU inhibit Shutdown override |  |  |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC JDEC Stationary regeneration setting |  |  |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Isuzu Escape mode command |  | 1060 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Parking brake switch |  | 1110 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Wait to start inhibit |  | 1110 |  | When this command is active, the iE 150 does not use the wait to start function.
EIC commands | EIC KWG ISO5 test telegram |  | 1120 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC KWG ISO5 reset telegram |  | 1120 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC KWG ISO5 buzzer reset telegram |  | 1120 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Scania EMS2 S8 Activate Safe regeneration signal |  | 1150 |  | Proprietary command. Sends a signal to the ECU to activate a heat break in the exhaust system.
EIC commands | EIC CAT ADEM6 Disable AT regen switch |  | 1150 |  | Proprietary command
EIC commands | EIC Yanmar Stage V Accelerator Interlock Switch |  | 1150 |  | Activates the EIC command. See the EIC documentation.
EIC commands | EIC Allow safe regeneration |  | 1160 |  | An additional condition for the iE 150 safe regeneration command.
EIC commands | EIC Inhibit DM1 protection lamp alarm |  | 1160 |  | Inhibits this DM1 alarm.
EIC commands | EIC Inhibit DM1 yellow lamp alarm |  | 1160 |  | Inhibits this DM1 alarm.
EIC commands | EIC Inhibit DM1 red lamp alarm |  | 1160 |  | Inhibits this DM1 alarm.
EIC commands | EIC Inhibit DM1 malfunction lamp alarm |  | 1160 |  | Inhibits this DM1 alarm.
EIC commands | EIC Enable Diagnostics |  | 1190 |  | Enable Diagnostics (menu 6701)
EIC commands | EIC Volvo EMS Preheat handled by ECU |  | 1200 |  | Preheat sequence is not requested from iE 150 because it is handled by EMS.
EIC commands | EIC CVT transmission enable |  | 1300 |  | Enable CVT transmission functionality
EIC commands | EIC CVT TVSI mode |  | 1300 |  | Enable CVT TVSI mode
EIC commands | EIC CVT normal mode |  | 1300 |  | Enable CVT normal mode
EIC commands | Guascor Fluxing Start |  | 1320 |  | Set startmode to fluxing for Guascor protocol.
EIC commands | EIC Fuel pump primer |  | 1350 |  | Set fuel pump primer activation (SPN 4082). Only active for Perkins CPCB IV.
DVC310 / DVC550 commands | Set stator current limitation off |  |  |  | Activates the DVC command. See the DVC documentation.
DVC310 / DVC550 commands | Set stator current limitation TM |  |  |  | Activates the DVC command. See the DVC documentation.
DVC310 / DVC550 commands | Set stator current limitation IM |  |  |  | Activates the DVC command. See the DVC documentation.
DVC310 / DVC550 commands | Reset trip alarms |  |  |  | Activates the DVC command. See the DVC documentation.
DVC350 commands | Reset fault alarms |  |  |  | Activates the DVC command. See the DVC documentation.
AOP Led 01 | Not used |  |  |  | Deactivate AOP LED 01.
AOP Led 01 | Red + Blink |  |  |  | AOP LED 01 is red and flashes.
AOP Led 01 | Red |  |  |  | AOP LED 01 is red continuously.
AOP Led 01 | Yellow + Blink |  |  |  | AOP LED 01 is yellow and flashes.
AOP Led 01 | Yellow |  |  |  | AOP LED 01 is yellow continuously.
AOP Led 01 | Green + Blink |  |  |  | AOP LED 01 is green and flashes.
AOP Led 01 | Green |  |  |  | AOP LED 01 is green continuously.
AOP Led 02 | Not used |  |  |  | Deactivate AOP LED 02.
AOP Led 02 | Red + Blink |  |  |  | AOP LED 02 is red and flashes.
AOP Led 02 | Red |  |  |  | AOP LED 02 is red continuously.
AOP Led 02 | Yellow + Blink |  |  |  | AOP LED 02 is yellow and flashes.
AOP Led 02 | Yellow |  |  |  | AOP LED 02 is yellow continuously.
AOP Led 02 | Green + Blink |  |  |  | AOP LED 02 is green and flashes.
AOP Led 02 | Green |  |  |  | AOP LED 02 is green continuously.
AOP Led 03 | Not used |  |  |  | Deactivate AOP LED 03.
AOP Led 03 | Red + Blink |  |  |  | AOP LED 03 is red and flashes.
AOP Led 03 | Red |  |  |  | AOP LED 03 is red continuously.
AOP Led 03 | Yellow + Blink |  |  |  | AOP LED 03 is yellow and flashes.
AOP Led 03 | Yellow |  |  |  | AOP LED 03 is yellow continuously.
AOP Led 03 | Green + Blink |  |  |  | AOP LED 03 is green and flashes.
AOP Led 03 | Green |  |  |  | AOP LED 03 is green continuously.
AOP Led 04 | Not used |  |  |  | Deactivate AOP LED 04.
AOP Led 04 | Red + Blink |  |  |  | AOP LED 04 is red and flashes.
AOP Led 04 | Red |  |  |  | AOP LED 04 is red continuously.
AOP Led 04 | Yellow + Blink |  |  |  | AOP LED 04 is yellow and flashes.
AOP Led 04 | Yellow |  |  |  | AOP LED 04 is yellow continuously.
AOP Led 04 | Green + Blink |  |  |  | AOP LED 04 is green and flashes.
AOP Led 04 | Green |  |  |  | AOP LED 04 is green continuously.
AOP Led 05 | Not used |  |  |  | Deactivate AOP LED 05.
AOP Led 05 | Red + Blink |  |  |  | AOP LED 05 is red and flashes.
AOP Led 05 | Red |  |  |  | AOP LED 05 is red continuously.
AOP Led 05 | Yellow + Blink |  |  |  | AOP LED 05 is yellow and flashes.
AOP Led 05 | Yellow |  |  |  | AOP LED 05 is yellow continuously.
AOP Led 05 | Green + Blink |  |  |  | AOP LED 05 is green and flashes.
AOP Led 05 | Green |  |  |  | AOP LED 05 is green continuously.
AOP Led 06 | Not used |  |  |  | Deactivate AOP LED 06.
AOP Led 06 | Red + Blink |  |  |  | AOP LED 06 is red and flashes.
AOP Led 06 | Red |  |  |  | AOP LED 06 is red continuously.
AOP Led 06 | Yellow + Blink |  |  |  | AOP LED 06 is yellow and flashes.
AOP Led 06 | Yellow |  |  |  | AOP LED 06 is yellow continuously.
AOP Led 06 | Green + Blink |  |  |  | AOP LED 06 is green and flashes.
AOP Led 06 | Green |  |  |  | AOP LED 06 is green continuously.
AOP Led 07 | Not used |  |  |  | Deactivate AOP LED 07.
AOP Led 07 | Red + Blink |  |  |  | AOP LED 07 is red and flashes.
AOP Led 07 | Red |  |  |  | AOP LED 07 is red continuously.
AOP Led 07 | Yellow + Blink |  |  |  | AOP LED 07 is yellow and flashes.
AOP Led 07 | Yellow |  |  |  | AOP LED 07 is yellow continuously.
AOP Led 07 | Green + Blink |  |  |  | AOP LED 07 is green and flashes.
AOP Led 07 | Green |  |  |  | AOP LED 07 is green continuously.
AOP Led 08 | Not used |  |  |  | Deactivate AOP LED 08.
AOP Led 08 | Red + Blink |  |  |  | AOP LED 08 is red and flashes.
AOP Led 08 | Red |  |  |  | AOP LED 08 is red continuously.
AOP Led 08 | Yellow + Blink |  |  |  | AOP LED 08 is yellow and flashes.
AOP Led 08 | Yellow |  |  |  | AOP LED 08 is yellow continuously.
AOP Led 08 | Green + Blink |  |  |  | AOP LED 08 is green and flashes.
AOP Led 08 | Green |  |  |  | AOP LED 08 is green continuously.
AOP Led 09 | Not used |  |  |  | Deactivate AOP LED 09.
AOP Led 09 | Red + Blink |  |  |  | AOP LED 09 is red and flashes.
AOP Led 09 | Red |  |  |  | AOP LED 09 is red continuously.
AOP Led 09 | Yellow + Blink |  |  |  | AOP LED 09 is yellow and flashes.
AOP Led 09 | Yellow |  |  |  | AOP LED 09 is yellow continuously.
AOP Led 09 | Green + Blink |  |  |  | AOP LED 09 is green and flashes.
AOP Led 09 | Green |  |  |  | AOP LED 09 is green continuously.
AOP Led 10 | Not used |  |  |  | Deactivate AOP LED 10.
AOP Led 10 | Red + Blink |  |  |  | AOP LED 10 is red and flashes.
AOP Led 10 | Red |  |  |  | AOP LED 10 is red continuously.
AOP Led 10 | Yellow + Blink |  |  |  | AOP LED 10 is yellow and flashes.
AOP Led 10 | Yellow |  |  |  | AOP LED 10 is yellow continuously.
AOP Led 10 | Green + Blink |  |  |  | AOP LED 10 is green and flashes.
AOP Led 10 | Green |  |  |  | AOP LED 10 is green continuously.
AOP Led 11 | Not used |  |  |  | Deactivate AOP LED 11.
AOP Led 11 | Red + Blink |  |  |  | AOP LED 11 is red and flashes.
AOP Led 11 | Red |  |  |  | AOP LED 11 is red continuously.
AOP Led 11 | Yellow + Blink |  |  |  | AOP LED 11 is yellow and flashes.
AOP Led 11 | Yellow |  |  |  | AOP LED 11 is yellow continuously.
AOP Led 11 | Green + Blink |  |  |  | AOP LED 11 is green and flashes.
AOP Led 11 | Green |  |  |  | AOP LED 11 is green continuously.
AOP Led 12 | Not used |  |  |  | Deactivate AOP LED 12.
AOP Led 12 | Red + Blink |  |  |  | AOP LED 12 is red and flashes.
AOP Led 12 | Red |  |  |  | AOP LED 12 is red continuously.
AOP Led 12 | Yellow + Blink |  |  |  | AOP LED 12 is yellow and flashes.
AOP Led 12 | Yellow |  |  |  | AOP LED 12 is yellow continuously.
AOP Led 12 | Green + Blink |  |  |  | AOP LED 12 is green and flashes.
AOP Led 12 | Green |  |  |  | AOP LED 12 is green continuously.
AOP Led 13 | Not used |  |  |  | Deactivate AOP LED 13.
AOP Led 13 | Red + Blink |  |  |  | AOP LED 13 is red and flashes.
AOP Led 13 | Red |  |  |  | AOP LED 13 is red continuously.
AOP Led 13 | Yellow + Blink |  |  |  | AOP LED 13 is yellow and flashes.
AOP Led 13 | Yellow |  |  |  | AOP LED 13 is yellow continuously.
AOP Led 13 | Green + Blink |  |  |  | AOP LED 13 is green and flashes.
AOP Led 13 | Green |  |  |  | AOP LED 13 is green continuously.
AOP Led 14 | Not used |  |  |  | Deactivate AOP LED 14.
AOP Led 14 | Red + Blink |  |  |  | AOP LED 14 is red and flashes.
AOP Led 14 | Red |  |  |  | AOP LED 14 is red continuously.
AOP Led 14 | Yellow + Blink |  |  |  | AOP LED 14 is yellow and flashes.
AOP Led 14 | Yellow |  |  |  | AOP LED 14 is yellow continuously.
AOP Led 14 | Green + Blink |  |  |  | AOP LED 14 is green and flashes.
AOP Led 14 | Green |  |  |  | AOP LED 14 is green continuously.
AOP Led 15 | Not used |  |  |  | Deactivate AOP LED 15.
AOP Led 15 | Red + Blink |  |  |  | AOP LED 15 is red and flashes.
AOP Led 15 | Red |  |  |  | AOP LED 15 is red continuously.
AOP Led 15 | Yellow + Blink |  |  |  | AOP LED 15 is yellow and flashes.
AOP Led 15 | Yellow |  |  |  | AOP LED 15 is yellow continuously.
AOP Led 15 | Green + Blink |  |  |  | AOP LED 15 is green and flashes.
AOP Led 15 | Green |  |  |  | AOP LED 15 is green continuously.
AOP Led 16 | Not used |  |  |  | Deactivate AOP LED 16.
AOP Led 16 | Red + Blink |  |  |  | AOP LED 16 is red and flashes.
AOP Led 16 | Red |  |  |  | AOP LED 16 is red continuously.
AOP Led 16 | Yellow + Blink |  |  |  | AOP LED 16 is yellow and flashes.
AOP Led 16 | Yellow |  |  |  | AOP LED 16 is yellow continuously.
AOP Led 16 | Green + Blink |  |  |  | AOP LED 16 is green and flashes.
AOP Led 16 | Green |  |  |  | AOP LED 16 is green continuously.
General Purpose PID commands | PID1 Activate |  |  |  | Activate general purpose PID1.
General Purpose PID commands | PID1 force min. outp. |  |  |  | Force the output of PID1 to the value in PID1 outp. > M-Logic min event setpoint.
General Purpose PID commands | PID1 force max. outp. |  |  |  | Force the output of PID1 to the value in PID1 outp. > M-Logic max event setpoint.
General Purpose PID commands | PID1 reset |  |  |  | Force the output of PID1 to the value in PID1 outp. > Analogue offset.
General Purpose PID commands | PID1 freeze output |  |  |  | Freeze the output of PID1 at its current value.
General Purpose PID commands | PID2 Activate |  |  |  | Activate general purpose PID2.
General Purpose PID commands | PID2 force min. outp. |  |  |  | Force the output of PID2 to the value in PID2 outp. > M-Logic min event setpoint.
General Purpose PID commands | PID2 force max. outp. |  |  |  | Force the output of PID2 to the value in PID2 outp. > M-Logic max event setpoint.
General Purpose PID commands | PID2 reset |  |  |  | Force the output of PID2 to the value in PID2 outp. > Analogue offset.
General Purpose PID commands | PID2 freeze output |  |  |  | Freeze the output of PID2 at its current value.
General Purpose PID commands | PID3 Activate |  |  |  | Activate general purpose PID3.
General Purpose PID commands | PID3 force min. outp. |  |  |  | Force the output of PID3 to the value in PID3 outp. > M-Logic min event setpoint.
General Purpose PID commands | PID3 force max. outp. |  |  |  | Force the output of PID3 to the value in PID3 outp. > M-Logic max event setpoint.
General Purpose PID commands | PID3 reset |  |  |  | Force the output of PID3 to the value in PID3 outp. > Analogue offset.
General Purpose PID commands | PID3 freeze output |  |  |  | Freeze the output of PID3 at its current value.
General Purpose PID commands | PID4 Activate |  |  |  | Activate general purpose PID4.
General Purpose PID commands | PID4 force min. outp. |  |  |  | Force the output of PID4 to the value in PID4 outp. > M-Logic min event setpoint.
General Purpose PID commands | PID4 force max. outp. |  |  |  | Force the output of PID4 to the value in PID4 outp. > M-Logic max event setpoint.
General Purpose PID commands | PID4 reset |  |  |  | Force the output of PID4 to the value in PID4 outp. > Analogue offset.
General Purpose PID commands | PID4 freeze output |  |  |  | Freeze the output of PID4 at its current value.
Virtual event set | Virtual event set 1 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 2 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 3 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 4 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 5 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 6 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 7 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 8 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 9 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 10 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 11 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 12 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 13 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 14 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 15 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 16 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 17 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 18 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 19 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 20 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 21 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 22 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 23 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 24 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 25 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 26 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 27 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 28 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 29 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 30 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 31 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 32 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 33 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 34 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 35 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 36 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 37 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 38 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 39 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 40 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 41 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 42 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 43 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 44 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 45 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 46 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 47 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 48 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 49 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 50 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 51 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 52 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 53 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 54 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 55 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 56 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 57 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 58 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 59 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 60 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 61 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 62 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 63 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 64 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 65 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 66 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 67 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 68 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 69 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 70 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 71 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 72 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 73 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 74 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 75 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 76 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 77 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 78 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 79 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 80 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 81 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 82 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 83 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 84 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 85 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 86 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 87 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 88 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 89 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 90 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 91 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 92 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 93 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 94 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 95 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual event set | Virtual event set 96 |  |  |  | Virtual events 1 to 96 can be activated by M-Logic or Modbus. The output is high as long as the input is high(i.e. is set).
Virtual toggle set | Virtual toggle set 1 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 2 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 3 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 4 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 5 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 6 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 7 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 8 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 9 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 10 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 11 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 12 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 13 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 14 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 15 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 16 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 17 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 18 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 19 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 20 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 21 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 22 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 23 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 24 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 25 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 26 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 27 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 28 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 29 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 30 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 31 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Virtual toggle set | Virtual toggle set 32 |  |  |  | Virtual toggle 1 to 32 can be activated by M-Logic or Modbus. The output changes state once every time the input goes high(i.e. is set).
Flip flops | Flip flop set 1 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 2 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 3 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 4 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 5 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 6 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 7 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 8 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 9 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 10 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 11 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 12 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 13 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 14 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 15 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop set 16 |  |  |  | The output is used to activate the flip flop. Once activated, the flip flop remains activated.
Flip flops | Flip flop reset 1 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 2 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 3 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 4 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 5 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 6 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 7 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 8 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 9 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 10 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 11 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 12 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 13 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 14 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 15 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop reset 16 |  |  |  | The output is used to deactivate the flip flop.
Flip flops | Flip flop toggle 1 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 2 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 3 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 4 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 5 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 6 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 7 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 8 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 9 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 10 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 11 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 12 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 13 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 14 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 15 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Flip flops | Flip flop toggle 16 |  |  |  | The output is used to toggle the state of the flip flop. That is, if the flip flop was deactivated, it is activated. If it was activated, it is deactivated.
Oneshots | Oneshot set 1 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 2 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 3 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 4 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 5 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 6 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 7 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 8 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 9 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 10 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 11 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 12 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 13 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 14 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 15 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Oneshots | Oneshot set 16 |  | 1120 |  | The oneshot is activated for a short time (about 100 ms) when the logic is true. If the logic remains true, the oneshot is not activated again. When the logic is false, the function is reset.
Viewline LED Lamps | LED 1 On |  | 1130 |  | Show LED 1 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 1 Blink |  | 1130 |  | Show LED 1 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 2 On |  | 1130 |  | Show LED 2 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 2 Blink |  | 1130 |  | Show LED 2 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 3 On |  | 1130 |  | Show LED 3 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 3 Blink |  | 1130 |  | Show LED 3 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 4 On |  | 1130 |  | Show LED 4 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 4 Blink |  | 1130 |  | Show LED 4 (a function in display view configuration) as blinking.
Viewline LED Lamps | LED 5 On |  | 1130 |  | Show LED 5 (a function in display view configuration) as ON.
Viewline LED Lamps | LED 5 Blink |  | 1130 |  | Show LED 5 (a function in display view configuration) as blinking.
M-Logic event counters | M-logic event counter 1 |  |  |  | Add 1 to M-Logic event counter 1 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 2 |  |  |  | Add 1 to M-Logic event counter 2 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 3 |  |  |  | Add 1 to M-Logic event counter 3 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 4 |  |  |  | Add 1 to M-Logic event counter 4 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 5 |  |  |  | Add 1 to M-Logic event counter 5 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 6 |  |  |  | Add 1 to M-Logic event counter 6 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 7 |  |  |  | Add 1 to M-Logic event counter 7 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event counter 8 |  |  |  | Add 1 to M-Logic event counter 8 (Counters > M-Logic event counters).
M-Logic event counters | M-logic event reset counter 1 |  |  |  | Reset M-Logic event counter 1.
M-Logic event counters | M-logic event reset counter 2 |  |  |  | Reset M-Logic event counter 2.
M-Logic event counters | M-logic event reset counter 3 |  |  |  | Reset M-Logic event counter 3.
M-Logic event counters | M-logic event reset counter 4 |  |  |  | Reset M-Logic event counter 4.
M-Logic event counters | M-logic event reset counter 5 |  |  |  | Reset M-Logic event counter 5.
M-Logic event counters | M-logic event reset counter 6 |  |  |  | Reset M-Logic event counter 6.
M-Logic event counters | M-logic event reset counter 7 |  |  |  | Reset M-Logic event counter 7.
M-Logic event counters | M-logic event reset counter 8 |  |  |  | Reset M-Logic event counter 8.