## Descriptions
ALC-4 Modbus descriptions
Software version
The information contained in these tables (Revision C) is applicable to software version 4.14.0 of the ALC-4.
Row | Hyperlink index
13 | Modbus function codes
24 | Discrete output coil
32 | Discrete input contact
41 | Output holding register
50 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
| Status flag | Read whether the status flag s activated. The controller returns 0 (false) when the status flag is not activated. The controller returns 1 (true) when the status flag is activated.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DC measurement | Read the operating value of the associated measurement.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus. These addresses are not listed in the Input register (04) worksheet. For more information, see Option H2 and H9, Modbus communication.
| Plant logic state | Read one bit to see whether the state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus. These addresses are not listed in the Input register (04) worksheet. For more information, see Option H2 and H9, Modbus communication.
| Relay state | Read one bit to see whether the relay is activated. The controller returns 0 (false) when the relay is not activated. The controller returns 1 (true) when the relay is activated.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | ALC
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X
Command flag | 10 | 11 | 01; 05; 15 | Nominal setting 1 | X
Command flag | 11 | 12 | 01; 05; 15 | Nominal setting 2 | X
Command flag | 16 | 17 | 01; 05; 15 | Load group 1 ON | X
Command flag | 17 | 18 | 01; 05; 15 | Load group 2 ON | X
Command flag | 18 | 19 | 01; 05; 15 | Load group 3 ON | X
Command flag | 19 | 20 | 01; 05; 15 | Load group 4 ON | X
Command flag | 20 | 21 | 01; 05; 15 | Load group 5 ON | X
Command flag | 21 | 22 | 01; 05; 15 | Load group 6 ON | X
Command flag | 22 | 23 | 01; 05; 15 | Load group 7 ON | X
Command flag | 23 | 24 | 01; 05; 15 | Load group 8 ON | X
Command flag | 24 | 25 | 01; 05; 15 | Load group 1 OFF | X
Command flag | 25 | 26 | 01; 05; 15 | Load group 2 OFF | X
Command flag | 26 | 27 | 01; 05; 15 | Load group 3 OFF | X
Command flag | 27 | 28 | 01; 05; 15 | Load group 4 OFF | X
Command flag | 28 | 29 | 01; 05; 15 | Load group 5 OFF | X
Command flag | 29 | 30 | 01; 05; 15 | Load group 6 OFF | X
Command flag | 30 | 31 | 01; 05; 15 | Load group 7 OFF | X
Command flag | 31 | 32 | 01; 05; 15 | Load group 8 OFF | X
Command flag | 32 | 33 | 01; 05; 15 | Semi-auto mode | X
Command flag | 33 | 34 | 01; 05; 15 | Auto mode | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual event 1 | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual event 2 | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual event 3 | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual event 4 | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual event 5 | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual event 6 | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual event 7 | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual event 8 | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual event 9 | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual event 10 | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual event 11 | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual event 12 | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual event 13 | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual event 14 | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual event 15 | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual event 16 | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual event 17 | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual event 18 | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual event 19 | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual event 20 | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual event 21 | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual event 22 | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual event 23 | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual event 24 | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual event 25 | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual event 26 | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual event 27 | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual event 28 | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual event 29 | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual event 30 | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual event 31 | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual event 32 | X
Command flag | 80 | 81 | 01; 05; 15 | Allow close on dead busbar in AUTO | X
Command flag | 81 | 82 | 01; 05; 15 | Close LG1 on dead busbar in AUTO | X
Command flag | 82 | 83 | 01; 05; 15 | Close LG2 on dead busbar in AUTO | X
Command flag | 83 | 84 | 01; 05; 15 | Close LG3 on dead busbar in AUTO | X
Command flag | 84 | 85 | 01; 05; 15 | Close LG4 on dead busbar in AUTO | X
Command flag | 85 | 86 | 01; 05; 15 | Close LG5 on dead busbar in AUTO | X
Command flag | 86 | 87 | 01; 05; 15 | Close LG6 on dead busbar in AUTO | X
Command flag | 87 | 88 | 01; 05; 15 | Close LG7 on dead busbar in AUTO | X
Command flag | 88 | 89 | 01; 05; 15 | Close LG8 on dead busbar in AUTO | X
Command flag | 89 | 90 | 01; 05; 15 | Allow open on dead busbar in AUTO | X
Command flag | 90 | 91 | 01; 05; 15 | Open LG1 on dead busbar in AUTO | X
Command flag | 91 | 92 | 01; 05; 15 | Open LG2 on dead busbar in AUTO | X
Command flag | 92 | 93 | 01; 05; 15 | Open LG3 on dead busbar in AUTO | X
Command flag | 93 | 94 | 01; 05; 15 | Open LG4 on dead busbar in AUTO | X
Command flag | 94 | 95 | 01; 05; 15 | Open LG5 on dead busbar in AUTO | X
Command flag | 95 | 96 | 01; 05; 15 | Open LG6 on dead busbar in AUTO | X
Command flag | 96 | 97 | 01; 05; 15 | Open LG7 on dead busbar in AUTO | X
Command flag | 97 | 98 | 01; 05; 15 | Open LG8 on dead busbar in AUTO | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X
Command flag | 135 | 136 | 01; 05; 15 | Reset horn | X
Command flag | 136 | 137 | 01; 05; 15 | Activate manual memory backup | X
Command flag | 137 | 138 | 01; 05; 15 | Activate heavy consumer 1 | X
Command flag | 138 | 139 | 01; 05; 15 | Activate heavy consumer 2 | X
Command flag | 139 | 140 | 01; 05; 15 | Activate heavy consumer 3 | X
Command flag | 140 | 141 | 01; 05; 15 | Activate heavy consumer 4 | X
Command flag | 141 | 142 | 01; 05; 15 | Activate heavy consumer 5 | X
Command flag | 142 | 143 | 01; 05; 15 | Activate heavy consumer 6 | X
Command flag | 143 | 144 | 01; 05; 15 | Activate heavy consumer 7 | X
Command flag | 144 | 145 | 01; 05; 15 | Activate heavy consumer 8 | X
Command flag | 145 | 146 | 01; 05; 15 | Disconnect heavy consumer 1 | X
Command flag | 146 | 147 | 01; 05; 15 | Disconnect heavy consumer 2 | X
Command flag | 147 | 148 | 01; 05; 15 | Disconnect heavy consumer 3 | X
Command flag | 148 | 149 | 01; 05; 15 | Disconnect heavy consumer 4 | X
Command flag | 149 | 150 | 01; 05; 15 | Disconnect heavy consumer 5 | X
Command flag | 150 | 151 | 01; 05; 15 | Disconnect heavy consumer 6 | X
Command flag | 151 | 152 | 01; 05; 15 | Disconnect heavy consumer 7 | X
Command flag | 152 | 153 | 01; 05; 15 | Disconnect heavy consumer 8 | X
Command flag | 153 | 154 | 01; 05; 15 | Acknowledge heavy consumer 1 | X
Command flag | 154 | 155 | 01; 05; 15 | Acknowledge heavy consumer 2 | X
Command flag | 155 | 156 | 01; 05; 15 | Acknowledge heavy consumer 3 | X
Command flag | 156 | 157 | 01; 05; 15 | Acknowledge heavy consumer 4 | X
Command flag | 157 | 158 | 01; 05; 15 | Acknowledge heavy consumer 5 | X
Command flag | 158 | 159 | 01; 05; 15 | Acknowledge heavy consumer 6 | X
Command flag | 159 | 160 | 01; 05; 15 | Acknowledge heavy consumer 7 | X
Command flag | 160 | 161 | 01; 05; 15 | Acknowledge heavy consumer 8 | X
Command flag | 161 | 162 | 01; 05; 15 | Set flipflop 01 | X
Command flag | 162 | 163 | 01; 05; 15 | Set flipflop 02 | X
Command flag | 163 | 164 | 01; 05; 15 | Set flipflop 03 | X
Command flag | 164 | 165 | 01; 05; 15 | Set flipflop 04 | X
Command flag | 165 | 166 | 01; 05; 15 | Set flipflop 05 | X
Command flag | 166 | 167 | 01; 05; 15 | Set flipflop 06 | X
Command flag | 167 | 168 | 01; 05; 15 | Set flipflop 07 | X
Command flag | 168 | 169 | 01; 05; 15 | Set flipflop 08 | X
Command flag | 169 | 170 | 01; 05; 15 | Set flipflop 09 | X
Command flag | 170 | 171 | 01; 05; 15 | Set flipflop 10 | X
Command flag | 171 | 172 | 01; 05; 15 | Set flipflop 11 | X
Command flag | 172 | 173 | 01; 05; 15 | Set flipflop 12 | X
Command flag | 173 | 174 | 01; 05; 15 | Set flipflop 13 | X
Command flag | 174 | 175 | 01; 05; 15 | Set flipflop 14 | X
Command flag | 175 | 176 | 01; 05; 15 | Set flipflop 15 | X
Command flag | 176 | 177 | 01; 05; 15 | Set flipflop 16 | X
Command flag | 177 | 178 | 01; 05; 15 | Reset flipflop 01 | X
Command flag | 178 | 179 | 01; 05; 15 | Reset flipflop 02 | X
Command flag | 179 | 180 | 01; 05; 15 | Reset flipflop 03 | X
Command flag | 180 | 181 | 01; 05; 15 | Reset flipflop 04 | X
Command flag | 181 | 182 | 01; 05; 15 | Reset flipflop 05 | X
Command flag | 182 | 183 | 01; 05; 15 | Reset flipflop 06 | X
Command flag | 183 | 184 | 01; 05; 15 | Reset flipflop 07 | X
Command flag | 184 | 185 | 01; 05; 15 | Reset flipflop 08 | X
Command flag | 185 | 186 | 01; 05; 15 | Reset flipflop 09 | X
Command flag | 186 | 187 | 01; 05; 15 | Reset flipflop 10 | X
Command flag | 187 | 188 | 01; 05; 15 | Reset flipflop 11 | X
Command flag | 188 | 189 | 01; 05; 15 | Reset flipflop 12 | X
Command flag | 189 | 190 | 01; 05; 15 | Reset flipflop 13 | X
Command flag | 190 | 191 | 01; 05; 15 | Reset flipflop 14 | X
Command flag | 191 | 192 | 01; 05; 15 | Reset flipflop 15 | X
Command flag | 192 | 193 | 01; 05; 15 | Reset flipflop 16 | X
Command flag | 193 | 194 | 01; 05; 15 | Toggle flipflop 01 | X
Command flag | 194 | 195 | 01; 05; 15 | Toggle flipflop 02 | X
Command flag | 195 | 196 | 01; 05; 15 | Toggle flipflop 03 | X
Command flag | 196 | 197 | 01; 05; 15 | Toggle flipflop 04 | X
Command flag | 197 | 198 | 01; 05; 15 | Toggle flipflop 05 | X
Command flag | 198 | 199 | 01; 05; 15 | Toggle flipflop 06 | X
Command flag | 199 | 200 | 01; 05; 15 | Toggle flipflop 07 | X
Command flag | 200 | 201 | 01; 05; 15 | Toggle flipflop 08 | X
Command flag | 201 | 202 | 01; 05; 15 | Toggle flipflop 09 | X
Command flag | 202 | 203 | 01; 05; 15 | Toggle flipflop 10 | X
Command flag | 203 | 204 | 01; 05; 15 | Toggle flipflop 11 | X
Command flag | 204 | 205 | 01; 05; 15 | Toggle flipflop 12 | X
Command flag | 205 | 206 | 01; 05; 15 | Toggle flipflop 13 | X
Command flag | 206 | 207 | 01; 05; 15 | Toggle flipflop 14 | X
Command flag | 207 | 208 | 01; 05; 15 | Toggle flipflop 15 | X
Command flag | 208 | 209 | 01; 05; 15 | Toggle flipflop 16 | X
Command flag | 209 | 210 | 01; 05; 15 | Virtual event 33 | X
Command flag | 210 | 211 | 01; 05; 15 | Virtual event 34 | X
Command flag | 211 | 212 | 01; 05; 15 | Virtual event 35 | X
Command flag | 212 | 213 | 01; 05; 15 | Virtual event 36 | X
Command flag | 213 | 214 | 01; 05; 15 | Virtual event 37 | X
Command flag | 214 | 215 | 01; 05; 15 | Virtual event 38 | X
Command flag | 215 | 216 | 01; 05; 15 | Virtual event 39 | X
Command flag | 216 | 217 | 01; 05; 15 | Virtual event 40 | X
Command flag | 217 | 218 | 01; 05; 15 | Virtual event 41 | X
Command flag | 218 | 219 | 01; 05; 15 | Virtual event 42 | X
Command flag | 219 | 220 | 01; 05; 15 | Virtual event 43 | X
Command flag | 220 | 221 | 01; 05; 15 | Virtual event 44 | X
Command flag | 221 | 222 | 01; 05; 15 | Virtual event 45 | X
Command flag | 222 | 223 | 01; 05; 15 | Virtual event 46 | X
Command flag | 223 | 224 | 01; 05; 15 | Virtual event 47 | X
Command flag | 224 | 225 | 01; 05; 15 | Virtual event 48 | X
Command flag | 225 | 226 | 01; 05; 15 | Virtual event 49 | X
Command flag | 226 | 227 | 01; 05; 15 | Virtual event 50 | X
Command flag | 227 | 228 | 01; 05; 15 | Virtual event 51 | X
Command flag | 228 | 229 | 01; 05; 15 | Virtual event 52 | X
Command flag | 229 | 230 | 01; 05; 15 | Virtual event 53 | X
Command flag | 230 | 231 | 01; 05; 15 | Virtual event 54 | X
Command flag | 231 | 232 | 01; 05; 15 | Virtual event 55 | X
Command flag | 232 | 233 | 01; 05; 15 | Virtual event 56 | X
Command flag | 233 | 234 | 01; 05; 15 | Virtual event 57 | X
Command flag | 234 | 235 | 01; 05; 15 | Virtual event 58 | X
Command flag | 235 | 236 | 01; 05; 15 | Virtual event 59 | X
Command flag | 236 | 237 | 01; 05; 15 | Virtual event 60 | X
Command flag | 237 | 238 | 01; 05; 15 | Virtual event 61 | X
Command flag | 238 | 239 | 01; 05; 15 | Virtual event 62 | X
Command flag | 239 | 240 | 01; 05; 15 | Virtual event 63 | X
Command flag | 240 | 241 | 01; 05; 15 | Virtual event 64 | X
Command flag | 241 | 242 | 01; 05; 15 | Virtual event 65 | X
Command flag | 242 | 243 | 01; 05; 15 | Virtual event 66 | X
Command flag | 243 | 244 | 01; 05; 15 | Virtual event 67 | X
Command flag | 244 | 245 | 01; 05; 15 | Virtual event 68 | X
Command flag | 245 | 246 | 01; 05; 15 | Virtual event 69 | X
Command flag | 246 | 247 | 01; 05; 15 | Virtual event 70 | X
Command flag | 247 | 248 | 01; 05; 15 | Virtual event 71 | X
Command flag | 248 | 249 | 01; 05; 15 | Virtual event 72 | X
Command flag | 249 | 250 | 01; 05; 15 | Virtual event 73 | X
Command flag | 250 | 251 | 01; 05; 15 | Virtual event 74 | X
Command flag | 251 | 252 | 01; 05; 15 | Virtual event 75 | X
Command flag | 252 | 253 | 01; 05; 15 | Virtual event 76 | X
Command flag | 253 | 254 | 01; 05; 15 | Virtual event 77 | X
Command flag | 254 | 255 | 01; 05; 15 | Virtual event 78 | X
Command flag | 255 | 256 | 01; 05; 15 | Virtual event 79 | X
Command flag | 256 | 257 | 01; 05; 15 | Virtual event 80 | X
Command flag | 257 | 258 | 01; 05; 15 | Virtual event 81 | X
Command flag | 258 | 259 | 01; 05; 15 | Virtual event 82 | X
Command flag | 259 | 260 | 01; 05; 15 | Virtual event 83 | X
Command flag | 260 | 261 | 01; 05; 15 | Virtual event 84 | X
Command flag | 261 | 262 | 01; 05; 15 | Virtual event 85 | X
Command flag | 262 | 263 | 01; 05; 15 | Virtual event 86 | X
Command flag | 263 | 264 | 01; 05; 15 | Virtual event 87 | X
Command flag | 264 | 265 | 01; 05; 15 | Virtual event 88 | X
Command flag | 265 | 266 | 01; 05; 15 | Virtual event 89 | X
Command flag | 266 | 267 | 01; 05; 15 | Virtual event 90 | X
Command flag | 267 | 268 | 01; 05; 15 | Virtual event 91 | X
Command flag | 268 | 269 | 01; 05; 15 | Virtual event 92 | X
Command flag | 269 | 270 | 01; 05; 15 | Virtual event 93 | X
Command flag | 270 | 271 | 01; 05; 15 | Virtual event 94 | X
Command flag | 271 | 272 | 01; 05; 15 | Virtual event 95 | X
Command flag | 272 | 273 | 01; 05; 15 | Virtual event 96 | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | ALC
Status flag | 8 | 100009 | 02 | Semi-auto mode | X
Status flag | 9 | 100010 | 02 | Auto mode | X
Status flag | 19 | 100020 | 02 | Power management | X
Status flag | 31 | 100032 | 02 | Ready auto-start Gen1 | X
Status flag | 32 | 100033 | 02 | Ready auto-start Gen2 | X
Status flag | 33 | 100034 | 02 | Ready auto-start Gen3 | X
Status flag | 34 | 100035 | 02 | Ready auto-start Gen4 | X
Status flag | 35 | 100036 | 02 | Ready auto-start Gen5 | X
Status flag | 36 | 100037 | 02 | Ready auto-start Gen6 | X
Status flag | 37 | 100038 | 02 | Ready auto-start Gen7 | X
Status flag | 38 | 100039 | 02 | Ready auto-start Gen8 | X
Digital input | 22500 | 122501 | 02 | Digital input 97 | X
Digital input | 22501 | 122502 | 02 | Digital input 96 | X
Digital input | 22502 | 122503 | 02 | Digital input 95 | X
Digital input | 22503 | 122504 | 02 | Digital input 94 | X
Digital input | 22504 | 122505 | 02 | Digital input 93 | X
Digital input | 22505 | 122506 | 02 | Digital input 92 | X
Digital input | 22506 | 122507 | 02 | Digital input 91 | X
Digital input | 22507 | 122508 | 02 | Digital input 133 | X
Digital input | 22508 | 122509 | 02 | Digital input 132 | X
Digital input | 22509 | 122510 | 02 | Digital input 131 | X
Digital input | 22510 | 122511 | 02 | Digital input 130 | X
Digital input | 22511 | 122512 | 02 | Digital input 129 | X
Digital input | 22512 | 122513 | 02 | Digital input 128 | X
Digital input | 22513 | 122514 | 02 | Digital input 127 | X
Digital input | 22514 | 122515 | 02 | Digital input 29 | X
Digital input | 22515 | 122516 | 02 | Digital input 30 | X
Digital input | 22516 | 122517 | 02 | Digital input 31 | X
Digital input | 22517 | 122518 | 02 | Digital input 32 | X
Digital input | 22518 | 122519 | 02 | Digital input 33 | X
Digital input | 22519 | 122520 | 02 | Digital input 34 | X
Digital input | 22520 | 122521 | 02 | Digital input 35 | X
Digital input | 22521 | 122522 | 02 | Digital input 65 | X
Digital input | 22522 | 122523 | 02 | Digital input 66 | X
Digital input | 22523 | 122524 | 02 | Digital input 67 | X
Digital input | 22524 | 122525 | 02 | Digital input 68 | X
Digital input | 22525 | 122526 | 02 | Digital input 69 | X
Digital input | 22526 | 122527 | 02 | Digital input 70 | X
Digital input | 22527 | 122528 | 02 | Digital input 71 | X
Digital input | 22528 | 122529 | 02 | Digital input 43 | X
Digital input | 22529 | 122530 | 02 | Digital input 44 | X
Digital input | 22530 | 122531 | 02 | Digital input 45 | X
Digital input | 22531 | 122532 | 02 | Digital input 46 | X
Digital input | 22532 | 122533 | 02 | Digital input 47 | X
Digital input | 22533 | 122534 | 02 | Digital input 48 | X
Digital input | 22534 | 122535 | 02 | Digital input 49 | X
Digital input | 22535 | 122536 | 02 | Digital input 50 | X
Digital input | 22536 | 122537 | 02 | Digital input 51 | X
Digital input | 22537 | 122538 | 02 | Digital input 52 | X
Digital input | 22538 | 122539 | 02 | Digital input 53 | X
Digital input | 22539 | 122540 | 02 | Digital input 54 | X
Digital input | 22540 | 122541 | 02 | Digital input 55 | X
Digital input | 22541 | 122542 | 02 | Digital input 23 | X
Digital input | 22542 | 122543 | 02 | Digital input 24 | X
Digital input | 22543 | 122544 | 02 | Digital input 25 | X
Digital input | 22544 | 122545 | 02 | Digital input 26 | X
Digital input | 22545 | 122546 | 02 | Digital input 27 | X
Digital input | 22583 | 122584 | 02 | Digital input 118 - Emergency stop | X
Digital input | 22584 | 122585 | 02 | Digital input 117 | X
Digital input | 22585 | 122586 | 02 | Digital input 116 | X
Digital input | 22586 | 122587 | 02 | Digital input 115 | X
Digital input | 22587 | 122588 | 02 | Digital input 114 | X
Digital input | 22588 | 122589 | 02 | Digital input 113 | X
Digital input | 22589 | 122590 | 02 | Digital input 112 | X
Digital input | 22591 | 122592 | 02 | Digital input 108 | X
Digital input | 22592 | 122593 | 02 | Digital input 105 | X
Digital input | 22593 | 122594 | 02 | Digital input 102 | X
Digital output | 23000 | 123001 | 02 | Relay 65 (M14.4) | X
Digital output | 23001 | 123002 | 02 | Relay 67 (M14.4) | X
Digital output | 23001 | 123002 | 02 | Relay 20 | X
Digital output | 23002 | 123003 | 02 | Relay 69 (M14.4) | X
Digital output | 23002 | 123003 | 02 | Relay 21 | X
Digital output | 23003 | 123004 | 02 | Relay 71 (M14.4) | X
Digital output | 23004 | 123005 | 02 | Relay 132 (M14.8) | X
Digital output | 23005 | 123006 | 02 | Relay 130 (M14.8) | X
Digital output | 23006 | 123007 | 02 | Relay 128 (M14.8) | X
Digital output | 23007 | 123008 | 02 | Relay 126 (M14.8) | X
Digital output | 23008 | 123009 | 02 | Relay 96 (M14.6) | X
Digital output | 23009 | 123010 | 02 | Relay 94 (M14.6) | X
Digital output | 23009 | 123010 | 02 | Relay 11 | X
Digital output | 23010 | 123011 | 02 | Relay 92 (M14.6) | X
Digital output | 23010 | 123011 | 02 | Relay 8 | X
Digital output | 23011 | 123012 | 02 | Relay 90 (M14.6) | X
Digital output | 23011 | 123012 | 02 | Relay 17 | X
Digital output | 23012 | 123013 | 02 | Relay 29 (M14.2) | X
Digital output | 23012 | 123013 | 02 | Relay 14 | X
Digital output | 23013 | 123014 | 02 | Relay 31 (M14.2) | X
Digital output | 23014 | 123015 | 02 | Relay 33 (M14.2) | X
Digital output | 23015 | 123016 | 02 | Relay 35 (M14.2) | X
Digital output | 23016 | 123017 | 02 | Relay 57 (M12) | X
Digital output | 23017 | 123018 | 02 | Relay 59 (M12) | X
Digital output | 23018 | 123019 | 02 | Relay 61 (M12) | X
Digital output | 23019 | 123020 | 02 | Relay 63 (M12) | X
Digital output | 23022 | 123023 | 02 | Any inhibit active (LED, DU2) | X
Digital output | 23025 | 123026 | 02 | Relay 5 | X
Digital output | 23053 | 123054 | 02 | LED CAN B | X
Digital output | 23054 | 123055 | 02 | LED CAN A | X
Digital output | 23055 | 123056 | 02 | LED USB | X
Digital output | 23072 | 123073 | 02 | Relay 118-119 (M4) | X
Digital output | 23073 | 123074 | 02 | Relay 118-120 (M4) | X
Digital output | 23074 | 123075 | 02 | Relay 121-122 (M4) | X
Digital output | 23075 | 123076 | 02 | Relay 123-124 (M4) | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | ALC
Control command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL |  |  |  | X
Control command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL |  |  |  | X
Control command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X
Control command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X
Control command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X
Control command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 6 | 1 | 400007 | 03; 06; 16 | Load group 1 ON | BOOL |  |  |  | X
Control command | 6 | 2 | 400007 | 03; 06; 16 | Load group 1 OFF | BOOL |  |  |  | X
Control command | 6 | 3 | 400007 | 03; 06; 16 | Load group 2 ON | BOOL |  |  |  | X
Control command | 6 | 4 | 400007 | 03; 06; 16 | Load group 2 OFF | BOOL |  |  |  | X
Control command | 6 | 5 | 400007 | 03; 06; 16 | Load group 3 ON | BOOL |  |  |  | X
Control command | 6 | 6 | 400007 | 03; 06; 16 | Load group 3 OFF | BOOL |  |  |  | X
Control command | 6 | 7 | 400007 | 03; 06; 16 | Load group 4 ON | BOOL |  |  |  | X
Control command | 6 | 8 | 400007 | 03; 06; 16 | Load group 4 OFF | BOOL |  |  |  | X
Control command | 6 | 9 | 400007 | 03; 06; 16 | Load group 5 ON | BOOL |  |  |  | X
Control command | 6 | 10 | 400007 | 03; 06; 16 | Load group 5 OFF | BOOL |  |  |  | X
Control command | 6 | 11 | 400007 | 03; 06; 16 | Load group 6 ON | BOOL |  |  |  | X
Control command | 6 | 12 | 400007 | 03; 06; 16 | Load group 6 OFF | BOOL |  |  |  | X
Control command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 7 | 1 | 400008 | 03; 06; 16 | Load group 7 ON | BOOL |  |  |  | X
Control command | 7 | 2 | 400008 | 03; 06; 16 | Load group 7 OFF | BOOL |  |  |  | X
Control command | 7 | 3 | 400008 | 03; 06; 16 | Load group 8 ON | BOOL |  |  |  | X
Control command | 7 | 4 | 400008 | 03; 06; 16 | Load group 8 OFF | BOOL |  |  |  | X
Control command | 7 | 5 | 400008 | 03; 06; 16 | Semi-Auto mode | BOOL |  |  |  | X
Control command | 7 | 6 | 400008 | 03; 06; 16 | Auto mode | BOOL |  |  |  | X
Control command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X
Control command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X
Control command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X
Control command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X
Control command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X
Control command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 8 | 1 | 400009 | 03; 06; 16 | Virtual event 1 | BOOL |  |  |  | X
Control command | 8 | 2 | 400009 | 03; 06; 16 | Virtual event 2 | BOOL |  |  |  | X
Control command | 8 | 3 | 400009 | 03; 06; 16 | Virtual event 3 | BOOL |  |  |  | X
Control command | 8 | 4 | 400009 | 03; 06; 16 | Virtual event 4 | BOOL |  |  |  | X
Control command | 8 | 5 | 400009 | 03; 06; 16 | Virtual event 5 | BOOL |  |  |  | X
Control command | 8 | 6 | 400009 | 03; 06; 16 | Virtual event 6 | BOOL |  |  |  | X
Control command | 8 | 7 | 400009 | 03; 06; 16 | Virtual event 7 | BOOL |  |  |  | X
Control command | 8 | 8 | 400009 | 03; 06; 16 | Virtual event 8 | BOOL |  |  |  | X
Control command | 8 | 9 | 400009 | 03; 06; 16 | Virtual event 9 | BOOL |  |  |  | X
Control command | 8 | 10 | 400009 | 03; 06; 16 | Virtual event 10 | BOOL |  |  |  | X
Control command | 8 | 11 | 400009 | 03; 06; 16 | Virtual event 11 | BOOL |  |  |  | X
Control command | 8 | 12 | 400009 | 03; 06; 16 | Virtual event 12 | BOOL |  |  |  | X
Control command | 8 | 13 | 400009 | 03; 06; 16 | Virtual event 13 | BOOL |  |  |  | X
Control command | 8 | 14 | 400009 | 03; 06; 16 | Virtual event 14 | BOOL |  |  |  | X
Control command | 8 | 15 | 400009 | 03; 06; 16 | Virtual event 15 | BOOL |  |  |  | X
Control command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 9 | 1 | 400010 | 03; 06; 16 | Virtual event 16 | BOOL |  |  |  | X
Control command | 9 | 2 | 400010 | 03; 06; 16 | Virtual event 17 | BOOL |  |  |  | X
Control command | 9 | 3 | 400010 | 03; 06; 16 | Virtual event 18 | BOOL |  |  |  | X
Control command | 9 | 4 | 400010 | 03; 06; 16 | Virtual event 19 | BOOL |  |  |  | X
Control command | 9 | 5 | 400010 | 03; 06; 16 | Virtual event 20 | BOOL |  |  |  | X
Control command | 9 | 6 | 400010 | 03; 06; 16 | Virtual event 21 | BOOL |  |  |  | X
Control command | 9 | 7 | 400010 | 03; 06; 16 | Virtual event 22 | BOOL |  |  |  | X
Control command | 9 | 8 | 400010 | 03; 06; 16 | Virtual event 23 | BOOL |  |  |  | X
Control command | 9 | 9 | 400010 | 03; 06; 16 | Virtual event 24 | BOOL |  |  |  | X
Control command | 9 | 10 | 400010 | 03; 06; 16 | Virtual event 25 | BOOL |  |  |  | X
Control command | 9 | 11 | 400010 | 03; 06; 16 | Virtual event 26 | BOOL |  |  |  | X
Control command | 9 | 12 | 400010 | 03; 06; 16 | Virtual event 27 | BOOL |  |  |  | X
Control command | 9 | 13 | 400010 | 03; 06; 16 | Virtual event 28 | BOOL |  |  |  | X
Control command | 9 | 14 | 400010 | 03; 06; 16 | Virtual event 29 | BOOL |  |  |  | X
Control command | 9 | 15 | 400010 | 03; 06; 16 | Virtual event 30 | BOOL |  |  |  | X
Control command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X
Control command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X
Control command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X
Control command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X
Control command | 11 | 0 | 400012 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 11 | 1 | 400012 | 03; 06; 16 | Allow close on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 2 | 400012 | 03; 06; 16 | Close LG1 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 3 | 400012 | 03; 06; 16 | Close LG2 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 4 | 400012 | 03; 06; 16 | Close LG3 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 5 | 400012 | 03; 06; 16 | Close LG4 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 6 | 400012 | 03; 06; 16 | Close LG5 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 7 | 400012 | 03; 06; 16 | Close LG6 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 8 | 400012 | 03; 06; 16 | Close LG7 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 11 | 9 | 400012 | 03; 06; 16 | Close LG8 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 0 | 400013 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 12 | 1 | 400013 | 03; 06; 16 | Allow open on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 2 | 400013 | 03; 06; 16 | Open LG1 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 3 | 400013 | 03; 06; 16 | Open LG2 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 4 | 400013 | 03; 06; 16 | Open LG3 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 5 | 400013 | 03; 06; 16 | Open LG4 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 6 | 400013 | 03; 06; 16 | Open LG5 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 7 | 400013 | 03; 06; 16 | Open LG6 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 8 | 400013 | 03; 06; 16 | Open LG7 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 12 | 9 | 400013 | 03; 06; 16 | Open LG8 on dead busbar in AUTO | BOOL |  |  |  | X
Control command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X
Control command | 14 | 0 | 400015 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 14 | 1 | 400015 | 03; 06; 16 | Activate heavy consumer 1 | BOOL |  |  |  | X
Control command | 14 | 2 | 400015 | 03; 06; 16 | Activate heavy consumer 2 | BOOL |  |  |  | X
Control command | 14 | 3 | 400015 | 03; 06; 16 | Activate heavy consumer 3 | BOOL |  |  |  | X
Control command | 14 | 4 | 400015 | 03; 06; 16 | Activate heavy consumer 4 | BOOL |  |  |  | X
Control command | 14 | 5 | 400015 | 03; 06; 16 | Activate heavy consumer 5 | BOOL |  |  |  | X
Control command | 14 | 6 | 400015 | 03; 06; 16 | Activate heavy consumer 6 | BOOL |  |  |  | X
Control command | 14 | 7 | 400015 | 03; 06; 16 | Activate heavy consumer 7 | BOOL |  |  |  | X
Control command | 14 | 8 | 400015 | 03; 06; 16 | Activate heavy consumer 8 | BOOL |  |  |  | X
Control command | 15 | 0 | 400016 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 15 | 1 | 400016 | 03; 06; 16 | Disconnect heavy consumer 1 | BOOL |  |  |  | X
Control command | 15 | 2 | 400016 | 03; 06; 16 | Disconnect heavy consumer 2 | BOOL |  |  |  | X
Control command | 15 | 3 | 400016 | 03; 06; 16 | Disconnect heavy consumer 3 | BOOL |  |  |  | X
Control command | 15 | 4 | 400016 | 03; 06; 16 | Disconnect heavy consumer 4 | BOOL |  |  |  | X
Control command | 15 | 5 | 400016 | 03; 06; 16 | Disconnect heavy consumer 5 | BOOL |  |  |  | X
Control command | 15 | 6 | 400016 | 03; 06; 16 | Disconnect heavy consumer 6 | BOOL |  |  |  | X
Control command | 15 | 7 | 400016 | 03; 06; 16 | Disconnect heavy consumer 7 | BOOL |  |  |  | X
Control command | 15 | 8 | 400016 | 03; 06; 16 | Disconnect heavy consumer 8 | BOOL |  |  |  | X
Control command | 16 | 0 | 400017 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X
Control command | 16 | 1 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 1 | BOOL |  |  |  | X
Control command | 16 | 2 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 2 | BOOL |  |  |  | X
Control command | 16 | 3 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 3 | BOOL |  |  |  | X
Control command | 16 | 4 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 4 | BOOL |  |  |  | X
Control command | 16 | 5 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 5 | BOOL |  |  |  | X
Control command | 16 | 6 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 6 | BOOL |  |  |  | X
Control command | 16 | 7 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 7 | BOOL |  |  |  | X
Control command | 16 | 8 | 400017 | 03; 06; 16 | Acknowledge heavy consumer 8 | BOOL |  |  |  | X
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | ALC
APPL version | 500 |  | 300501 | 04 |  | Application version | INT16s | AB | 0 |  | X
AC measurement | 539 |  | 300540 | 04 |  | Busbar voltage L1-L2 | INT16s | AB | 0 | V | X
AC measurement | 540 |  | 300541 | 04 |  | Busbar voltage L2-L3 | INT16s | AB | 0 | V | X
AC measurement | 541 |  | 300542 | 04 |  | Busbar voltage L3-L1 | INT16s | AB | 0 | V | X
AC measurement | 542 |  | 300543 | 04 |  | Busbar voltage L1-N | INT16s | AB | 0 | V | X
AC measurement | 543 |  | 300544 | 04 |  | Busbar voltage L2-N | INT16s | AB | 0 | V | X
AC measurement | 544 |  | 300545 | 04 |  | Busbar voltage L3-N | INT16s | AB | 0 | V | X
AC measurement | 545 |  | 300546 | 04 |  | Busbar frequency L1 | INT16s | AB | 2 | Hz | X
AC measurement | 546 |  | 300547 | 04 |  | Busbar frequency L2 | INT16s | AB | 2 | Hz | X
AC measurement | 547 |  | 300548 | 04 |  | Busbar frequency L3 | INT16s | AB | 2 | Hz | X
AC measurement | 548 |  | 300549 | 04 |  | Busbar voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X
AC measurement | 549 |  | 300550 | 04 |  | Busbar voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X
AC measurement | 550 |  | 300551 | 04 |  | Busbar voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X
Counter | 558 |  | 300559 | 04 |  | No. of alarms | INT16s | AB | 0 |  | X
Counter | 559 |  | 300560 | 04 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X
Counter | 560 |  | 300561 | 04 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X
DC measurement | 567 |  | 300568 | 04 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X
DC measurement | 568 |  | 300569 | 04 |  | DC supply term. 98-99 | INT16s | AB | 1 | V | X
DC measurement | 580 |  | 300581 | 04 |  | Multi-input 102 unscaled | INT16s | AB | 0 |  | X
DC measurement | 581 |  | 300582 | 04 |  | Multi-input 105 unscaled | INT16s | AB | 0 |  | X
DC measurement | 582 |  | 300583 | 04 |  | Multi-input 108 unscaled | INT16s | AB | 0 |  | X
DC measurement | 583 |  | 300584 | 04 |  | Multi-input 102 scaled | INT16s | AB | 0 |  | X
DC measurement | 584 |  | 300585 | 04 |  | Multi-input 105 scaled | INT16s | AB | 0 |  | X
DC measurement | 585 |  | 300586 | 04 |  | Multi-input 108 scaled | INT16s | AB | 0 |  | X
DC measurement | 586 |  | 300587 | 04 |  | Analogue input 91 scaled | INT16s | AB | 0 |  | X
DC measurement | 587 |  | 300588 | 04 |  | Analogue input 93 scaled | INT16s | AB | 0 |  | X
DC measurement | 588 |  | 300589 | 04 |  | Analogue input 95 scaled | INT16s | AB | 0 |  | X
DC measurement | 589 |  | 300590 | 04 |  | Analogue input 97 scaled | INT16s | AB | 0 |  | X
DC measurement | 590 |  | 300591 | 04 |  | Internal Temperature | INT16s | AB | 1 | Deg C | X
Plant logic state | 593 |  | 300594 | 04 |  | Load group 1 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 594 |  | 300595 | 04 |  | Load group 2 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 595 |  | 300596 | 04 |  | Load group 3 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 596 |  | 300597 | 04 |  | Load group 4 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 597 |  | 300598 | 04 |  | Load group 5 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 598 |  | 300599 | 04 |  | Load group 6 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 599 |  | 300600 | 04 |  | Load group 7 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 600 |  | 300601 | 04 |  | Load group 8 closed feedback | INT16s | AB | 0 |  | X
Plant logic state | 601 |  | 300602 | 04 |  | Heavy customer 1 state: 0 = No request. 10 = Waiting for turn. 20 = Waiting for power. 30 = Keep requesting start power until acknowledge. 40 = Requesting nominal power (variable HC only) | INT16s | AB | 0 |  | X
Plant logic state | 602 |  | 300603 | 04 |  | Heavy customer 2 state | INT16s | AB | 0 |  | X
Plant logic state | 603 |  | 300604 | 04 |  | Heavy customer 3 state | INT16s | AB | 0 |  | X
Plant logic state | 604 |  | 300605 | 04 |  | Heavy customer 4 state | INT16s | AB | 0 |  | X
Plant logic state | 605 |  | 300606 | 04 |  | Heavy customer 5 state | INT16s | AB | 0 |  | X
Plant logic state | 606 |  | 300607 | 04 |  | Heavy customer 6 state | INT16s | AB | 0 |  | X
Plant logic state | 607 |  | 300608 | 04 |  | Heavy customer 7 state | INT16s | AB | 0 |  | X
Plant logic state | 608 |  | 300609 | 04 |  | Heavy customer 8 state | INT16s | AB | 0 |  | X
M-Logic state | 609 |  | 300610 | 04 |  | Flip flop output 1-16 in bits | INT16s | AB | 0 |  | X
AC measurement | 610 |  | 300611 | 04 |  | Power requested by this ALC-4. | INT16s | AB | 0 |  | X
AC measurement | 611 |  | 300612 | 04 |  | Power requested by dynamic section ALC's on busbar. | INT16s | AB | 0 |  | X
AC measurement | 612 |  | 300613 | 04 |  | HC power requested by this ALC-4. | INT16s | AB | 0 |  | X
AC measurement | 613 |  | 300614 | 04 |  | HC power requested by dynamic section ALC's on busbar. | INT16s | AB | 0 |  | X
Control command state | 642 |  | 300643 | 04 |  | Control command address 0 | INT16s | AB | 0 |  | X
Control command state | 643 |  | 300644 | 04 |  | Control command address 1 | INT16s | AB | 0 |  | X
Control command state | 644 |  | 300645 | 04 |  | Control command address 2 | INT16s | AB | 0 |  | X
Control command state | 645 |  | 300646 | 04 |  | Control command address 3 | INT16s | AB | 0 |  | X
Control command state | 646 |  | 300647 | 04 |  | Control command address 4 | INT16s | AB | 0 |  | X
Control command state | 647 |  | 300648 | 04 |  | Control command address 5 | INT16s | AB | 0 |  | X
Control command state | 648 |  | 300649 | 04 |  | Control command address 6 | INT16s | AB | 0 |  | X
Control command state | 649 |  | 300650 | 04 |  | Control command address 7 | INT16s | AB | 0 |  | X
Control command state | 650 |  | 300651 | 04 |  | Control command address 8 | INT16s | AB | 0 |  | X
Control command state | 651 |  | 300652 | 04 |  | Control command address 9 | INT16s | AB | 0 |  | X
Control command state | 652 |  | 300653 | 04 |  | Control command address 10 | INT16s | AB | 0 |  | X
Control command state | 653 |  | 300654 | 04 |  | Control command address 11 | INT16s | AB | 0 |  | X
Control command state | 654 |  | 300655 | 04 |  | Control command address 12 | INT16s | AB | 0 |  | X
Control command state | 655 |  | 300656 | 04 |  | Control command address 13 | INT16s | AB | 0 |  | X
DC measurement | 656 |  | 300657 | 04 |  | Analogue input 127 | INT16s | AB | 0 |  | X
DC measurement | 657 |  | 300658 | 04 |  | Analogue input 129 | INT16s | AB | 0 |  | X
DC measurement | 658 |  | 300659 | 04 |  | Analogue input 131 | INT16s | AB | 0 |  | X
DC measurement | 659 |  | 300660 | 04 |  | Analogue input 133 | INT16s | AB | 0 |  | X
AC alarm | 1002 | 0 | 301003 | 04 | 1000 | BB f< 1 | BOOL |  |  |  | X
AC alarm | 1002 | 1 | 301003 | 04 | 1010 | BB f< 2 | BOOL |  |  |  | X
AC alarm | 1002 | 2 | 301003 | 04 | 1020 | BB f< 3 | BOOL |  |  |  | X
AC alarm | 1002 | 3 | 301003 | 04 | 1030 | BB f< 4 | BOOL |  |  |  | X
AC alarm | 1002 | 4 | 301003 | 04 | 1040 | BB f< 5 | BOOL |  |  |  | X
AC alarm | 1002 | 5 | 301003 | 04 | 1050 | BB f< 6 | BOOL |  |  |  | X
AC alarm | 1002 | 6 | 301003 | 04 | 1060 | BB f< 7 | BOOL |  |  |  | X
AC alarm | 1002 | 7 | 301003 | 04 | 1070 | BB f< 8 | BOOL |  |  |  | X
AC alarm | 1003 | 0 | 301004 | 04 | 1971 | Load group 1 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 1 | 301004 | 04 | 1973 | Load group 2 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 2 | 301004 | 04 | 1975 | Load group 3 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 3 | 301004 | 04 | 1981 | Load group 4 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 4 | 301004 | 04 | 1983 | Load group 5 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 5 | 301004 | 04 | 1985 | Load group 6 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 6 | 301004 | 04 | 1991 | Load group 7 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 7 | 301004 | 04 | 1993 | Load group 8 externally tripped | BOOL |  |  |  | X
AC alarm | 1003 | 8 | 301004 | 04 | 8250 | DG Overload alarm 1 | BOOL |  |  |  | X
AC alarm | 1003 | 9 | 301004 | 04 | 8260 | DG Overload alarm 2 | BOOL |  |  |  | X
AC alarm | 1003 | 10 | 301004 | 04 | 8270 | DG Overload alarm 3 | BOOL |  |  |  | X
AC alarm | 1003 | 11 | 301004 | 04 | 8280 | DG Overload alarm 4 | BOOL |  |  |  | X
AC alarm | 1003 | 12 | 301004 | 04 | 82990 | DG Overload alarm 5 | BOOL |  |  |  | X
AC alarm | 1004 | 0 | 301005 | 04 | 2110 | Load group 1 open failure | BOOL |  |  |  | X
AC alarm | 1004 | 1 | 301005 | 04 | 2120 | Load group 1 close failure | BOOL |  |  |  | X
AC alarm | 1004 | 2 | 301005 | 04 | 2130 | Load group 1 position failure | BOOL |  |  |  | X
AC alarm | 1004 | 3 | 301005 | 04 | 2140 | Load group 2 open failure | BOOL |  |  |  | X
AC alarm | 1004 | 4 | 301005 | 04 | 2150 | Load group 2 close failure | BOOL |  |  |  | X
AC alarm | 1004 | 5 | 301005 | 04 | 2160 | Load group 2 position failure | BOOL |  |  |  | X
AC alarm | 1004 | 6 | 301005 | 04 | 2170 | Load group 3 open failure | BOOL |  |  |  | X
AC alarm | 1004 | 7 | 301005 | 04 | 2180 | Load group 3 close failure | BOOL |  |  |  | X
AC alarm | 1004 | 8 | 301005 | 04 | 2190 | Load group 3 position failure | BOOL |  |  |  | X
AC alarm | 1004 | 9 | 301005 | 04 | 2200 | Load group 4 open failure | BOOL |  |  |  | X
AC alarm | 1004 | 10 | 301005 | 04 | 2210 | Load group 4 close failure | BOOL |  |  |  | X
AC alarm | 1004 | 11 | 301005 | 04 | 2220 | Load group 4 position failure | BOOL |  |  |  | X
AC alarm | 1004 | 12 | 301005 | 04 | 2230 | Load group 5 open failure | BOOL |  |  |  | X
AC alarm | 1004 | 13 | 301005 | 04 | 2240 | Load group 5 close failure | BOOL |  |  |  | X
AC alarm | 1004 | 14 | 301005 | 04 | 2250 | Load group 5 position failure | BOOL |  |  |  | X
AC alarm | 1005 | 0 | 301006 | 04 | 2260 | Load group 6 open failure | BOOL |  |  |  | X
AC alarm | 1005 | 1 | 301006 | 04 | 2270 | Load group 6 close failure | BOOL |  |  |  | X
AC alarm | 1005 | 2 | 301006 | 04 | 2280 | Load group 6 position failure | BOOL |  |  |  | X
AC alarm | 1005 | 3 | 301006 | 04 | 2290 | Load group 7 open failure | BOOL |  |  |  | X
AC alarm | 1005 | 4 | 301006 | 04 | 2300 | Load group 7 close failure | BOOL |  |  |  | X
AC alarm | 1005 | 5 | 301006 | 04 | 2310 | Load group 7 position failure | BOOL |  |  |  | X
AC alarm | 1005 | 6 | 301006 | 04 | 2320 | Load group 8 open failure | BOOL |  |  |  | X
AC alarm | 1005 | 7 | 301006 | 04 | 2330 | Load group 8 close failure | BOOL |  |  |  | X
AC alarm | 1005 | 8 | 301006 | 04 | 2340 | Load group 8 position failure | BOOL |  |  |  | X
Alarm | 1007 | 0 | 301008 | 04 | 3000 | Digital alarm input 23 | BOOL |  |  |  | X
Alarm | 1007 | 1 | 301008 | 04 | 3010 | Digital alarm input 24 | BOOL |  |  |  | X
Alarm | 1007 | 2 | 301008 | 04 | 3020 | Digital alarm input 25 | BOOL |  |  |  | X
Alarm | 1007 | 3 | 301008 | 04 | 3030 | Digital alarm input 26 | BOOL |  |  |  | X
Alarm | 1007 | 4 | 301008 | 04 | 3040 | Digital alarm input 27 | BOOL |  |  |  | X
Alarm | 1007 | 6 | 301008 | 04 | 3060 | Digital alarm input 29 | BOOL |  |  |  | X
Alarm | 1007 | 7 | 301008 | 04 | 3070 | Digital alarm input 30 | BOOL |  |  |  | X
Alarm | 1007 | 8 | 301008 | 04 | 3080 | Digital alarm input 31 | BOOL |  |  |  | X
Alarm | 1007 | 9 | 301008 | 04 | 3090 | Digital alarm input 32 | BOOL |  |  |  | X
Alarm | 1007 | 10 | 301008 | 04 | 3100 | Digital alarm input 33 | BOOL |  |  |  | X
Alarm | 1007 | 11 | 301008 | 04 | 3110 | Digital alarm input 34 | BOOL |  |  |  | X
Alarm | 1007 | 12 | 301008 | 04 | 3120 | Digital alarm input 35 | BOOL |  |  |  | X
Alarm | 1008 | 0 | 301009 | 04 | 3130 | Digital alarm input 43 | BOOL |  |  |  | X
Alarm | 1008 | 1 | 301009 | 04 | 3140 | Digital alarm input 44 | BOOL |  |  |  | X
Alarm | 1008 | 2 | 301009 | 04 | 3150 | Digital alarm input 45 | BOOL |  |  |  | X
Alarm | 1008 | 3 | 301009 | 04 | 3160 | Digital alarm input 46 | BOOL |  |  |  | X
Alarm | 1008 | 4 | 301009 | 04 | 3170 | Digital alarm input 47 | BOOL |  |  |  | X
Alarm | 1008 | 5 | 301009 | 04 | 3180 | Digital alarm input 48 | BOOL |  |  |  | X
Alarm | 1008 | 6 | 301009 | 04 | 3190 | Digital alarm input 49 | BOOL |  |  |  | X
Alarm | 1008 | 7 | 301009 | 04 | 3200 | Digital alarm input 50 | BOOL |  |  |  | X
Alarm | 1008 | 8 | 301009 | 04 | 3210 | Digital alarm input 51 | BOOL |  |  |  | X
Alarm | 1008 | 9 | 301009 | 04 | 3220 | Digital alarm input 52 | BOOL |  |  |  | X
Alarm | 1008 | 10 | 301009 | 04 | 3230 | Digital alarm input 53 | BOOL |  |  |  | X
Alarm | 1008 | 11 | 301009 | 04 | 3240 | Digital alarm input 54 | BOOL |  |  |  | X
Alarm | 1008 | 12 | 301009 | 04 | 3250 | Digital alarm input 55 | BOOL |  |  |  | X
Alarm | 1009 | 0 | 301010 | 04 | 3260 | Digital alarm input 65 | BOOL |  |  |  | X
Alarm | 1009 | 1 | 301010 | 04 | 3270 | Digital alarm input 66 | BOOL |  |  |  | X
Alarm | 1009 | 2 | 301010 | 04 | 3280 | Digital alarm input 67 | BOOL |  |  |  | X
Alarm | 1009 | 3 | 301010 | 04 | 3290 | Digital alarm input 68 | BOOL |  |  |  | X
Alarm | 1009 | 4 | 301010 | 04 | 3300 | Digital alarm input 69 | BOOL |  |  |  | X
Alarm | 1009 | 5 | 301010 | 04 | 3310 | Digital alarm input 70 | BOOL |  |  |  | X
Alarm | 1009 | 6 | 301010 | 04 | 3320 | Digital alarm input 71 | BOOL |  |  |  | X
Alarm | 1009 | 7 | 301010 | 04 | 3330 | Digital alarm input 91 | BOOL |  |  |  | X
Alarm | 1009 | 8 | 301010 | 04 | 3340 | Digital alarm input 92 | BOOL |  |  |  | X
Alarm | 1009 | 9 | 301010 | 04 | 3350 | Digital alarm input 93 | BOOL |  |  |  | X
Alarm | 1009 | 10 | 301010 | 04 | 3360 | Digital alarm input 94 | BOOL |  |  |  | X
Alarm | 1009 | 11 | 301010 | 04 | 3370 | Digital alarm input 95 | BOOL |  |  |  | X
Alarm | 1009 | 12 | 301010 | 04 | 3380 | Digital alarm input 96 | BOOL |  |  |  | X
Alarm | 1009 | 13 | 301010 | 04 | 3390 | Digital alarm input 97 | BOOL |  |  |  | X
Alarm | 1010 | 0 | 301011 | 04 | 3400 | Multi-in. Alarm 102 | BOOL |  |  |  | X
Alarm | 1010 | 1 | 301011 | 04 | 3410 | Multi-in. Alarm 105 | BOOL |  |  |  | X
Alarm | 1010 | 2 | 301011 | 04 | 3420 | Multi-in. Alarm 108 | BOOL |  |  |  | X
Alarm | 1010 | 3 | 301011 | 04 | 3401 | Wire fail. 102 | BOOL |  |  |  | X
Alarm | 1010 | 4 | 301011 | 04 | 3411 | Wire fail. 105 | BOOL |  |  |  | X
Alarm | 1010 | 5 | 301011 | 04 | 3421 | Wire fail. 108 | BOOL |  |  |  | X
Alarm | 1010 | 6 | 301011 | 04 | 3430 | Digital alarm input 112 | BOOL |  |  |  | X
Alarm | 1010 | 7 | 301011 | 04 | 3440 | Digital alarm input 113 | BOOL |  |  |  | X
Alarm | 1010 | 8 | 301011 | 04 | 3450 | Digital alarm input 114 | BOOL |  |  |  | X
Alarm | 1010 | 9 | 301011 | 04 | 3460 | Digital alarm input 115 | BOOL |  |  |  | X
Alarm | 1010 | 10 | 301011 | 04 | 3470 | Digital alarm input 116 | BOOL |  |  |  | X
Alarm | 1010 | 11 | 301011 | 04 | 3480 | Digital alarm input 117 | BOOL |  |  |  | X
Alarm | 1010 | 12 | 301011 | 04 | 3490 | Digital alarm input 118 (Emergency stop) | BOOL |  |  |  | X
Alarm | 1011 | 0 | 301012 | 04 | 3500 | Digital alarm input 127 | BOOL |  |  |  | X
Alarm | 1011 | 1 | 301012 | 04 | 3510 | Digital alarm input 128 | BOOL |  |  |  | X
Alarm | 1011 | 2 | 301012 | 04 | 3520 | Digital alarm input 129 | BOOL |  |  |  | X
Alarm | 1011 | 3 | 301012 | 04 | 3530 | Digital alarm input 130 | BOOL |  |  |  | X
Alarm | 1011 | 4 | 301012 | 04 | 3540 | Digital alarm input 131 | BOOL |  |  |  | X
Alarm | 1011 | 5 | 301012 | 04 | 3550 | Digital alarm input 132 | BOOL |  |  |  | X
Alarm | 1011 | 6 | 301012 | 04 | 3560 | Digital alarm input 133 | BOOL |  |  |  | X
Alarm | 1011 | 7 | 301012 | 04 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X
Alarm | 1011 | 8 | 301012 | 04 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X
Alarm | 1011 | 9 | 301012 | 04 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X
Alarm | 1011 | 10 | 301012 | 04 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X
Alarm | 1011 | 11 | 301012 | 04 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X
Alarm | 1012 | 0 | 301013 | 04 | 4000 | Analogue input 91.1 | BOOL |  |  |  | X
Alarm | 1012 | 1 | 301013 | 04 | 4010 | Analogue input 91.2 | BOOL |  |  |  | X
Alarm | 1012 | 2 | 301013 | 04 | 4020 | Wire failure analogue 91 | BOOL |  |  |  | X
Alarm | 1012 | 3 | 301013 | 04 | 4030 | Analogue input 93.1 | BOOL |  |  |  | X
Alarm | 1012 | 4 | 301013 | 04 | 4040 | Analogue input 93.2 | BOOL |  |  |  | X
Alarm | 1012 | 5 | 301013 | 04 | 4050 | Wire failure analogue 93 | BOOL |  |  |  | X
Alarm | 1012 | 6 | 301013 | 04 | 4060 | Analogue input 95.1 | BOOL |  |  |  | X
Alarm | 1012 | 7 | 301013 | 04 | 4070 | Analogue input 95.2 | BOOL |  |  |  | X
Alarm | 1012 | 8 | 301013 | 04 | 4080 | Wire failure analogue 95 | BOOL |  |  |  | X
Alarm | 1012 | 9 | 301013 | 04 | 4090 | Analogue input 97.1 | BOOL |  |  |  | X
Alarm | 1012 | 10 | 301013 | 04 | 4100 | Analogue input 97.2 | BOOL |  |  |  | X
Alarm | 1012 | 11 | 301013 | 04 | 4110 | Wire failure analogue 97 | BOOL |  |  |  | X
Alarm | 1013 | 0 | 301014 | 04 | 4120, 4140, 4160, 4180, 4200, 4220 | Multi input terminal 102.1 | BOOL |  |  |  | X
Alarm | 1013 | 1 | 301014 | 04 | 4130, 4150, 4170, 4190, 4210, 4230 | Multi input terminal 102.2 | BOOL |  |  |  | X
Alarm | 1013 | 2 | 301014 | 04 | 4240 | W. fail. 102 | BOOL |  |  |  | X
Alarm | 1013 | 3 | 301014 | 04 | 4250, 4270, 4290, 4310, 4330, 4350 | Multi input terminal 105.1 | BOOL |  |  |  | X
Alarm | 1013 | 4 | 301014 | 04 | 4260, 4280, 4300, 4320, 4340, 4360 | Multi input terminal 105.2 | BOOL |  |  |  | X
Alarm | 1013 | 5 | 301014 | 04 | 4370 | W. fail. 105 | BOOL |  |  |  | X
Alarm | 1013 | 6 | 301014 | 04 | 4380, 4400, 4420, 4440, 4460, 4480 | Multi input terminal 108.1 | BOOL |  |  |  | X
Alarm | 1013 | 7 | 301014 | 04 | 4390, 4410, 4430, 4450, 4470, 4490 | Multi input terminal 108.2 | BOOL |  |  |  | X
Alarm | 1013 | 8 | 301014 | 04 | 4500 | W. fail. 108 | BOOL |  |  |  | X
Alarm | 1013 | 9 | 301014 | 04 | 3660 | M-Logic alarm 10 | BOOL |  |  |  | X
Alarm | 1013 | 10 | 301014 | 04 | 3670 | M-Logic alarm 11 | BOOL |  |  |  | X
Alarm | 1013 | 11 | 301014 | 04 | 3680 | M-Logic alarm 12 | BOOL |  |  |  | X
Alarm | 1013 | 12 | 301014 | 04 | 3690 | M-Logic alarm 13 | BOOL |  |  |  | X
Alarm | 1013 | 13 | 301014 | 04 | 3700 | M-Logic alarm 14 | BOOL |  |  |  | X
Alarm | 1014 | 1 | 301015 | 04 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X
Alarm | 1014 | 2 | 301015 | 04 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X
Alarm | 1014 | 3 | 301015 | 04 | 4980 | U< aux. term. 98 | BOOL |  |  |  | X
Alarm | 1014 | 4 | 301015 | 04 | 4990 | U> aux. term. 98 | BOOL |  |  |  | X
Alarm | 1015 | 3 | 301016 | 04 | 6280 | Internal communication failure | BOOL |  |  |  | X
Alarm | 1015 | 12 | 301016 | 04 | 6540 | Unit not in auto | BOOL |  |  |  | X
Relay state | 1016 | 0 | 301017 | 04 | 5000 | Relay 5 | BOOL |  |  |  | X
Relay state | 1016 | 1 | 301017 | 04 | 5010 | Relay 8 | BOOL |  |  |  | X
Relay state | 1016 | 2 | 301017 | 04 | 5020 | Relay 11 | BOOL |  |  |  | X
Relay state | 1016 | 3 | 301017 | 04 | 5030 | Relay 14 | BOOL |  |  |  | X
Relay state | 1016 | 4 | 301017 | 04 | 5040 | Relay 17 | BOOL |  |  |  | X
Relay state | 1016 | 5 | 301017 | 04 | 5050 | Relay T20 | BOOL |  |  |  | X
Relay state | 1016 | 6 | 301017 | 04 | 5060 | Relay T21 | BOOL |  |  |  | X
Relay state | 1016 | 7 | 301017 | 04 | 5070 | Relay 29 | BOOL |  |  |  | X
Relay state | 1016 | 8 | 301017 | 04 | 5080 | Relay 31 | BOOL |  |  |  | X
Relay state | 1016 | 9 | 301017 | 04 | 5090 | Relay 33 | BOOL |  |  |  | X
Relay state | 1016 | 10 | 301017 | 04 | 5100 | Relay 35 | BOOL |  |  |  | X
Relay state | 1016 | 11 | 301017 | 04 | 5110 | Relay 57 | BOOL |  |  |  | X
Relay state | 1016 | 12 | 301017 | 04 | 5120 | Relay 59 | BOOL |  |  |  | X
Relay state | 1016 | 13 | 301017 | 04 | 5130 | Relay 61 | BOOL |  |  |  | X
Relay state | 1016 | 14 | 301017 | 04 | 5140 | Relay 63 | BOOL |  |  |  | X
Relay state | 1017 | 0 | 301018 | 04 | 5150 | Relay 65 | BOOL |  |  |  | X
Relay state | 1017 | 1 | 301018 | 04 | 5160 | Relay 67 | BOOL |  |  |  | X
Relay state | 1017 | 2 | 301018 | 04 | 5170 | Relay 69 | BOOL |  |  |  | X
Relay state | 1017 | 3 | 301018 | 04 | 5180 | Relay 71 | BOOL |  |  |  | X
Relay state | 1017 | 4 | 301018 | 04 | 5190 | Relay 90 | BOOL |  |  |  | X
Relay state | 1017 | 5 | 301018 | 04 | 5200 | Relay 92 | BOOL |  |  |  | X
Relay state | 1017 | 6 | 301018 | 04 | 5210 | Relay 94 | BOOL |  |  |  | X
Relay state | 1017 | 7 | 301018 | 04 | 5220 | Relay 96 | BOOL |  |  |  | X
Relay state | 1017 | 8 | 301018 | 04 | 5230 | Relay 126 | BOOL |  |  |  | X
Relay state | 1017 | 9 | 301018 | 04 | 5240 | Relay 128 | BOOL |  |  |  | X
Relay state | 1017 | 10 | 301018 | 04 | 5250 | Relay 130 | BOOL |  |  |  | X
Relay state | 1017 | 11 | 301018 | 04 | 5260 | Relay 132 | BOOL |  |  |  | X
Relay state | 1017 | 12 | 301018 | 04 | 5280 | Relay 119 | BOOL |  |  |  | X
Relay state | 1017 | 13 | 301018 | 04 | 5290 | Relay 120 | BOOL |  |  |  | X
Relay state | 1017 | 14 | 301018 | 04 | 5300 | Relay 121 | BOOL |  |  |  | X
Relay state | 1017 | 15 | 301018 | 04 | 5310 | Relay 123 | BOOL |  |  |  | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | Busbar Hz/V OK, timer expired | BOOL |  |  |  | X
Modes | 1019 | 2 | 301020 | 04 |  | Semi auto mode | BOOL |  |  |  | X
Modes | 1019 | 3 | 301020 | 04 |  | Auto mode | BOOL |  |  |  | X
PM alarm | 1031 | 1 | 301032 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X
PM alarm | 1031 | 2 | 301032 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X
PM alarm | 1031 | 3 | 301032 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X
PM alarm | 1031 | 4 | 301032 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X
PM alarm | 1031 | 5 | 301032 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X
PM alarm | 1031 | 6 | 301032 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X
PM alarm | 1031 | 7 | 301032 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X
PM alarm | 1031 | 8 | 301032 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X
PM alarm | 1031 | 9 | 301032 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X
PM alarm | 1031 | 10 | 301032 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X
PM alarm | 1031 | 11 | 301032 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X
PM alarm | 1031 | 12 | 301032 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X
PM alarm | 1031 | 13 | 301032 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X
PM alarm | 1031 | 14 | 301032 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X
PM alarm | 1031 | 15 | 301032 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X
PM alarm | 1032 | 0 | 301033 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X
PM alarm | 1032 | 2 | 301033 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X
PM alarm | 1032 | 3 | 301033 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X
PM alarm | 1032 | 4 | 301033 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X
PM alarm | 1032 | 5 | 301033 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X
PM alarm | 1032 | 6 | 301033 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X
PM alarm | 1032 | 7 | 301033 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X
PM alarm | 1032 | 8 | 301033 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X
PM alarm | 1032 | 9 | 301033 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X
PM alarm | 1032 | 10 | 301033 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X
PM alarm | 1032 | 11 | 301033 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X
PM alarm | 1032 | 12 | 301033 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X
PM alarm | 1032 | 13 | 301033 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X
PM alarm | 1032 | 14 | 301033 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X
PM alarm | 1032 | 15 | 301033 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X
Alarm | 1033 | 2 | 301034 | 04 | 7520 | Communication error ext. | BOOL |  |  |  | X
PM alarm | 1033 | 0 | 301034 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X
PM alarm | 1033 | 1 | 301034 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X
PM alarm | 1034 | 1 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X
PM alarm | 1034 | 2 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X
PM alarm | 1034 | 3 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 3 | BOOL |  |  |  | X
PM alarm | 1034 | 4 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 4 | BOOL |  |  |  | X
PM alarm | 1034 | 5 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 5 | BOOL |  |  |  | X
PM alarm | 1034 | 6 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 6 | BOOL |  |  |  | X
PM alarm | 1034 | 7 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 7 | BOOL |  |  |  | X
PM alarm | 1034 | 8 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 8 | BOOL |  |  |  | X
PM alarm | 1034 | 9 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 9 | BOOL |  |  |  | X
PM alarm | 1034 | 10 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 10 | BOOL |  |  |  | X
PM alarm | 1034 | 11 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 11 | BOOL |  |  |  | X
PM alarm | 1034 | 12 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 12 | BOOL |  |  |  | X
PM alarm | 1034 | 13 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 13 | BOOL |  |  |  | X
PM alarm | 1034 | 14 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 14 | BOOL |  |  |  | X
PM alarm | 1034 | 15 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 15 | BOOL |  |  |  | X
PM alarm | 1035 | 0 | 301036 | 04 |  | Ext. Modbus comm. error, CAN ID 16 | BOOL |  |  |  | X
PM alarm | 1040 | 0 | 301041 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X
PM alarm | 1040 | 1 | 301041 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X
PM alarm | 1040 | 2 | 301041 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X
PM alarm | 1040 | 3 | 301041 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X
PM alarm | 1040 | 4 | 301041 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X
PM alarm | 1040 | 5 | 301041 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X
PM alarm | 1040 | 6 | 301041 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X
PM alarm | 1040 | 7 | 301041 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X
PM alarm | 1040 | 8 | 301041 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X
PM alarm | 1040 | 9 | 301041 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X
PM alarm | 1040 | 10 | 301041 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X
PM alarm | 1040 | 11 | 301041 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X
PM alarm | 1040 | 12 | 301041 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X
PM alarm | 1040 | 13 | 301041 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X
PM alarm | 1040 | 14 | 301041 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X
PM alarm | 1040 | 15 | 301041 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X
PM alarm | 1041 | 0 | 301042 | 04 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X
PM alarm | 1041 | 1 | 301042 | 04 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X
PM alarm | 1041 | 2 | 301042 | 04 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X
PM alarm | 1041 | 3 | 301042 | 04 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X
PM alarm | 1041 | 4 | 301042 | 04 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X
PM alarm | 1041 | 5 | 301042 | 04 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X
PM alarm | 1041 | 6 | 301042 | 04 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X
PM alarm | 1041 | 7 | 301042 | 04 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X
PM alarm | 1041 | 8 | 301042 | 04 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X
PM alarm | 1041 | 9 | 301042 | 04 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X
PM alarm | 1041 | 10 | 301042 | 04 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X
PM alarm | 1041 | 11 | 301042 | 04 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X
PM alarm | 1041 | 12 | 301042 | 04 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X
PM alarm | 1041 | 13 | 301042 | 04 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X
PM alarm | 1041 | 14 | 301042 | 04 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X
PM alarm | 1041 | 15 | 301042 | 04 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X
PM alarm | 1042 | 0 | 301043 | 04 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X
PM alarm | 1042 | 1 | 301043 | 04 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X
PM alarm | 1042 | 2 | 301043 | 04 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X
PM alarm | 1042 | 3 | 301043 | 04 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X
PM alarm | 1042 | 4 | 301043 | 04 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X
PM alarm | 1042 | 5 | 301043 | 04 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X
PM alarm | 1042 | 6 | 301043 | 04 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X
PM alarm | 1042 | 7 | 301043 | 04 |  | CAN 1 missing ID 40 | BOOL |  |  |  | X
PM alarm | 1043 | 0 | 301044 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X
PM alarm | 1043 | 1 | 301044 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X
PM alarm | 1043 | 2 | 301044 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X
PM alarm | 1043 | 3 | 301044 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X
PM alarm | 1043 | 4 | 301044 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X
PM alarm | 1043 | 5 | 301044 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X
PM alarm | 1043 | 6 | 301044 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X
PM alarm | 1043 | 7 | 301044 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X
PM alarm | 1043 | 8 | 301044 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X
PM alarm | 1043 | 9 | 301044 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X
PM alarm | 1043 | 10 | 301044 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X
PM alarm | 1043 | 11 | 301044 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X
PM alarm | 1043 | 12 | 301044 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X
PM alarm | 1043 | 13 | 301044 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X
PM alarm | 1043 | 14 | 301044 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X
PM alarm | 1043 | 15 | 301044 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X
PM alarm | 1044 | 0 | 301045 | 04 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X
PM alarm | 1044 | 1 | 301045 | 04 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X
PM alarm | 1044 | 2 | 301045 | 04 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X
PM alarm | 1044 | 3 | 301045 | 04 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X
PM alarm | 1044 | 4 | 301045 | 04 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X
PM alarm | 1044 | 5 | 301045 | 04 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X
PM alarm | 1044 | 6 | 301045 | 04 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X
PM alarm | 1044 | 7 | 301045 | 04 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X
PM alarm | 1044 | 8 | 301045 | 04 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X
PM alarm | 1044 | 9 | 301045 | 04 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X
PM alarm | 1044 | 10 | 301045 | 04 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X
PM alarm | 1044 | 11 | 301045 | 04 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X
PM alarm | 1044 | 12 | 301045 | 04 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X
PM alarm | 1044 | 13 | 301045 | 04 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X
PM alarm | 1044 | 14 | 301045 | 04 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X
PM alarm | 1044 | 15 | 301045 | 04 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X
PM alarm | 1045 | 0 | 301046 | 04 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X
PM alarm | 1045 | 1 | 301046 | 04 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X
PM alarm | 1045 | 2 | 301046 | 04 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X
PM alarm | 1045 | 3 | 301046 | 04 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X
PM alarm | 1045 | 4 | 301046 | 04 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X
PM alarm | 1045 | 5 | 301046 | 04 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X
PM alarm | 1045 | 6 | 301046 | 04 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X
PM alarm | 1045 | 7 | 301046 | 04 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X
Alarm | 1046 | 0 | 301047 | 04 | 4800 | Analogue input 127.1 | BOOL |  |  |  | X
Alarm | 1046 | 1 | 301047 | 04 | 4810 | Analogue input 127.2 | BOOL |  |  |  | X
Alarm | 1046 | 2 | 301047 | 04 | 4820 | Wire fail analogue input 127 | BOOL |  |  |  | X
Alarm | 1046 | 3 | 301047 | 04 | 4830 | Analogue input 129.1 | BOOL |  |  |  | X
Alarm | 1046 | 4 | 301047 | 04 | 4840 | Analogue input 129.2 | BOOL |  |  |  | X
Alarm | 1046 | 5 | 301047 | 04 | 4850 | Wire fail analogue input 129 | BOOL |  |  |  | X
Alarm | 1046 | 6 | 301047 | 04 | 4860 | Analogue input 131.1 | BOOL |  |  |  | X
Alarm | 1046 | 7 | 301047 | 04 | 4870 | Analogue input 131.2 | BOOL |  |  |  | X
Alarm | 1046 | 8 | 301047 | 04 | 4880 | Wire fail analogue input 131 | BOOL |  |  |  | X
Alarm | 1046 | 9 | 301047 | 04 | 4890 | Analogue input 133.1 | BOOL |  |  |  | X
Alarm | 1046 | 10 | 301047 | 04 | 4900 | Analogue input 133.2 | BOOL |  |  |  | X
Alarm | 1046 | 11 | 301047 | 04 | 4910 | Wire fail analogue input 133 | BOOL |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | Load U > 30% of U nominal | BOOL |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 04 |  | BB U > 30% of U nominal | BOOL |  |  |  | X
M-Logic state | 1051 |  | 301052 | 04 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X
M-Logic state | 1052 |  | 301053 | 04 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X
Alarm | 1053 | 4 | 301054 | 04 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 5 | 301054 | 04 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X
Alarm | 1053 | 6 | 301054 | 04 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 7 | 301054 | 04 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X
Alarm | 1053 | 8 | 301054 | 04 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 9 | 301054 | 04 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X
Alarm | 1053 | 10 | 301054 | 04 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 11 | 301054 | 04 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X
Alarm | 1053 | 12 | 301054 | 04 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 13 | 301054 | 04 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X
Alarm | 1053 | 14 | 301054 | 04 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X
Alarm | 1053 | 15 | 301054 | 04 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X
Plant logic state | 1055 | 0 | 301056 | 04 |  | Load group 1 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 1 | 301056 | 04 |  | Load group 2 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 2 | 301056 | 04 |  | Load group 3 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 3 | 301056 | 04 |  | Load group 4 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 4 | 301056 | 04 |  | Load group 5 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 5 | 301056 | 04 |  | Load group 6 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 6 | 301056 | 04 |  | Load group 7 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 7 | 301056 | 04 |  | Load group 8 open feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 8 | 301056 | 04 |  | Load group 1 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 9 | 301056 | 04 |  | Load group 2 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 10 | 301056 | 04 |  | Load group 3 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 11 | 301056 | 04 |  | Load group 4 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 12 | 301056 | 04 |  | Load group 5 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 13 | 301056 | 04 |  | Load group 6 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 14 | 301056 | 04 |  | Load group 7 close feedback | BOOL |  |  |  | X
Plant logic state | 1055 | 15 | 301056 | 04 |  | Load group 8 close feedback | BOOL |  |  |  | X
Alarm | 1057 | 0 | 301058 | 04 |  | Fail class: Warning active | BOOL |  |  |  | X
Alarm | 1057 | 1 | 301058 | 04 |  | Fail class: Trip load group 1 active | BOOL |  |  |  | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Trip load group 2 active | BOOL |  |  |  | X
Alarm | 1057 | 3 | 301058 | 04 |  | Fail class: Trip load group 3 active | BOOL |  |  |  | X
Alarm | 1057 | 4 | 301058 | 04 |  | Fail class: Trip load group 4 active | BOOL |  |  |  | X
Alarm | 1057 | 5 | 301058 | 04 |  | Fail class: Trip load group 5 active | BOOL |  |  |  | X
Alarm | 1057 | 6 | 301058 | 04 |  | Fail class: Trip load group 6 active | BOOL |  |  |  | X
Alarm | 1057 | 7 | 301058 | 04 |  | Fail class: Trip load group 7 active | BOOL |  |  |  | X
Alarm | 1057 | 8 | 301058 | 04 |  | Fail class: Trip load group 8 active | BOOL |  |  |  | X
Alarm | 1057 | 9 | 301058 | 04 |  | Fail class: Trip all load groups active | BOOL |  |  |  | X
Alarm | 1058 | 1 | 301059 | 04 |  | Fail class: Block load group 1 active | BOOL |  |  |  | X
Alarm | 1058 | 2 | 301059 | 04 |  | Fail class: Block load group 2 active | BOOL |  |  |  | X
Alarm | 1058 | 3 | 301059 | 04 |  | Fail class: Block load group 3 active | BOOL |  |  |  | X
Alarm | 1058 | 4 | 301059 | 04 |  | Fail class: Block load group 4 active | BOOL |  |  |  | X
Alarm | 1058 | 5 | 301059 | 04 |  | Fail class: Block load group 5 active | BOOL |  |  |  | X
Alarm | 1058 | 6 | 301059 | 04 |  | Fail class: Block load group 6 active | BOOL |  |  |  | X
Alarm | 1058 | 7 | 301059 | 04 |  | Fail class: Block load group 7 active | BOOL |  |  |  | X
Alarm | 1058 | 8 | 301059 | 04 |  | Fail class: Block load group 8 active | BOOL |  |  |  | X
Alarm | 1058 | 9 | 301059 | 04 |  | Fail class: Block all load groups active | BOOL |  |  |  | X
M-Logic state | 1059 |  | 301060 | 04 |  | Virtual events 33-48 | INT16s | AB | 0 |  | X
M-Logic state | 1060 |  | 301061 | 04 |  | Virtual events 49-64 | INT16s | AB | 0 |  | X
M-Logic state | 1061 |  | 301062 | 04 |  | Virtual events 65-80 | INT16s | AB | 0 |  | X
M-Logic state | 1062 |  | 301063 | 04 |  | Virtual events 81-96 | INT16s | AB | 0 |  | X
PM AC measurement | 1505 |  | 301506 | 04 |  | Number of gensets in application | INT16s | AB | 0 |  | X
PM AC measurement | 1510 |  | 301511 | 04 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X
PM AC measurement | 1511 |  | 301512 | 04 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X
PM AC measurement | 1512 |  | 301513 | 04 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X
PM AC measurement | 1513 |  | 301514 | 04 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X
PM AC measurement | 1514 |  | 301515 | 04 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X
PM AC measurement | 1515 |  | 301516 | 04 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X
PM AC measurement | 1516 |  | 301517 | 04 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X
PM AC measurement | 1517 |  | 301518 | 04 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X
PM AC measurement | 1518 |  | 301519 | 04 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X
PM AC measurement | 1519 |  | 301520 | 04 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X
PM AC measurement | 1520 |  | 301521 | 04 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X
PM AC measurement | 1521 |  | 301522 | 04 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X
PM AC measurement | 1522 |  | 301523 | 04 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X
PM AC measurement | 1523 |  | 301524 | 04 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X
PM AC measurement | 1524 |  | 301525 | 04 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X
PM AC measurement | 1525 |  | 301526 | 04 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X
PM AC measurement | 1526 |  | 301527 | 04 |  | Active Power ID 1 | INT16s | AB | 0 |  | X
PM AC measurement | 1527 |  | 301528 | 04 |  | Active Power ID 2 | INT16s | AB | 0 |  | X
PM AC measurement | 1528 |  | 301529 | 04 |  | Active Power ID 3 | INT16s | AB | 0 |  | X
PM AC measurement | 1529 |  | 301530 | 04 |  | Active Power ID 4 | INT16s | AB | 0 |  | X
PM AC measurement | 1530 |  | 301531 | 04 |  | Active Power ID 5 | INT16s | AB | 0 |  | X
PM AC measurement | 1531 |  | 301532 | 04 |  | Active Power ID 6 | INT16s | AB | 0 |  | X
PM AC measurement | 1532 |  | 301533 | 04 |  | Active Power ID 7 | INT16s | AB | 0 |  | X
PM AC measurement | 1533 |  | 301534 | 04 |  | Active Power ID 8 | INT16s | AB | 0 |  | X
PM AC measurement | 1534 |  | 301535 | 04 |  | Active Power ID 9 | INT16s | AB | 0 |  | X
PM AC measurement | 1535 |  | 301536 | 04 |  | Active Power ID 10 | INT16s | AB | 0 |  | X
PM AC measurement | 1536 |  | 301537 | 04 |  | Active Power ID 11 | INT16s | AB | 0 |  | X
PM AC measurement | 1537 |  | 301538 | 04 |  | Active Power ID 12 | INT16s | AB | 0 |  | X
PM AC measurement | 1538 |  | 301539 | 04 |  | Active Power ID 13 | INT16s | AB | 0 |  | X
PM AC measurement | 1539 |  | 301540 | 04 |  | Active Power ID 14 | INT16s | AB | 0 |  | X
PM AC measurement | 1540 |  | 301541 | 04 |  | Active Power ID 15 | INT16s | AB | 0 |  | X
PM AC measurement | 1541 |  | 301542 | 04 |  | Active Power ID 16 | INT16s | AB | 0 |  | X
PM AC measurement | 1542 |  | 301543 | 04 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X
PM AC measurement | 1543 |  | 301544 | 04 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X
PM AC measurement | 1544 |  | 301545 | 04 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X
PM AC measurement | 1545 |  | 301546 | 04 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X
PM AC measurement | 1546 |  | 301547 | 04 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X
PM AC measurement | 1547 |  | 301548 | 04 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X
PM AC measurement | 1548 |  | 301549 | 04 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X
PM AC measurement | 1549 |  | 301550 | 04 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X
PM AC measurement | 1550 |  | 301551 | 04 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X
PM AC measurement | 1551 |  | 301552 | 04 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X
PM AC measurement | 1552 |  | 301553 | 04 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X
PM AC measurement | 1553 |  | 301554 | 04 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X
PM AC measurement | 1554 |  | 301555 | 04 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X
PM AC measurement | 1555 |  | 301556 | 04 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X
PM AC measurement | 1556 |  | 301557 | 04 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X
PM AC measurement | 1557 |  | 301558 | 04 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X
PM AC measurement | 1569 |  | 301570 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X
PM AC measurement | 1570 |  | 301571 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X
PM AC measurement | 1571 |  | 301572 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X
PM AC measurement | 1572 |  | 301573 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X
PM AC measurement | 1573 |  | 301574 | 04 |  | Active Power ID 21 | INT16s | AB | 0 |  | X
PM AC measurement | 1574 |  | 301575 | 04 |  | Active Power ID 22 | INT16s | AB | 0 |  | X
PM AC measurement | 1575 |  | 301576 | 04 |  | Active Power ID 23 | INT16s | AB | 0 |  | X
PM AC measurement | 1576 |  | 301577 | 04 |  | Active Power ID 24 | INT16s | AB | 0 |  | X
PM AC measurement | 1577 |  | 301578 | 04 |  | Active Power ID 25 | INT16s | AB | 0 |  | X
PM AC measurement | 1578 |  | 301579 | 04 |  | Active Power ID 26 | INT16s | AB | 0 |  | X
PM AC measurement | 1579 |  | 301580 | 04 |  | Active Power ID 27 | INT16s | AB | 0 |  | X
PM AC measurement | 1580 |  | 301581 | 04 |  | Active Power ID 28 | INT16s | AB | 0 |  | X
PM AC measurement | 1581 |  | 301582 | 04 |  | Active Power ID 29 | INT16s | AB | 0 |  | X
PM AC measurement | 1582 |  | 301583 | 04 |  | Active Power ID 30 | INT16s | AB | 0 |  | X
PM AC measurement | 1583 |  | 301584 | 04 |  | Active Power ID 31 | INT16s | AB | 0 |  | X
PM AC measurement | 1584 |  | 301585 | 04 |  | Active Power ID 32 | INT16s | AB | 0 |  | X
PM AC measurement | 1585 |  | 301586 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X
PM AC measurement | 1586 |  | 301587 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X
PM AC measurement | 1587 |  | 301588 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X
PM AC measurement | 1588 |  | 301589 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X
PM AC measurement | 1589 |  | 301590 | 04 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X
PM AC measurement | 1590 |  | 301591 | 04 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X
PM AC measurement | 1591 |  | 301592 | 04 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X
PM AC measurement | 1592 |  | 301593 | 04 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X
PM AC measurement | 1593 |  | 301594 | 04 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X
PM AC measurement | 1594 |  | 301595 | 04 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X
PM AC measurement | 1595 |  | 301596 | 04 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X
PM AC measurement | 1596 |  | 301597 | 04 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X
PM AC measurement | 1597 |  | 301598 | 04 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X
PM AC measurement | 1598 |  | 301599 | 04 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X
PM AC measurement | 1599 |  | 301600 | 04 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X
PM AC measurement | 1600 |  | 301601 | 04 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X
PM AC measurement | 1601 |  | 301602 | 04 |  | Active Power ID 33 | INT16s | AB | 0 |  | X
PM AC measurement | 1602 |  | 301603 | 04 |  | Active Power ID 34 | INT16s | AB | 0 |  | X
PM AC measurement | 1603 |  | 301604 | 04 |  | Active Power ID 35 | INT16s | AB | 0 |  | X
PM AC measurement | 1604 |  | 301605 | 04 |  | Active Power ID 36 | INT16s | AB | 0 |  | X
PM AC measurement | 1605 |  | 301606 | 04 |  | Active Power ID 37 | INT16s | AB | 0 |  | X
PM AC measurement | 1606 |  | 301607 | 04 |  | Active Power ID 38 | INT16s | AB | 0 |  | X
PM AC measurement | 1607 |  | 301608 | 04 |  | Active Power ID 39 | INT16s | AB | 0 |  | X
PM AC measurement | 1608 |  | 301609 | 04 |  | Active Power ID 40 | INT16s | AB | 0 |  | X
PM AC measurement | 1609 |  | 301610 | 04 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X
PM AC measurement | 1610 |  | 301611 | 04 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X
PM AC measurement | 1611 |  | 301612 | 04 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X
PM AC measurement | 1612 |  | 301613 | 04 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X
PM AC measurement | 1613 |  | 301614 | 04 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X
PM AC measurement | 1614 |  | 301615 | 04 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X
PM AC measurement | 1615 |  | 301616 | 04 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X
PM AC measurement | 1616 |  | 301617 | 04 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X
PM AC measurement | 1617 |  | 301618 | 04 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X
PM AC measurement | 1618 |  | 301619 | 04 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X
PM AC measurement | 1619 |  | 301620 | 04 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X
PM AC measurement | 1620 |  | 301621 | 04 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X
PM AC measurement | 1621 |  | 301622 | 04 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X
PM AC measurement | 1622 |  | 301623 | 04 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X
PM AC measurement | 1623 |  | 301624 | 04 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X
PM AC measurement | 1624 |  | 301625 | 04 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X
PM AC measurement | 1625 |  | 301626 | 04 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X
PM AC measurement | 1626 |  | 301627 | 04 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X
PM AC measurement | 1627 |  | 301628 | 04 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X
PM AC measurement | 1628 |  | 301629 | 04 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X
PM AC measurement | 1629 |  | 301630 | 04 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X
PM AC measurement | 1630 |  | 301631 | 04 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X
PM AC measurement | 1631 |  | 301632 | 04 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X
PM AC measurement | 1632 |  | 301633 | 04 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X
PM AC measurement | 1633 |  | 301634 | 04 |  | Bus power mains 17 | INT16s | AB | 0 |  | X
PM AC measurement | 1634 |  | 301635 | 04 |  | Bus power mains 18 | INT16s | AB | 0 |  | X
PM AC measurement | 1635 |  | 301636 | 04 |  | Bus power mains 19 | INT16s | AB | 0 |  | X
PM AC measurement | 1636 |  | 301637 | 04 |  | Bus power mains 20 | INT16s | AB | 0 |  | X
PM AC measurement | 1637 |  | 301638 | 04 |  | Bus power mains 21 | INT16s | AB | 0 |  | X
PM AC measurement | 1638 |  | 301639 | 04 |  | Bus power mains 22 | INT16s | AB | 0 |  | X
PM AC measurement | 1639 |  | 301640 | 04 |  | Bus power mains 23 | INT16s | AB | 0 |  | X
PM AC measurement | 1640 |  | 301641 | 04 |  | Bus power mains 24 | INT16s | AB | 0 |  | X
PM AC measurement | 1641 |  | 301642 | 04 |  | Bus power mains 25 | INT16s | AB | 0 |  | X
PM AC measurement | 1642 |  | 301643 | 04 |  | Bus power mains 26 | INT16s | AB | 0 |  | X
PM AC measurement | 1643 |  | 301644 | 04 |  | Bus power mains 27 | INT16s | AB | 0 |  | X
PM AC measurement | 1644 |  | 301645 | 04 |  | Bus power mains 28 | INT16s | AB | 0 |  | X
PM AC measurement | 1645 |  | 301646 | 04 |  | Bus power mains 29 | INT16s | AB | 0 |  | X
PM AC measurement | 1646 |  | 301647 | 04 |  | Bus power mains 30 | INT16s | AB | 0 |  | X
PM AC measurement | 1647 |  | 301648 | 04 |  | Bus power mains 31 | INT16s | AB | 0 |  | X
PM AC measurement | 1648 |  | 301649 | 04 |  | Bus power mains 32 | INT16s | AB | 0 |  | X
PM Plant logic state | 1649 | 0 | 301650 | 04 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 1 | 301650 | 04 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 2 | 301650 | 04 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 3 | 301650 | 04 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 4 | 301650 | 04 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 5 | 301650 | 04 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 6 | 301650 | 04 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 7 | 301650 | 04 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 8 | 301650 | 04 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 9 | 301650 | 04 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 10 | 301650 | 04 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 11 | 301650 | 04 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 12 | 301650 | 04 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 13 | 301650 | 04 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 14 | 301650 | 04 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1649 | 15 | 301650 | 04 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 0 | 301651 | 04 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 1 | 301651 | 04 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 2 | 301651 | 04 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 3 | 301651 | 04 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 4 | 301651 | 04 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 5 | 301651 | 04 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 6 | 301651 | 04 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 7 | 301651 | 04 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 8 | 301651 | 04 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 9 | 301651 | 04 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 10 | 301651 | 04 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 11 | 301651 | 04 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 12 | 301651 | 04 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 13 | 301651 | 04 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 14 | 301651 | 04 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1650 | 15 | 301651 | 04 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 0 | 301652 | 04 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 1 | 301652 | 04 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 2 | 301652 | 04 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 3 | 301652 | 04 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 4 | 301652 | 04 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 5 | 301652 | 04 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 6 | 301652 | 04 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1651 | 7 | 301652 | 04 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1652 | 0 | 301653 | 04 |  | ID 33 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 1 | 301653 | 04 |  | ID 34 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 2 | 301653 | 04 |  | ID 35 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 3 | 301653 | 04 |  | ID 36 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 4 | 301653 | 04 |  | ID 37 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 5 | 301653 | 04 |  | ID 38 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 6 | 301653 | 04 |  | ID 39 BTB controlled | BOOL |  |  |  | X
PM Plant logic state | 1652 | 7 | 301653 | 04 |  | ID 40 BTB controlled | BOOL |  |  |  | X
PM AC measurement | 1653 |  | 301654 | 04 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X
PM AC measurement | 1654 |  | 301655 | 04 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X
PM AC measurement | 1655 |  | 301656 | 04 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X
PM AC measurement | 1656 |  | 301657 | 04 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X
PM AC measurement | 1657 |  | 301658 | 04 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X
PM AC measurement | 1658 |  | 301659 | 04 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X
PM AC measurement | 1659 |  | 301660 | 04 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X
PM AC measurement | 1660 |  | 301661 | 04 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X
PM AC measurement | 1661 |  | 301662 | 04 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X
PM AC measurement | 1662 |  | 301663 | 04 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X
PM AC measurement | 1663 |  | 301664 | 04 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X
PM AC measurement | 1664 |  | 301665 | 04 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X
PM AC measurement | 1665 |  | 301666 | 04 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X
PM AC measurement | 1666 |  | 301667 | 04 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X
PM AC measurement | 1667 |  | 301668 | 04 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X
PM AC measurement | 1668 |  | 301669 | 04 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X
PM Plant logic state | 1700 | 1 | 301701 | 04 |  | Mains unit available | BOOL |  |  |  | X
PM Plant logic state | 1700 | 4 | 301701 | 04 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X
PM Plant logic state | 1700 | 5 | 301701 | 04 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X
PM Plant logic state | 1700 | 6 | 301701 | 04 |  | Any GB pos. ON | BOOL |  |  |  | X
PM Plant logic state | 1701 | 0 | 301702 | 04 |  | GB pos. ON ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 1 | 301702 | 04 |  | GB pos. ON ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 2 | 301702 | 04 |  | GB pos. ON ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 3 | 301702 | 04 |  | GB pos. ON ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 4 | 301702 | 04 |  | GB pos. ON ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 5 | 301702 | 04 |  | GB pos. ON ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 6 | 301702 | 04 |  | GB pos. ON ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 7 | 301702 | 04 |  | GB pos. ON ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 8 | 301702 | 04 |  | GB pos. ON ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 9 | 301702 | 04 |  | GB pos. ON ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 10 | 301702 | 04 |  | GB pos. ON ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 11 | 301702 | 04 |  | GB pos. ON ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 12 | 301702 | 04 |  | GB pos. ON ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 13 | 301702 | 04 |  | GB pos. ON ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 14 | 301702 | 04 |  | GB pos. ON ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1701 | 15 | 301702 | 04 |  | GB pos. ON ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 0 | 301703 | 04 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 1 | 301703 | 04 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 2 | 301703 | 04 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 3 | 301703 | 04 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 4 | 301703 | 04 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 5 | 301703 | 04 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 6 | 301703 | 04 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 7 | 301703 | 04 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 8 | 301703 | 04 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 9 | 301703 | 04 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 10 | 301703 | 04 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 11 | 301703 | 04 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 12 | 301703 | 04 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 13 | 301703 | 04 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 14 | 301703 | 04 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1702 | 15 | 301703 | 04 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 0 | 301704 | 04 |  | DG Hz/V OK, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 1 | 301704 | 04 |  | DG Hz/V OK, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 2 | 301704 | 04 |  | DG Hz/V OK, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 3 | 301704 | 04 |  | DG Hz/V OK, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 4 | 301704 | 04 |  | DG Hz/V OK, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 5 | 301704 | 04 |  | DG Hz/V OK, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 6 | 301704 | 04 |  | DG Hz/V OK, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 7 | 301704 | 04 |  | DG Hz/V OK, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 8 | 301704 | 04 |  | DG Hz/V OK, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 9 | 301704 | 04 |  | DG Hz/V OK, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 10 | 301704 | 04 |  | DG Hz/V OK, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 11 | 301704 | 04 |  | DG Hz/V OK, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 12 | 301704 | 04 |  | DG Hz/V OK, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 13 | 301704 | 04 |  | DG Hz/V OK, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 14 | 301704 | 04 |  | DG Hz/V OK, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1703 | 15 | 301704 | 04 |  | DG Hz/V OK, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 0 | 301706 | 04 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 1 | 301706 | 04 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 2 | 301706 | 04 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 3 | 301706 | 04 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 4 | 301706 | 04 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 5 | 301706 | 04 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 6 | 301706 | 04 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 7 | 301706 | 04 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 8 | 301706 | 04 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 9 | 301706 | 04 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 10 | 301706 | 04 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 11 | 301706 | 04 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 12 | 301706 | 04 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 13 | 301706 | 04 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 14 | 301706 | 04 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1705 | 15 | 301706 | 04 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 0 | 301708 | 04 |  | Any alarms, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 1 | 301708 | 04 |  | Any alarms, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 2 | 301708 | 04 |  | Any alarms, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 3 | 301708 | 04 |  | Any alarms, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 4 | 301708 | 04 |  | Any alarms, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 5 | 301708 | 04 |  | Any alarms, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 6 | 301708 | 04 |  | Any alarms, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 7 | 301708 | 04 |  | Any alarms, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 8 | 301708 | 04 |  | Any alarms, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 9 | 301708 | 04 |  | Any alarms, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 10 | 301708 | 04 |  | Any alarms, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 11 | 301708 | 04 |  | Any alarms, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 12 | 301708 | 04 |  | Any alarms, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 13 | 301708 | 04 |  | Any alarms, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 14 | 301708 | 04 |  | Any alarms, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1707 | 15 | 301708 | 04 |  | Any alarms, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 0 | 301710 | 04 |  | Engine running, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 1 | 301710 | 04 |  | Engine running, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 2 | 301710 | 04 |  | Engine running, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 3 | 301710 | 04 |  | Engine running, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 4 | 301710 | 04 |  | Engine running, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 5 | 301710 | 04 |  | Engine running, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 6 | 301710 | 04 |  | Engine running, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 7 | 301710 | 04 |  | Engine running, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 8 | 301710 | 04 |  | Engine running, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 9 | 301710 | 04 |  | Engine running, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 10 | 301710 | 04 |  | Engine running, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 11 | 301710 | 04 |  | Engine running, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 12 | 301710 | 04 |  | Engine running, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 13 | 301710 | 04 |  | Engine running, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 14 | 301710 | 04 |  | Engine running, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1709 | 15 | 301710 | 04 |  | Engine running, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 0 | 301712 | 04 |  | GB synchronising, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 1 | 301712 | 04 |  | GB synchronising, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 2 | 301712 | 04 |  | GB synchronising, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 3 | 301712 | 04 |  | GB synchronising, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 4 | 301712 | 04 |  | GB synchronising, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 5 | 301712 | 04 |  | GB synchronising, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 6 | 301712 | 04 |  | GB synchronising, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 7 | 301712 | 04 |  | GB synchronising, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 8 | 301712 | 04 |  | GB synchronising, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 9 | 301712 | 04 |  | GB synchronising, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 10 | 301712 | 04 |  | GB synchronising, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 11 | 301712 | 04 |  | GB synchronising, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 12 | 301712 | 04 |  | GB synchronising, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 13 | 301712 | 04 |  | GB synchronising, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 14 | 301712 | 04 |  | GB synchronising, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1711 | 15 | 301712 | 04 |  | GB synchronising, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 0 | 301713 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 1 | 301713 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 2 | 301713 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 3 | 301713 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 4 | 301713 | 04 |  | Mains OK, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 5 | 301713 | 04 |  | Mains OK, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 6 | 301713 | 04 |  | Mains OK, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 7 | 301713 | 04 |  | Mains OK, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 8 | 301713 | 04 |  | Mains OK, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 9 | 301713 | 04 |  | Mains OK, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 10 | 301713 | 04 |  | Mains OK, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 11 | 301713 | 04 |  | Mains OK, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 12 | 301713 | 04 |  | Mains OK, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 13 | 301713 | 04 |  | Mains OK, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 14 | 301713 | 04 |  | Mains OK, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1712 | 15 | 301713 | 04 |  | Mains OK, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 0 | 301714 | 04 |  | Mains not in semi 17 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 1 | 301714 | 04 |  | Mains not in semi 18 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 2 | 301714 | 04 |  | Mains not in semi 19 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 3 | 301714 | 04 |  | Mains not in semi 20 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 4 | 301714 | 04 |  | Mains not in semi 21 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 5 | 301714 | 04 |  | Mains not in semi 22 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 6 | 301714 | 04 |  | Mains not in semi 23 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 7 | 301714 | 04 |  | Mains not in semi 24 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 8 | 301714 | 04 |  | Mains not in semi 25 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 9 | 301714 | 04 |  | Mains not in semi 26 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 10 | 301714 | 04 |  | Mains not in semi 27 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 11 | 301714 | 04 |  | Mains not in semi 28 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 12 | 301714 | 04 |  | Mains not in semi 29 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 13 | 301714 | 04 |  | Mains not in semi 30 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 14 | 301714 | 04 |  | Mains not in semi 31 | BOOL |  |  |  | X
PM Plant logic state | 1713 | 15 | 301714 | 04 |  | Mains not in semi 32 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 0 | 301715 | 04 |  | Any alarms, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 1 | 301715 | 04 |  | Any alarms, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 2 | 301715 | 04 |  | Any alarms, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 3 | 301715 | 04 |  | Any alarms, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 4 | 301715 | 04 |  | Any alarms, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 5 | 301715 | 04 |  | Any alarms, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 6 | 301715 | 04 |  | Any alarms, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 7 | 301715 | 04 |  | Any alarms, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 8 | 301715 | 04 |  | Any alarms, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 9 | 301715 | 04 |  | Any alarms, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 10 | 301715 | 04 |  | Any alarms, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 11 | 301715 | 04 |  | Any alarms, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 12 | 301715 | 04 |  | Any alarms, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 13 | 301715 | 04 |  | Any alarms, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 14 | 301715 | 04 |  | Any alarms, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1714 | 15 | 301715 | 04 |  | Any alarms, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 0 | 301716 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 1 | 301716 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 2 | 301716 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 3 | 301716 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 4 | 301716 | 04 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 5 | 301716 | 04 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 6 | 301716 | 04 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 7 | 301716 | 04 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 8 | 301716 | 04 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 9 | 301716 | 04 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 10 | 301716 | 04 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 11 | 301716 | 04 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 12 | 301716 | 04 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 13 | 301716 | 04 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 14 | 301716 | 04 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1715 | 15 | 301716 | 04 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 0 | 301717 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 1 | 301717 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 2 | 301717 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 3 | 301717 | 04 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 4 | 301717 | 04 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 5 | 301717 | 04 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 6 | 301717 | 04 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 7 | 301717 | 04 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 8 | 301717 | 04 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 9 | 301717 | 04 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 10 | 301717 | 04 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 11 | 301717 | 04 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 12 | 301717 | 04 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 13 | 301717 | 04 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 14 | 301717 | 04 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1716 | 15 | 301717 | 04 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 0 | 301718 | 04 |  | Mains failure, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 1 | 301718 | 04 |  | Mains failure, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 2 | 301718 | 04 |  | Mains failure, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 3 | 301718 | 04 |  | Mains failure, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 4 | 301718 | 04 |  | Mains failure, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 5 | 301718 | 04 |  | Mains failure, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 6 | 301718 | 04 |  | Mains failure, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 7 | 301718 | 04 |  | Mains failure, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 8 | 301718 | 04 |  | Mains failure, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 9 | 301718 | 04 |  | Mains failure, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 10 | 301718 | 04 |  | Mains failure, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 11 | 301718 | 04 |  | Mains failure, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 12 | 301718 | 04 |  | Mains failure, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 13 | 301718 | 04 |  | Mains failure, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 14 | 301718 | 04 |  | Mains failure, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1717 | 15 | 301718 | 04 |  | Mains failure, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 0 | 301719 | 04 |  | MB synchronising, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 1 | 301719 | 04 |  | MB synchronising, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 2 | 301719 | 04 |  | MB synchronising, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 3 | 301719 | 04 |  | MB synchronising, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 4 | 301719 | 04 |  | MB synchronising, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 5 | 301719 | 04 |  | MB synchronising, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 6 | 301719 | 04 |  | MB synchronising, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 7 | 301719 | 04 |  | MB synchronising, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 8 | 301719 | 04 |  | MB synchronising, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 9 | 301719 | 04 |  | MB synchronising, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 10 | 301719 | 04 |  | MB synchronising, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 11 | 301719 | 04 |  | MB synchronising, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 12 | 301719 | 04 |  | MB synchronising, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 13 | 301719 | 04 |  | MB synchronising, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 14 | 301719 | 04 |  | MB synchronising, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1718 | 15 | 301719 | 04 |  | MB synchronising, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 0 | 301720 | 04 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 1 | 301720 | 04 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 2 | 301720 | 04 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 3 | 301720 | 04 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 4 | 301720 | 04 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 5 | 301720 | 04 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 6 | 301720 | 04 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 7 | 301720 | 04 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 8 | 301720 | 04 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 9 | 301720 | 04 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 10 | 301720 | 04 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 11 | 301720 | 04 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 12 | 301720 | 04 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 13 | 301720 | 04 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 14 | 301720 | 04 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1719 | 15 | 301720 | 04 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 0 | 301721 | 04 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 1 | 301721 | 04 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 2 | 301721 | 04 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 3 | 301721 | 04 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 4 | 301721 | 04 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 5 | 301721 | 04 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 6 | 301721 | 04 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 7 | 301721 | 04 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 8 | 301721 | 04 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 9 | 301721 | 04 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 10 | 301721 | 04 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 11 | 301721 | 04 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 12 | 301721 | 04 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 13 | 301721 | 04 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 14 | 301721 | 04 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1720 | 15 | 301721 | 04 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 0 | 301722 | 04 |  | TB synchronising, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 1 | 301722 | 04 |  | TB synchronising, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 2 | 301722 | 04 |  | TB synchronising, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 3 | 301722 | 04 |  | TB synchronising, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 4 | 301722 | 04 |  | TB synchronising, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 5 | 301722 | 04 |  | TB synchronising, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 6 | 301722 | 04 |  | TB synchronising, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 7 | 301722 | 04 |  | TB synchronising, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 8 | 301722 | 04 |  | TB synchronising, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 9 | 301722 | 04 |  | TB synchronising, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 10 | 301722 | 04 |  | TB synchronising, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 11 | 301722 | 04 |  | TB synchronising, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 12 | 301722 | 04 |  | TB synchronising, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 13 | 301722 | 04 |  | TB synchronising, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 14 | 301722 | 04 |  | TB synchronising, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1721 | 15 | 301722 | 04 |  | TB synchronising, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 0 | 301723 | 04 |  | Any alarms, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 1 | 301723 | 04 |  | Any alarms, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 2 | 301723 | 04 |  | Any alarms, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 3 | 301723 | 04 |  | Any alarms, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 4 | 301723 | 04 |  | Any alarms, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 5 | 301723 | 04 |  | Any alarms, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 6 | 301723 | 04 |  | Any alarms, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1722 | 7 | 301723 | 04 |  | Any alarms, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 0 | 301726 | 04 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 1 | 301726 | 04 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 2 | 301726 | 04 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 3 | 301726 | 04 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 4 | 301726 | 04 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 5 | 301726 | 04 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 6 | 301726 | 04 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1725 | 7 | 301726 | 04 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X
PM alarm | 1727 | 0 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X
PM alarm | 1727 | 1 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X
PM alarm | 1727 | 2 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X
PM alarm | 1727 | 3 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X
PM alarm | 1727 | 4 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X
PM alarm | 1727 | 5 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X
PM alarm | 1727 | 6 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X
PM alarm | 1727 | 7 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X
PM alarm | 1727 | 8 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X
PM alarm | 1727 | 9 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X
PM alarm | 1727 | 10 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X
PM alarm | 1727 | 11 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X
PM alarm | 1727 | 12 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X
PM alarm | 1727 | 13 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X
PM alarm | 1727 | 14 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X
PM alarm | 1727 | 15 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X
PM alarm | 1728 | 0 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X
PM alarm | 1728 | 1 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X
PM alarm | 1728 | 2 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X
PM alarm | 1728 | 3 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X
PM alarm | 1728 | 4 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X
PM alarm | 1728 | 5 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X
PM alarm | 1728 | 6 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X
PM alarm | 1728 | 7 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 0 | 301733 | 04 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 1 | 301733 | 04 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 2 | 301733 | 04 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 3 | 301733 | 04 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 4 | 301733 | 04 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 5 | 301733 | 04 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 6 | 301733 | 04 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 7 | 301733 | 04 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 8 | 301733 | 04 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 9 | 301733 | 04 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 10 | 301733 | 04 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 11 | 301733 | 04 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 12 | 301733 | 04 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 13 | 301733 | 04 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 14 | 301733 | 04 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1732 | 15 | 301733 | 04 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 0 | 301734 | 04 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 1 | 301734 | 04 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 2 | 301734 | 04 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 3 | 301734 | 04 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 4 | 301734 | 04 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 5 | 301734 | 04 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 6 | 301734 | 04 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 7 | 301734 | 04 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 8 | 301734 | 04 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 9 | 301734 | 04 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 10 | 301734 | 04 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 11 | 301734 | 04 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 12 | 301734 | 04 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 13 | 301734 | 04 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 14 | 301734 | 04 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1733 | 15 | 301734 | 04 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 0 | 301735 | 04 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 1 | 301735 | 04 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 2 | 301735 | 04 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 3 | 301735 | 04 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 4 | 301735 | 04 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 5 | 301735 | 04 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 6 | 301735 | 04 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1734 | 7 | 301735 | 04 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 0 | 301736 | 04 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 1 | 301736 | 04 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 2 | 301736 | 04 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 3 | 301736 | 04 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 4 | 301736 | 04 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 5 | 301736 | 04 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 6 | 301736 | 04 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 7 | 301736 | 04 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 8 | 301736 | 04 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 9 | 301736 | 04 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 10 | 301736 | 04 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 11 | 301736 | 04 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 12 | 301736 | 04 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 13 | 301736 | 04 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 14 | 301736 | 04 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1735 | 15 | 301736 | 04 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 0 | 301737 | 04 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 1 | 301737 | 04 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 2 | 301737 | 04 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 3 | 301737 | 04 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 4 | 301737 | 04 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 5 | 301737 | 04 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 6 | 301737 | 04 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 7 | 301737 | 04 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 8 | 301737 | 04 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 9 | 301737 | 04 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 10 | 301737 | 04 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 11 | 301737 | 04 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 12 | 301737 | 04 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 13 | 301737 | 04 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 14 | 301737 | 04 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1736 | 15 | 301737 | 04 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 0 | 301738 | 04 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 1 | 301738 | 04 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 2 | 301738 | 04 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 3 | 301738 | 04 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 4 | 301738 | 04 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 5 | 301738 | 04 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 6 | 301738 | 04 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1737 | 7 | 301738 | 04 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 0 | 301739 | 04 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 1 | 301739 | 04 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 2 | 301739 | 04 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 3 | 301739 | 04 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 4 | 301739 | 04 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 5 | 301739 | 04 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 6 | 301739 | 04 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1738 | 7 | 301739 | 04 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 0 | 301740 | 04 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 1 | 301740 | 04 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 2 | 301740 | 04 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 3 | 301740 | 04 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 4 | 301740 | 04 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 5 | 301740 | 04 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 6 | 301740 | 04 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 7 | 301740 | 04 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 8 | 301740 | 04 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 9 | 301740 | 04 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 10 | 301740 | 04 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 11 | 301740 | 04 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 12 | 301740 | 04 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 13 | 301740 | 04 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 14 | 301740 | 04 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1739 | 15 | 301740 | 04 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 0 | 301741 | 04 |  | Hz/V present, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 1 | 301741 | 04 |  | Hz/V present, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 2 | 301741 | 04 |  | Hz/V present, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 3 | 301741 | 04 |  | Hz/V present, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 4 | 301741 | 04 |  | Hz/V present, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 5 | 301741 | 04 |  | Hz/V present, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 6 | 301741 | 04 |  | Hz/V present, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 7 | 301741 | 04 |  | Hz/V present, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 8 | 301741 | 04 |  | Hz/V present, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 9 | 301741 | 04 |  | Hz/V present, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 10 | 301741 | 04 |  | Hz/V present, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 11 | 301741 | 04 |  | Hz/V present, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 12 | 301741 | 04 |  | Hz/V present, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 13 | 301741 | 04 |  | Hz/V present, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 14 | 301741 | 04 |  | Hz/V present, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1740 | 15 | 301741 | 04 |  | Hz/V present, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 0 | 301742 | 04 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 1 | 301742 | 04 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 2 | 301742 | 04 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 3 | 301742 | 04 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 4 | 301742 | 04 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 5 | 301742 | 04 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 6 | 301742 | 04 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1741 | 7 | 301742 | 04 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 0 | 301744 | 04 |  | Redundant backup present ID1 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 1 | 301744 | 04 |  | Redundant backup present ID2 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 2 | 301744 | 04 |  | Redundant backup present ID3 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 3 | 301744 | 04 |  | Redundant backup present ID4 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 4 | 301744 | 04 |  | Redundant backup present ID5 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 5 | 301744 | 04 |  | Redundant backup present ID6 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 6 | 301744 | 04 |  | Redundant backup present ID7 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 7 | 301744 | 04 |  | Redundant backup present ID8 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 8 | 301744 | 04 |  | Redundant backup present ID9 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 9 | 301744 | 04 |  | Redundant backup present ID10 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 10 | 301744 | 04 |  | Redundant backup present ID11 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 11 | 301744 | 04 |  | Redundant backup present ID12 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 12 | 301744 | 04 |  | Redundant backup present ID13 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 13 | 301744 | 04 |  | Redundant backup present ID14 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 14 | 301744 | 04 |  | Redundant backup present ID15 | BOOL |  |  |  | X
PM Plant logic state | 1743 | 15 | 301744 | 04 |  | Redundant backup present ID16 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 0 | 301747 | 04 |  | Controller B active on ID1 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 1 | 301747 | 04 |  | Controller B active on ID2 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 2 | 301747 | 04 |  | Controller B active on ID3 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 3 | 301747 | 04 |  | Controller B active on ID4 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 4 | 301747 | 04 |  | Controller B active on ID5 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 5 | 301747 | 04 |  | Controller B active on ID6 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 6 | 301747 | 04 |  | Controller B active on ID7 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 7 | 301747 | 04 |  | Controller B active on ID8 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 8 | 301747 | 04 |  | Controller B active on ID9 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 9 | 301747 | 04 |  | Controller B active on ID10 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 10 | 301747 | 04 |  | Controller B active on ID11 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 11 | 301747 | 04 |  | Controller B active on ID12 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 12 | 301747 | 04 |  | Controller B active on ID13 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 13 | 301747 | 04 |  | Controller B active on ID14 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 14 | 301747 | 04 |  | Controller B active on ID15 | BOOL |  |  |  | X
PM Plant logic state | 1746 | 15 | 301747 | 04 |  | Controller B active on ID16 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 0 | 301748 | 04 |  | Controller B active on ID17 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 1 | 301748 | 04 |  | Controller B active on ID18 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 2 | 301748 | 04 |  | Controller B active on ID19 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 3 | 301748 | 04 |  | Controller B active on ID20 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 4 | 301748 | 04 |  | Controller B active on ID21 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 5 | 301748 | 04 |  | Controller B active on ID22 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 6 | 301748 | 04 |  | Controller B active on ID23 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 7 | 301748 | 04 |  | Controller B active on ID24 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 8 | 301748 | 04 |  | Controller B active on ID25 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 9 | 301748 | 04 |  | Controller B active on ID26 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 10 | 301748 | 04 |  | Controller B active on ID27 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 11 | 301748 | 04 |  | Controller B active on ID28 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 12 | 301748 | 04 |  | Controller B active on ID29 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 13 | 301748 | 04 |  | Controller B active on ID30 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 14 | 301748 | 04 |  | Controller B active on ID31 | BOOL |  |  |  | X
PM Plant logic state | 1747 | 15 | 301748 | 04 |  | Controller B active on ID32 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 0 | 301749 | 04 |  | Controller B active on ID33 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 1 | 301749 | 04 |  | Controller B active on ID34 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 2 | 301749 | 04 |  | Controller B active on ID35 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 3 | 301749 | 04 |  | Controller B active on ID36 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 4 | 301749 | 04 |  | Controller B active on ID37 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 5 | 301749 | 04 |  | Controller B active on ID38 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 6 | 301749 | 04 |  | Controller B active on ID39 | BOOL |  |  |  | X
PM Plant logic state | 1748 | 7 | 301749 | 04 |  | Controller B active on ID40 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 0 | 301750 | 04 |  | Dry Mode active on ID1 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 1 | 301750 | 04 |  | Dry Mode active on ID2 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 2 | 301750 | 04 |  | Dry Mode active on ID3 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 3 | 301750 | 04 |  | Dry Mode active on ID4 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 4 | 301750 | 04 |  | Dry Mode active on ID5 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 5 | 301750 | 04 |  | Dry Mode active on ID6 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 6 | 301750 | 04 |  | Dry Mode active on ID7 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 7 | 301750 | 04 |  | Dry Mode active on ID8 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 8 | 301750 | 04 |  | Dry Mode active on ID9 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 9 | 301750 | 04 |  | Dry Mode active on ID10 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 10 | 301750 | 04 |  | Dry Mode active on ID11 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 11 | 301750 | 04 |  | Dry Mode active on ID12 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 12 | 301750 | 04 |  | Dry Mode active on ID13 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 13 | 301750 | 04 |  | Dry Mode active on ID14 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 14 | 301750 | 04 |  | Dry Mode active on ID15 | BOOL |  |  |  | X
PM Plant logic state | 1749 | 15 | 301750 | 04 |  | Dry Mode active on ID16 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 0 | 301751 | 04 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 1 | 301751 | 04 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 2 | 301751 | 04 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 3 | 301751 | 04 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 4 | 301751 | 04 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 5 | 301751 | 04 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 6 | 301751 | 04 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 7 | 301751 | 04 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 8 | 301751 | 04 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 9 | 301751 | 04 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 10 | 301751 | 04 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 11 | 301751 | 04 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 12 | 301751 | 04 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 13 | 301751 | 04 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 14 | 301751 | 04 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1750 | 15 | 301751 | 04 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 0 | 301752 | 04 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 1 | 301752 | 04 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 2 | 301752 | 04 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 3 | 301752 | 04 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 4 | 301752 | 04 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 5 | 301752 | 04 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 6 | 301752 | 04 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 7 | 301752 | 04 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 8 | 301752 | 04 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 9 | 301752 | 04 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 10 | 301752 | 04 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 11 | 301752 | 04 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 12 | 301752 | 04 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 13 | 301752 | 04 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 14 | 301752 | 04 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1751 | 15 | 301752 | 04 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 0 | 301753 | 04 |  | GB synchronising, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 1 | 301753 | 04 |  | GB synchronising, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 2 | 301753 | 04 |  | GB synchronising, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 3 | 301753 | 04 |  | GB synchronising, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 4 | 301753 | 04 |  | GB synchronising, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 5 | 301753 | 04 |  | GB synchronising, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 6 | 301753 | 04 |  | GB synchronising, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 7 | 301753 | 04 |  | GB synchronising, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 8 | 301753 | 04 |  | GB synchronising, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 9 | 301753 | 04 |  | GB synchronising, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 10 | 301753 | 04 |  | GB synchronising, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 11 | 301753 | 04 |  | GB synchronising, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 12 | 301753 | 04 |  | GB synchronising, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 13 | 301753 | 04 |  | GB synchronising, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 14 | 301753 | 04 |  | GB synchronising, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1752 | 15 | 301753 | 04 |  | GB synchronising, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 0 | 301754 | 04 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 1 | 301754 | 04 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 2 | 301754 | 04 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 3 | 301754 | 04 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 4 | 301754 | 04 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 5 | 301754 | 04 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 6 | 301754 | 04 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 7 | 301754 | 04 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 8 | 301754 | 04 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 9 | 301754 | 04 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 10 | 301754 | 04 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 11 | 301754 | 04 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 12 | 301754 | 04 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 13 | 301754 | 04 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 14 | 301754 | 04 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1753 | 15 | 301754 | 04 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 0 | 301755 | 04 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 1 | 301755 | 04 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 2 | 301755 | 04 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 3 | 301755 | 04 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 4 | 301755 | 04 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 5 | 301755 | 04 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 6 | 301755 | 04 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 7 | 301755 | 04 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 8 | 301755 | 04 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 9 | 301755 | 04 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 10 | 301755 | 04 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 11 | 301755 | 04 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 12 | 301755 | 04 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 13 | 301755 | 04 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 14 | 301755 | 04 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1754 | 15 | 301755 | 04 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 0 | 301756 | 04 |  | Running, ID 17 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 1 | 301756 | 04 |  | Running, ID 18 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 2 | 301756 | 04 |  | Running, ID 19 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 3 | 301756 | 04 |  | Running, ID 20 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 4 | 301756 | 04 |  | Running, ID 21 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 5 | 301756 | 04 |  | Running, ID 22 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 6 | 301756 | 04 |  | Running, ID 23 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 7 | 301756 | 04 |  | Running, ID 24 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 8 | 301756 | 04 |  | Running, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 9 | 301756 | 04 |  | Running, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 10 | 301756 | 04 |  | Running, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 11 | 301756 | 04 |  | Running, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 12 | 301756 | 04 |  | Running, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 13 | 301756 | 04 |  | Running, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 14 | 301756 | 04 |  | Running, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1755 | 15 | 301756 | 04 |  | Running, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 0 | 301757 | 04 |  | Dry Mode active on ID17 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 1 | 301757 | 04 |  | Dry Mode active on ID18 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 2 | 301757 | 04 |  | Dry Mode active on ID19 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 3 | 301757 | 04 |  | Dry Mode active on ID20 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 4 | 301757 | 04 |  | Dry Mode active on ID21 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 5 | 301757 | 04 |  | Dry Mode active on ID22 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 6 | 301757 | 04 |  | Dry Mode active on ID23 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 7 | 301757 | 04 |  | Dry Mode active on ID24 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 8 | 301757 | 04 |  | Dry Mode active on ID25 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 9 | 301757 | 04 |  | Dry Mode active on ID26 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 10 | 301757 | 04 |  | Dry Mode active on ID27 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 11 | 301757 | 04 |  | Dry Mode active on ID28 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 12 | 301757 | 04 |  | Dry Mode active on ID29 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 13 | 301757 | 04 |  | Dry Mode active on ID30 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 14 | 301757 | 04 |  | Dry Mode active on ID31 | BOOL |  |  |  | X
PM Plant logic state | 1756 | 15 | 301757 | 04 |  | Dry Mode active on ID32 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 0 | 301758 | 04 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 1 | 301758 | 04 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 2 | 301758 | 04 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 3 | 301758 | 04 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 4 | 301758 | 04 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 5 | 301758 | 04 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 6 | 301758 | 04 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 7 | 301758 | 04 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 8 | 301758 | 04 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 9 | 301758 | 04 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 10 | 301758 | 04 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 11 | 301758 | 04 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 12 | 301758 | 04 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 13 | 301758 | 04 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 14 | 301758 | 04 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1757 | 15 | 301758 | 04 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 0 | 301759 | 04 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 1 | 301759 | 04 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 2 | 301759 | 04 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 3 | 301759 | 04 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 4 | 301759 | 04 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 5 | 301759 | 04 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 6 | 301759 | 04 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 7 | 301759 | 04 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 8 | 301759 | 04 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 9 | 301759 | 04 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 10 | 301759 | 04 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 11 | 301759 | 04 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 12 | 301759 | 04 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 13 | 301759 | 04 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 14 | 301759 | 04 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1758 | 15 | 301759 | 04 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 0 | 301760 | 04 |  | MB synchronising, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 1 | 301760 | 04 |  | MB synchronising, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 2 | 301760 | 04 |  | MB synchronising, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 3 | 301760 | 04 |  | MB synchronising, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 4 | 301760 | 04 |  | MB synchronising, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 5 | 301760 | 04 |  | MB synchronising, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 6 | 301760 | 04 |  | MB synchronising, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 7 | 301760 | 04 |  | MB synchronising, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 8 | 301760 | 04 |  | MB synchronising, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 9 | 301760 | 04 |  | MB synchronising, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 10 | 301760 | 04 |  | MB synchronising, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 11 | 301760 | 04 |  | MB synchronising, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 12 | 301760 | 04 |  | MB synchronising, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 13 | 301760 | 04 |  | MB synchronising, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 14 | 301760 | 04 |  | MB synchronising, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1759 | 15 | 301760 | 04 |  | MB synchronising, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 0 | 301761 | 04 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 1 | 301761 | 04 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 2 | 301761 | 04 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 3 | 301761 | 04 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 4 | 301761 | 04 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 5 | 301761 | 04 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 6 | 301761 | 04 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 7 | 301761 | 04 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 8 | 301761 | 04 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 9 | 301761 | 04 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 10 | 301761 | 04 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 11 | 301761 | 04 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 12 | 301761 | 04 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 13 | 301761 | 04 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 14 | 301761 | 04 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1760 | 15 | 301761 | 04 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 0 | 301762 | 04 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 1 | 301762 | 04 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 2 | 301762 | 04 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 3 | 301762 | 04 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 4 | 301762 | 04 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 5 | 301762 | 04 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 6 | 301762 | 04 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 7 | 301762 | 04 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 8 | 301762 | 04 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 9 | 301762 | 04 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 10 | 301762 | 04 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 11 | 301762 | 04 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 12 | 301762 | 04 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 13 | 301762 | 04 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 14 | 301762 | 04 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1761 | 15 | 301762 | 04 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 0 | 301763 | 04 |  | TB synchronising, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 1 | 301763 | 04 |  | TB synchronising, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 2 | 301763 | 04 |  | TB synchronising, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 3 | 301763 | 04 |  | TB synchronising, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 4 | 301763 | 04 |  | TB synchronising, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 5 | 301763 | 04 |  | TB synchronising, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 6 | 301763 | 04 |  | TB synchronising, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 7 | 301763 | 04 |  | TB synchronising, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 8 | 301763 | 04 |  | TB synchronising, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 9 | 301763 | 04 |  | TB synchronising, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 10 | 301763 | 04 |  | TB synchronising, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 11 | 301763 | 04 |  | TB synchronising, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 12 | 301763 | 04 |  | TB synchronising, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 13 | 301763 | 04 |  | TB synchronising, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 14 | 301763 | 04 |  | TB synchronising, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1762 | 15 | 301763 | 04 |  | TB synchronising, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 0 | 301764 | 04 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 1 | 301764 | 04 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 2 | 301764 | 04 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 3 | 301764 | 04 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 4 | 301764 | 04 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 5 | 301764 | 04 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 6 | 301764 | 04 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 7 | 301764 | 04 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 8 | 301764 | 04 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 9 | 301764 | 04 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 10 | 301764 | 04 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 11 | 301764 | 04 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 12 | 301764 | 04 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 13 | 301764 | 04 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 14 | 301764 | 04 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1763 | 15 | 301764 | 04 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 0 | 301765 | 04 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 1 | 301765 | 04 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 2 | 301765 | 04 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 3 | 301765 | 04 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 4 | 301765 | 04 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 5 | 301765 | 04 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 6 | 301765 | 04 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 7 | 301765 | 04 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 8 | 301765 | 04 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 9 | 301765 | 04 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 10 | 301765 | 04 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 11 | 301765 | 04 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 12 | 301765 | 04 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 13 | 301765 | 04 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 14 | 301765 | 04 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1764 | 15 | 301765 | 04 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 0 | 301766 | 04 |  | Mains OK, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 1 | 301766 | 04 |  | Mains OK, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 2 | 301766 | 04 |  | Mains OK, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 3 | 301766 | 04 |  | Mains OK, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 4 | 301766 | 04 |  | Mains OK, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 5 | 301766 | 04 |  | Mains OK, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 6 | 301766 | 04 |  | Mains OK, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 7 | 301766 | 04 |  | Mains OK, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 8 | 301766 | 04 |  | Mains OK, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 9 | 301766 | 04 |  | Mains OK, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 10 | 301766 | 04 |  | Mains OK, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 11 | 301766 | 04 |  | Mains OK, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 12 | 301766 | 04 |  | Mains OK, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 13 | 301766 | 04 |  | Mains OK, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 14 | 301766 | 04 |  | Mains OK, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1765 | 15 | 301766 | 04 |  | Mains OK, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 0 | 301767 | 04 |  | Mains not in semi 1 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 1 | 301767 | 04 |  | Mains not in semi 2 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 2 | 301767 | 04 |  | Mains not in semi 3 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 3 | 301767 | 04 |  | Mains not in semi 4 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 4 | 301767 | 04 |  | Mains not in semi 5 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 5 | 301767 | 04 |  | Mains not in semi 6 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 6 | 301767 | 04 |  | Mains not in semi 7 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 7 | 301767 | 04 |  | Mains not in semi 8 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 8 | 301767 | 04 |  | Mains not in semi 9 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 9 | 301767 | 04 |  | Mains not in semi 10 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 10 | 301767 | 04 |  | Mains not in semi 11 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 11 | 301767 | 04 |  | Mains not in semi 12 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 12 | 301767 | 04 |  | Mains not in semi 13 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 13 | 301767 | 04 |  | Mains not in semi 14 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 14 | 301767 | 04 |  | Mains not in semi 15 | BOOL |  |  |  | X
PM Plant logic state | 1766 | 15 | 301767 | 04 |  | Mains not in semi 16 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 0 | 301768 | 04 |  | Mains failure, ID 1 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 1 | 301768 | 04 |  | Mains failure, ID 2 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 2 | 301768 | 04 |  | Mains failure, ID 3 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 3 | 301768 | 04 |  | Mains failure, ID 4 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 4 | 301768 | 04 |  | Mains failure, ID 5 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 5 | 301768 | 04 |  | Mains failure, ID 6 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 6 | 301768 | 04 |  | Mains failure, ID 7 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 7 | 301768 | 04 |  | Mains failure, ID 8 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 8 | 301768 | 04 |  | Mains failure, ID 9 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 9 | 301768 | 04 |  | Mains failure, ID 10 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 10 | 301768 | 04 |  | Mains failure, ID 11 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 11 | 301768 | 04 |  | Mains failure, ID 12 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 12 | 301768 | 04 |  | Mains failure, ID 13 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 13 | 301768 | 04 |  | Mains failure, ID 14 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 14 | 301768 | 04 |  | Mains failure, ID 15 | BOOL |  |  |  | X
PM Plant logic state | 1767 | 15 | 301768 | 04 |  | Mains failure, ID 16 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 0 | 301770 | 04 |  | PV breaker OFF, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 1 | 301770 | 04 |  | PV breaker OFF, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 2 | 301770 | 04 |  | PV breaker OFF, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 3 | 301770 | 04 |  | PV breaker OFF, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 4 | 301770 | 04 |  | PV breaker OFF, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 5 | 301770 | 04 |  | PV breaker OFF, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 6 | 301770 | 04 |  | PV breaker OFF, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1769 | 7 | 301770 | 04 |  | PV breaker OFF, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 0 | 301771 | 04 |  | Breaker synchronising, PV ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 1 | 301771 | 04 |  | Breaker synchronising, PV ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 2 | 301771 | 04 |  | Breaker synchronising, PV ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 3 | 301771 | 04 |  | Breaker synchronising, PV ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 4 | 301771 | 04 |  | Breaker synchronising, PV ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 5 | 301771 | 04 |  | Breaker synchronising, PV ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 6 | 301771 | 04 |  | Breaker synchronising, PV ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1770 | 7 | 301771 | 04 |  | Breaker synchronising, PV ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 0 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 1 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 2 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 3 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 4 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 5 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 6 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 7 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 8 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 9 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 10 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 11 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 12 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 13 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 14 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1771 | 15 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 0 | 301773 | 04 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 1 | 301773 | 04 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 2 | 301773 | 04 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 3 | 301773 | 04 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 4 | 301773 | 04 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 5 | 301773 | 04 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 6 | 301773 | 04 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 7 | 301773 | 04 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 8 | 301773 | 04 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 9 | 301773 | 04 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 10 | 301773 | 04 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 11 | 301773 | 04 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 12 | 301773 | 04 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 13 | 301773 | 04 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 14 | 301773 | 04 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1772 | 15 | 301773 | 04 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 0 | 301774 | 04 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 1 | 301774 | 04 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 2 | 301774 | 04 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 3 | 301774 | 04 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 4 | 301774 | 04 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 5 | 301774 | 04 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 6 | 301774 | 04 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 7 | 301774 | 04 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 8 | 301774 | 04 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 9 | 301774 | 04 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 10 | 301774 | 04 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 11 | 301774 | 04 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 12 | 301774 | 04 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 13 | 301774 | 04 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 14 | 301774 | 04 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1773 | 15 | 301774 | 04 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 0 | 301775 | 04 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 1 | 301775 | 04 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 2 | 301775 | 04 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 3 | 301775 | 04 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 4 | 301775 | 04 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 5 | 301775 | 04 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 6 | 301775 | 04 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 7 | 301775 | 04 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 8 | 301775 | 04 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 9 | 301775 | 04 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 10 | 301775 | 04 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 11 | 301775 | 04 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 12 | 301775 | 04 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 13 | 301775 | 04 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 14 | 301775 | 04 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1774 | 15 | 301775 | 04 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 0 | 301776 | 04 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 1 | 301776 | 04 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 2 | 301776 | 04 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 3 | 301776 | 04 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 4 | 301776 | 04 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 5 | 301776 | 04 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 6 | 301776 | 04 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 7 | 301776 | 04 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 8 | 301776 | 04 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 9 | 301776 | 04 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 10 | 301776 | 04 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 11 | 301776 | 04 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 12 | 301776 | 04 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 13 | 301776 | 04 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 14 | 301776 | 04 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1775 | 15 | 301776 | 04 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 0 | 301777 | 04 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 1 | 301777 | 04 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 2 | 301777 | 04 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 3 | 301777 | 04 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 4 | 301777 | 04 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 5 | 301777 | 04 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 6 | 301777 | 04 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 7 | 301777 | 04 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 8 | 301777 | 04 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 9 | 301777 | 04 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 10 | 301777 | 04 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 11 | 301777 | 04 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 12 | 301777 | 04 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 13 | 301777 | 04 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 14 | 301777 | 04 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1776 | 15 | 301777 | 04 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 0 | 301778 | 04 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 1 | 301778 | 04 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 2 | 301778 | 04 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 3 | 301778 | 04 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 4 | 301778 | 04 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 5 | 301778 | 04 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 6 | 301778 | 04 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 7 | 301778 | 04 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 8 | 301778 | 04 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 9 | 301778 | 04 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 10 | 301778 | 04 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 11 | 301778 | 04 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 12 | 301778 | 04 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 13 | 301778 | 04 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 14 | 301778 | 04 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1777 | 15 | 301778 | 04 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 0 | 301779 | 04 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 1 | 301779 | 04 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 2 | 301779 | 04 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 3 | 301779 | 04 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 4 | 301779 | 04 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 5 | 301779 | 04 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 6 | 301779 | 04 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 7 | 301779 | 04 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 8 | 301779 | 04 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 9 | 301779 | 04 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 10 | 301779 | 04 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 11 | 301779 | 04 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 12 | 301779 | 04 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 13 | 301779 | 04 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 14 | 301779 | 04 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1778 | 15 | 301779 | 04 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 0 | 301780 | 04 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 1 | 301780 | 04 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 2 | 301780 | 04 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 3 | 301780 | 04 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 4 | 301780 | 04 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 5 | 301780 | 04 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 6 | 301780 | 04 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 7 | 301780 | 04 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 8 | 301780 | 04 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 9 | 301780 | 04 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 10 | 301780 | 04 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 11 | 301780 | 04 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 12 | 301780 | 04 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 13 | 301780 | 04 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 14 | 301780 | 04 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1779 | 15 | 301780 | 04 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 0 | 301781 | 04 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 1 | 301781 | 04 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 2 | 301781 | 04 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 3 | 301781 | 04 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 4 | 301781 | 04 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 5 | 301781 | 04 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 6 | 301781 | 04 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 7 | 301781 | 04 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 8 | 301781 | 04 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 9 | 301781 | 04 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 10 | 301781 | 04 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 11 | 301781 | 04 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 12 | 301781 | 04 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 13 | 301781 | 04 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 14 | 301781 | 04 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1780 | 15 | 301781 | 04 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 0 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 1 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 2 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 3 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 4 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 5 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 6 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 7 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 8 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 9 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 10 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 11 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 12 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 13 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 14 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1781 | 15 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 0 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 1 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 2 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 3 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 4 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 5 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 6 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 7 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 8 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 9 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 10 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 11 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 12 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 13 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 14 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1782 | 15 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 0 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 1 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 2 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 3 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 4 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 5 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 6 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 7 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 8 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 9 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 10 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 11 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 12 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 13 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 14 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1783 | 15 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 0 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 1 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 2 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 3 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 4 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 5 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 6 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 7 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 8 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 9 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 10 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 11 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 12 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 13 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 14 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1784 | 15 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 0 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 1 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 2 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 3 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 4 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 5 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 6 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 7 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 8 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 9 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 10 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 11 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 12 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 13 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 14 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1785 | 15 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 0 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 1 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 2 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 3 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 4 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 5 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 6 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 7 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 8 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 9 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 10 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 11 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 12 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 13 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 14 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1786 | 15 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 0 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 1 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 2 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 3 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 4 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 5 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 6 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 7 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 8 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 9 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 10 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 11 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 12 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 13 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 14 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1787 | 15 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 0 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 1 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 2 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 3 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 4 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 5 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 6 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 7 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 8 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 9 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 10 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 11 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 12 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 13 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 14 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1788 | 15 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 0 | 301790 | 04 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 1 | 301790 | 04 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 2 | 301790 | 04 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 3 | 301790 | 04 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 4 | 301790 | 04 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 5 | 301790 | 04 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 6 | 301790 | 04 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 7 | 301790 | 04 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 8 | 301790 | 04 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 9 | 301790 | 04 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 10 | 301790 | 04 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 11 | 301790 | 04 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 12 | 301790 | 04 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 13 | 301790 | 04 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 14 | 301790 | 04 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1789 | 15 | 301790 | 04 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 0 | 301791 | 04 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 1 | 301791 | 04 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 2 | 301791 | 04 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 3 | 301791 | 04 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 4 | 301791 | 04 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 5 | 301791 | 04 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 6 | 301791 | 04 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 7 | 301791 | 04 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 8 | 301791 | 04 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 9 | 301791 | 04 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 10 | 301791 | 04 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 11 | 301791 | 04 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 12 | 301791 | 04 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 13 | 301791 | 04 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 14 | 301791 | 04 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1790 | 15 | 301791 | 04 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 0 | 301792 | 04 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 1 | 301792 | 04 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 2 | 301792 | 04 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 3 | 301792 | 04 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 4 | 301792 | 04 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 5 | 301792 | 04 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 6 | 301792 | 04 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 7 | 301792 | 04 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 8 | 301792 | 04 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 9 | 301792 | 04 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 10 | 301792 | 04 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 11 | 301792 | 04 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 12 | 301792 | 04 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 13 | 301792 | 04 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 14 | 301792 | 04 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1791 | 15 | 301792 | 04 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 0 | 301793 | 04 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 1 | 301793 | 04 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 2 | 301793 | 04 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 3 | 301793 | 04 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 4 | 301793 | 04 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 5 | 301793 | 04 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 6 | 301793 | 04 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 7 | 301793 | 04 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 8 | 301793 | 04 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 9 | 301793 | 04 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 10 | 301793 | 04 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 11 | 301793 | 04 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 12 | 301793 | 04 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 13 | 301793 | 04 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 14 | 301793 | 04 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1792 | 15 | 301793 | 04 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 0 | 301794 | 04 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 1 | 301794 | 04 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 2 | 301794 | 04 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 3 | 301794 | 04 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 4 | 301794 | 04 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 5 | 301794 | 04 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 6 | 301794 | 04 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 7 | 301794 | 04 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 8 | 301794 | 04 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 9 | 301794 | 04 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 10 | 301794 | 04 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 11 | 301794 | 04 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 12 | 301794 | 04 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 13 | 301794 | 04 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 14 | 301794 | 04 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1793 | 15 | 301794 | 04 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 0 | 301795 | 04 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 1 | 301795 | 04 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 2 | 301795 | 04 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 3 | 301795 | 04 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 4 | 301795 | 04 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 5 | 301795 | 04 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 6 | 301795 | 04 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 7 | 301795 | 04 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 8 | 301795 | 04 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 9 | 301795 | 04 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 10 | 301795 | 04 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 11 | 301795 | 04 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 12 | 301795 | 04 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 13 | 301795 | 04 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 14 | 301795 | 04 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1794 | 15 | 301795 | 04 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 0 | 301796 | 04 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 1 | 301796 | 04 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 2 | 301796 | 04 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 3 | 301796 | 04 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 4 | 301796 | 04 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 5 | 301796 | 04 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 6 | 301796 | 04 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 7 | 301796 | 04 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 8 | 301796 | 04 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 9 | 301796 | 04 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 10 | 301796 | 04 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 11 | 301796 | 04 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 12 | 301796 | 04 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 13 | 301796 | 04 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 14 | 301796 | 04 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1795 | 15 | 301796 | 04 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 0 | 301797 | 04 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 1 | 301797 | 04 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 2 | 301797 | 04 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 3 | 301797 | 04 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 4 | 301797 | 04 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 5 | 301797 | 04 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 6 | 301797 | 04 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 7 | 301797 | 04 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 8 | 301797 | 04 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 9 | 301797 | 04 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 10 | 301797 | 04 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 11 | 301797 | 04 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 12 | 301797 | 04 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 13 | 301797 | 04 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 14 | 301797 | 04 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X
PM Plant logic state | 1796 | 15 | 301797 | 04 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X