## Descriptions
GPU Modbus descriptions
Software version
The information contained in these tables are applicable to software version 1.0.1 of the GPU 300 product.
Row | Hyperlink index
14 | Modbus function codes
25 | Discrete output coil
38 | Discrete input contact
55 | Output holding register
70 | Input register
81 | List of alarm states
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value(s) to multiple consecutive discrete output coils.
| 16 | Write a value(s) to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
| Alarm parameter: Enable | Read or change the alarm enable configuration. Read: The controller returns 0 (false) when the alarm is Not enabled and 1 (true) when the alarm is Enabled. Write: The controller changes the alarm configuration. Danger! You can disable critical controller protections. Only disable alarms if you have a thorough understanding of the system, the controller, and the consequences of disabling an alarm.
| Alarm parameter: Latch | Read or change the alarm latch configuration. Read: The controller returns 0 (false) when the latch is Not enabled and 1 (true) when the latch parameter is Enabled. Write: The controller changes the alarm latch configuration. Danger! You can disable critical controller protections, and the built-in controller lockout relay function. Only disable alarm latches if you have a thorough understanding of the system, the controller, and the consequences of disabling an alarm latch.
| Alarm action: Acknowledge alarm | Acknowledge the alarm. Read: The controller always returns 0 (false). Write: If the alarm is active and unacknowledged, and you write 1 (true), the controller acknowledges the alarm.
| Alarm action: Reset latch | Reset the alarm latch. Read: The controller always returns 0 (false). Write: If the alarm is latched, acknowledged and the operating value does not exceed the set point, and you write 1 (true), the controller resets the latch.
| General parameter: Enable | Read or change the parameter configuration. Read: The controller returns 0 (false) when the parameter is Not enabled and 1 (true) when the parameter is Enabled. Write: The controller changes the parameter configuration.
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Alarm status: Active | Read whether an alarm is activated. The controller returns 0 (false) when the alarm is not activated (state 0, 3, 6 or 7). The controller returns 1 (true) when the alarm is activated (state 1, 2, 4 or 5).
The alarm states are described in row 81.
| Alarm status: Acknowledged | Read whether an alarm is acknowledged. The controller returns 0 (false) when the alarm is not acknowledged (state 0, 1, 3, 4, 6 or 7). The controller returns 1 (true) when the alarm is acknowledged (state 2 or 5).
The alarm states are described in row 81.
| Alarm status: Latched | Read whether an alarm is latched. The controller returns 0 (false) when the alarm has a state other than latched (state 0, 1, 2, 3, 6 or 7). The controller returns 1 (true) when the alarm is latched (state 4 or 5).
The alarm states are described in row 81.
| Alarm status: Shelved | Read whether an alarm is shelved. The controller returns 0 (false) when the alarm is not shelved (state 0, 1, 2, 3, 4, 5 or 7). The controller returns 1 (true) when the alarm is shelved (state 6).
The alarm states are described in row 81.
| Alarm status: Delay timer running | Read whether an alarm delay timer is running. The controller returns 0 (false) if the alarm delay timer is not running. The controller returns 1 (true) if the operating value exceeds the alarm set point and the alarm delay timer is running.
| Alarm status: Delay timer expired | Read whether an alarm delay timer is expired. The controller returns 0 (false) when the alarm delay timer has not expired, or if the operating value does not exceed the alarm set point. The controller returns 1 (true) if the operating value exceeds the alarm set point and the alarm delay timer has expired.
| General parameter: Delay timer running | Read whether a function delay timer is running. The controller returns 0 (false) if the function delay timer is not running. The controller returns 1 (true) if the function delay timer is running.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Alarm parameter: Set point | Read and write the alarm set point. Read: The controller returns the current set point value. Write: The controller changes the set point of the associated alarm if a valid value is entered.
Only values within the minimum and maximum range of the set point are valid inputs. Refer to the Designer's handbook for alarm descriptions. Danger! You can change critical controller protections. Only adjust alarm set points if you have a thorough understanding of the system, the controller, and the consequences of adjusting an alarm set point.
| Alarm parameter: Reset ratio | Read and write the reset ratio of the alarm. Read: The controller returns the current reset ratio of the alarm. Write: The controller changes the reset ratio of the alarm if a valid value is entered. Only values within the minimum and maximum range of the associated alarm's reset ratio are valid inputs. Refer to the Designer's handbook for alarm descriptions.
| Alarm parameter: Delay | Read and write the delay timer value (in seconds) of the alarm. Read: The controller returns the current delay time of the alarm. Write: The controller changes the delay time of the alarm if a valid value is entered.
Only values within the minimum and maximum range of the alarm's delay time are valid inputs. Refer to the Designer's handbook for alarm descriptions. Danger! You can change critical controller protections. Only adjust a delay if you have a thorough understanding of the system, the controller, and the consequences of adjusting the delay.
| Alarm parameter: Inhibit | Read and write the alarm inhibits. The alarm inhibits stop the controller from activating the alarm. Read: The controller returns a 32-bit number, where each bit corresponds to an alarm inhibit. The inhibit is enabled when its bit is 1, and not enabled when its bit is 0. Write: The controller changes the alarm inhibits.
These bits are allocated to the GPU inhibits: Bit 2 = Generator breaker closed Bit 3 = Generator breaker open Bit 6 = Generator voltage present Bit 7 = Generator voltage not present Bit 8 = Generator frequency present Bit 9 = Generator frequency not present Bit 28 = ACM wire break Bit 29 = Inhibit 1 Bit 30 = Inhibit 2 Bit 31 = Inhibit 3
For example, to enable the Generator breaker open and the Generator voltage not present inhibits for an alarm, write the sum of their values. Bit 3 plus Bit 7 corresponds to 8 + 128 = 136. Danger! You can write other values to the controller, and these will not return an error message. Only the valid inhibits are enabled. Only use combinations of the values listed above.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| [Controlled equipment] ACM measurements | Read the operating value of the AC measurement on the generator side of the breaker.
| [Busbar] ACM measurements | Read the operating value of the AC measurement on the busbar side of the breaker.
| 4th current ACM measurements | Read the operating value of the 4th current AC measurement.
| Alarm status: Operating value | Read the measured value of the alarm. An alarm with an ON/OFF status returns 1 or 0. An alarm with an operating value in a specific range returns the measured value.
| Alarm status: Delay timer elapsed time | Read the time (in seconds) since the delay timer of the alarm started. The controller returns 0 if the alarm operating value is below the set point. The controller returns up to the delay time when the alarm is triggered and the operating value still exceeds the set point.
| Alarm status: Delay timer remaining time | Read the time (in seconds) before the alarm is activated. The controller returns the delay time if the alarm operating value does not exceed the set point. The controller returns 0 when the alarm is activated and the operating value is above the set point.
| Alarm status: Alarm state | Read the alarm state of the alarm. These are the alarm states (decimal values): 0 = The alarm state is normal. 1 = The alarm is unacknowledged. 2 = The alarm is acknowledged. 3 = The alarm state is normal and the alarm is unacknowledged. 4 = The alarm is unacknowledged and latched. 5 = The alarm is acknowledged and latched. 6 = The alarm is shelved. 7 = The alarm is removed from service.
| Alarm status: Alarm active | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated (state 0, 3, 6 or 7 above). The controller returns 1 (true) when the alarm is activated (state 1, 2, 4 or 5 above).
| Alarm status: Alarm acknowledged | Read one bit to see whether an alarm is acknowledged. The controller returns 0 (false) when the alarm is not acknowledged (state 0, 1, 3, 4, 6 or 7 above). The controller returns 1 (true) when the alarm is acknowledged (state 2 or 5 above).
| Alarm status: Alarm latched | Read one bit to see whether an alarm is latched. The controller returns 0 (false) when the alarm has a state other than latched (state 0, 1, 2, 3, 6 or 7 above). The controller returns 1 (true) when the alarm is latched (state 4 or 5 above).
| General parameter: Delay timer elapsed time | Read the time (in seconds) since the delay timer of the function was activated. The controller returns 0 if the timer is not running, and has been reset. The controller returns the delay time when the timer has run out and is not reset.
| General parameter: Delay timer remaining time | Read the time (in seconds) before the function can be activated. The controller returns the delay time if the timer is not running, and is reset. The controller returns 0 if the timer has run out and is not reset.

## Discrete output coil (01;05;15)
Discrete output coil (01; 05; 15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name
Command | 1009 | 1010 | 01; 05; 15 | Activate breaker close
Command | 1010 | 1011 | 01; 05; 15 | Deactivate breaker close
Command | 1011 | 1012 | 01; 05; 15 | Generator breaker close block
Command | 1012 | 1013 | 01; 05; 15 | Reset generator breaker close block
Command | 1017 | 1018 | 01; 05; 15 | Acknowledge all alarms
Command | 1019 | 1020 | 01; 05; 15 | Reset all latches
Command | 1020 | 1021 | 01; 05; 15 | Reset alarm horn
Alarm parameter: Enable | 20020 | 20021 | 01; 05; 15 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm parameter: Enable | 20022 | 20023 | 01; 05; 15 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm parameter: Enable | 20023 | 20024 | 01; 05; 15 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm parameter: Enable | 20032 | 20033 | 01; 05; 15 | Synchronisation > Alarms > Vector mismatch
Alarm parameter: Enable | 20037 | 20038 | 01; 05; 15 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm parameter: Enable | 20038 | 20039 | 01; 05; 15 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm parameter: Enable | 20039 | 20040 | 01; 05; 15 | AC configuration > Generator > Voltage or frequency not OK
Alarm parameter: Enable | 20040 | 20041 | 01; 05; 15 | Generator > Current protections > Zero sequence current
Alarm parameter: Enable | 20041 | 20042 | 01; 05; 15 | Generator > Voltage protections > Zero sequence voltage
Alarm parameter: Enable | 20042 | 20043 | 01; 05; 15 | Generator > Current protections > Negative sequence current
Alarm parameter: Enable | 20043 | 20044 | 01; 05; 15 | Generator > Voltage protections > Negative sequence voltage
Alarm parameter: Enable | 20044 | 20045 | 01; 05; 15 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm parameter: Enable | 20045 | 20046 | 01; 05; 15 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm parameter: Enable | 20046 | 20047 | 01; 05; 15 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm parameter: Enable | 20047 | 20048 | 01; 05; 15 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm parameter: Enable | 20048 | 20049 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 2
Alarm parameter: Enable | 20049 | 20050 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 1
Alarm parameter: Enable | 20050 | 20051 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 2
Alarm parameter: Enable | 20051 | 20052 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 1
Alarm parameter: Enable | 20052 | 20053 | 01; 05; 15 | Generator > Power protections > Reverse power 2
Alarm parameter: Enable | 20053 | 20054 | 01; 05; 15 | Generator > Power protections > Reverse power 1
Alarm parameter: Enable | 20054 | 20055 | 01; 05; 15 | Generator > Power protections > Overload 2
Alarm parameter: Enable | 20055 | 20056 | 01; 05; 15 | Generator > Power protections > Overload 1
Alarm parameter: Enable | 20056 | 20057 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm parameter: Enable | 20057 | 20058 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm parameter: Enable | 20058 | 20059 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm parameter: Enable | 20059 | 20060 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm parameter: Enable | 20060 | 20061 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm parameter: Enable | 20061 | 20062 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm parameter: Enable | 20062 | 20063 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm parameter: Enable | 20063 | 20064 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm parameter: Enable | 20064 | 20065 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm parameter: Enable | 20065 | 20066 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm parameter: Enable | 20066 | 20067 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm parameter: Enable | 20067 | 20068 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm parameter: Enable | 20068 | 20069 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm parameter: Enable | 20069 | 20070 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm parameter: Enable | 20070 | 20071 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm parameter: Enable | 20071 | 20072 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm parameter: Enable | 20072 | 20073 | 01; 05; 15 | Generator > Current protections > Directional over-current 2
Alarm parameter: Enable | 20073 | 20074 | 01; 05; 15 | Generator > Current protections > Directional over-current 1
Alarm parameter: Enable | 20074 | 20075 | 01; 05; 15 | Generator > Current protections > Fast over-current 2
Alarm parameter: Enable | 20075 | 20076 | 01; 05; 15 | Generator > Current protections > Fast over-current 1
Alarm parameter: Enable | 20076 | 20077 | 01; 05; 15 | Generator > Current protections > Over-current 2
Alarm parameter: Enable | 20077 | 20078 | 01; 05; 15 | Generator > Current protections > Over-current 1
Alarm parameter: Enable | 20078 | 20079 | 01; 05; 15 | Generator > Current protections > Inverse time over-current
Alarm parameter: Enable | 20079 | 20080 | 01; 05; 15 | 4th current input > Current protections > Earth inverse time over-current
Alarm parameter: Enable | 20080 | 20081 | 01; 05; 15 | 4th current input > Current protections > Neutral inverse time over-current
Alarm parameter: Enable | 20100 | 20101 | 01; 05; 15 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm parameter: Enable | 20101 | 20102 | 01; 05; 15 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm parameter: Enable | 20102 | 20103 | 01; 05; 15 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm parameter: Enable | 20103 | 20104 | 01; 05; 15 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm parameter: Enable | 20104 | 20105 | 01; 05; 15 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm parameter: Enable | 20105 | 20106 | 01; 05; 15 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm parameter: Enable | 20106 | 20107 | 01; 05; 15 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm parameter: Enable | 20107 | 20108 | 01; 05; 15 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm parameter: Enable | 20119 | 20120 | 01; 05; 15 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm parameter: Enable | 20120 | 20121 | 01; 05; 15 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm parameter: Enable | 20121 | 20122 | 01; 05; 15 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm parameter: Enable | 20122 | 20123 | 01; 05; 15 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm parameter: Enable | 20123 | 20124 | 01; 05; 15 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm parameter: Enable | 20124 | 20125 | 01; 05; 15 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm parameter: Enable | 20125 | 20126 | 01; 05; 15 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm parameter: Enable | 20126 | 20127 | 01; 05; 15 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm parameter: Enable | 20208 | 20209 | 01; 05; 15 | Utility > Network > Ethernet redundancy broken
Alarm parameter: Enable | 20226 | 20227 | 01; 05; 15 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm parameter: Enable | 20227 | 20228 | 01; 05; 15 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm parameter: Enable | 20228 | 20229 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm parameter: Enable | 20229 | 20230 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm parameter: Enable | 20230 | 20231 | 01; 05; 15 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm parameter: Enable | 20231 | 20232 | 01; 05; 15 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm parameter: Enable | 20232 | 20233 | 01; 05; 15 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm parameter: Enable | 20233 | 20234 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm parameter: Enable | 20234 | 20235 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm parameter: Enable | 20235 | 20236 | 01; 05; 15 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm parameter: Enable | 20236 | 20237 | 01; 05; 15 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm parameter: Enable | 20237 | 20238 | 01; 05; 15 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm parameter: Enable | 20238 | 20239 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm parameter: Enable | 20239 | 20240 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm parameter: Enable | 20240 | 20241 | 01; 05; 15 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm parameter: Enable | 20246 | 20247 | 01; 05; 15 | Utility > Network > Modbus communication timeout
Alarm parameter: Enable | 21500 | 21501 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21501 | 21502 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21502 | 21503 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21503 | 21504 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21504 | 21505 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21505 | 21506 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21506 | 21507 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21507 | 21508 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21508 | 21509 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21509 | 21510 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21510 | 21511 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21511 | 21512 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21512 | 21513 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21513 | 21514 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21514 | 21515 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21515 | 21516 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21516 | 21517 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21517 | 21518 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21518 | 21519 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21519 | 21520 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21520 | 21521 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21521 | 21522 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21522 | 21523 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21523 | 21524 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21524 | 21525 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21525 | 21526 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21526 | 21527 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21527 | 21528 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21528 | 21529 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21529 | 21530 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21530 | 21531 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21531 | 21532 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21532 | 21533 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21533 | 21534 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21534 | 21535 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21535 | 21536 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21536 | 21537 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21537 | 21538 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21538 | 21539 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21539 | 21540 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21540 | 21541 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21541 | 21542 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21542 | 21543 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21543 | 21544 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21544 | 21545 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21545 | 21546 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21546 | 21547 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21547 | 21548 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21548 | 21549 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Enable | 21549 | 21550 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 22016 | 22017 | 01; 05; 15 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm parameter: Latch | 22017 | 22018 | 01; 05; 15 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm parameter: Latch | 22018 | 22019 | 01; 05; 15 | Breakers > Generator breaker > Position failure > GB position failure
Alarm parameter: Latch | 22019 | 22020 | 01; 05; 15 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm parameter: Latch | 22020 | 22021 | 01; 05; 15 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm parameter: Latch | 22022 | 22023 | 01; 05; 15 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm parameter: Latch | 22023 | 22024 | 01; 05; 15 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm parameter: Latch | 22032 | 22033 | 01; 05; 15 | Synchronisation > Alarms > Vector mismatch
Alarm parameter: Latch | 22037 | 22038 | 01; 05; 15 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm parameter: Latch | 22038 | 22039 | 01; 05; 15 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm parameter: Latch | 22039 | 22040 | 01; 05; 15 | AC configuration > Generator > Voltage or frequency not OK
Alarm parameter: Latch | 22040 | 22041 | 01; 05; 15 | Generator > Current protections > Zero sequence current
Alarm parameter: Latch | 22041 | 22042 | 01; 05; 15 | Generator > Voltage protections > Zero sequence voltage
Alarm parameter: Latch | 22042 | 22043 | 01; 05; 15 | Generator > Current protections > Negative sequence current
Alarm parameter: Latch | 22043 | 22044 | 01; 05; 15 | Generator > Voltage protections > Negative sequence voltage
Alarm parameter: Latch | 22044 | 22045 | 01; 05; 15 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm parameter: Latch | 22045 | 22046 | 01; 05; 15 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm parameter: Latch | 22046 | 22047 | 01; 05; 15 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm parameter: Latch | 22047 | 22048 | 01; 05; 15 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm parameter: Latch | 22048 | 22049 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 2
Alarm parameter: Latch | 22049 | 22050 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 1
Alarm parameter: Latch | 22050 | 22051 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 2
Alarm parameter: Latch | 22051 | 22052 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 1
Alarm parameter: Latch | 22052 | 22053 | 01; 05; 15 | Generator > Power protections > Reverse power 2
Alarm parameter: Latch | 22053 | 22054 | 01; 05; 15 | Generator > Power protections > Reverse power 1
Alarm parameter: Latch | 22054 | 22055 | 01; 05; 15 | Generator > Power protections > Overload 2
Alarm parameter: Latch | 22055 | 22056 | 01; 05; 15 | Generator > Power protections > Overload 1
Alarm parameter: Latch | 22056 | 22057 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm parameter: Latch | 22057 | 22058 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm parameter: Latch | 22058 | 22059 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm parameter: Latch | 22059 | 22060 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm parameter: Latch | 22060 | 22061 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm parameter: Latch | 22061 | 22062 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm parameter: Latch | 22062 | 22063 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm parameter: Latch | 22063 | 22064 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm parameter: Latch | 22064 | 22065 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm parameter: Latch | 22065 | 22066 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm parameter: Latch | 22066 | 22067 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm parameter: Latch | 22067 | 22068 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm parameter: Latch | 22068 | 22069 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm parameter: Latch | 22069 | 22070 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm parameter: Latch | 22070 | 22071 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm parameter: Latch | 22071 | 22072 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm parameter: Latch | 22072 | 22073 | 01; 05; 15 | Generator > Current protections > Directional over-current 2
Alarm parameter: Latch | 22073 | 22074 | 01; 05; 15 | Generator > Current protections > Directional over-current 1
Alarm parameter: Latch | 22074 | 22075 | 01; 05; 15 | Generator > Current protections > Fast over-current 2
Alarm parameter: Latch | 22075 | 22076 | 01; 05; 15 | Generator > Current protections > Fast over-current 1
Alarm parameter: Latch | 22076 | 22077 | 01; 05; 15 | Generator > Current protections > Over-current 2
Alarm parameter: Latch | 22077 | 22078 | 01; 05; 15 | Generator > Current protections > Over-current 1
Alarm parameter: Latch | 22078 | 22079 | 01; 05; 15 | Generator > Current protections > Inverse time over-current
Alarm parameter: Latch | 22079 | 22080 | 01; 05; 15 | 4th current input > Current protections > Earth inverse time over-current
Alarm parameter: Latch | 22080 | 22081 | 01; 05; 15 | 4th current input > Current protections > Neutral inverse time over-current
Alarm parameter: Latch | 22100 | 22101 | 01; 05; 15 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm parameter: Latch | 22101 | 22102 | 01; 05; 15 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm parameter: Latch | 22102 | 22103 | 01; 05; 15 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm parameter: Latch | 22103 | 22104 | 01; 05; 15 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm parameter: Latch | 22104 | 22105 | 01; 05; 15 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm parameter: Latch | 22105 | 22106 | 01; 05; 15 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm parameter: Latch | 22106 | 22107 | 01; 05; 15 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm parameter: Latch | 22107 | 22108 | 01; 05; 15 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm parameter: Latch | 22119 | 22120 | 01; 05; 15 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm parameter: Latch | 22120 | 22121 | 01; 05; 15 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm parameter: Latch | 22121 | 22122 | 01; 05; 15 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm parameter: Latch | 22122 | 22123 | 01; 05; 15 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm parameter: Latch | 22123 | 22124 | 01; 05; 15 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm parameter: Latch | 22124 | 22125 | 01; 05; 15 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm parameter: Latch | 22125 | 22126 | 01; 05; 15 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm parameter: Latch | 22126 | 22127 | 01; 05; 15 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm parameter: Latch | 22226 | 22227 | 01; 05; 15 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm parameter: Latch | 22227 | 22228 | 01; 05; 15 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm parameter: Latch | 22228 | 22229 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm parameter: Latch | 22229 | 22230 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm parameter: Latch | 22230 | 22231 | 01; 05; 15 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm parameter: Latch | 22231 | 22232 | 01; 05; 15 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm parameter: Latch | 22232 | 22233 | 01; 05; 15 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm parameter: Latch | 22233 | 22234 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm parameter: Latch | 22234 | 22235 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm parameter: Latch | 22235 | 22236 | 01; 05; 15 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm parameter: Latch | 22236 | 22237 | 01; 05; 15 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm parameter: Latch | 22237 | 22238 | 01; 05; 15 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm parameter: Latch | 22238 | 22239 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm parameter: Latch | 22239 | 22240 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm parameter: Latch | 22240 | 22241 | 01; 05; 15 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm parameter: Latch | 22246 | 22247 | 01; 05; 15 | Utility > Network > Modbus communication timeout
Alarm parameter: Latch | 23500 | 23501 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23501 | 23502 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23502 | 23503 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23503 | 23504 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23504 | 23505 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23505 | 23506 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23506 | 23507 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23507 | 23508 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23508 | 23509 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23509 | 23510 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23510 | 23511 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23511 | 23512 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23512 | 23513 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23513 | 23514 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23514 | 23515 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23515 | 23516 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23516 | 23517 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23517 | 23518 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23518 | 23519 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23519 | 23520 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23520 | 23521 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23521 | 23522 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23522 | 23523 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23523 | 23524 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23524 | 23525 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23525 | 23526 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23526 | 23527 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23527 | 23528 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23528 | 23529 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23529 | 23530 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23530 | 23531 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23531 | 23532 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23532 | 23533 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23533 | 23534 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23534 | 23535 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23535 | 23536 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23536 | 23537 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23537 | 23538 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23538 | 23539 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23539 | 23540 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23540 | 23541 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23541 | 23542 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23542 | 23543 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23543 | 23544 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23544 | 23545 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23545 | 23546 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23546 | 23547 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23547 | 23548 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23548 | 23549 | 01; 05; 15 | Digital custom alarm
Alarm parameter: Latch | 23549 | 23550 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 24000 | 24001 | 01; 05; 15 | Application initialisation error
Alarm action: Acknowledge alarm | 24012 | 24013 | 01; 05; 15 | Total running hours notification
Alarm action: Acknowledge alarm | 24016 | 24017 | 01; 05; 15 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm action: Acknowledge alarm | 24017 | 24018 | 01; 05; 15 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm action: Acknowledge alarm | 24018 | 24019 | 01; 05; 15 | Breakers > Generator breaker > Position failure > GB position failure
Alarm action: Acknowledge alarm | 24019 | 24020 | 01; 05; 15 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm action: Acknowledge alarm | 24020 | 24021 | 01; 05; 15 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm action: Acknowledge alarm | 24022 | 24023 | 01; 05; 15 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm action: Acknowledge alarm | 24023 | 24024 | 01; 05; 15 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm action: Acknowledge alarm | 24032 | 24033 | 01; 05; 15 | Synchronisation > Alarms > Vector mismatch
Alarm action: Acknowledge alarm | 24037 | 24038 | 01; 05; 15 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm action: Acknowledge alarm | 24038 | 24039 | 01; 05; 15 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm action: Acknowledge alarm | 24039 | 24040 | 01; 05; 15 | AC configuration > Generator > Voltage or frequency not OK
Alarm action: Acknowledge alarm | 24040 | 24041 | 01; 05; 15 | Generator > Current protections > Zero sequence current
Alarm action: Acknowledge alarm | 24041 | 24042 | 01; 05; 15 | Generator > Voltage protections > Zero sequence voltage
Alarm action: Acknowledge alarm | 24042 | 24043 | 01; 05; 15 | Generator > Current protections > Negative sequence current
Alarm action: Acknowledge alarm | 24043 | 24044 | 01; 05; 15 | Generator > Voltage protections > Negative sequence voltage
Alarm action: Acknowledge alarm | 24044 | 24045 | 01; 05; 15 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm action: Acknowledge alarm | 24045 | 24046 | 01; 05; 15 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm action: Acknowledge alarm | 24046 | 24047 | 01; 05; 15 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm action: Acknowledge alarm | 24047 | 24048 | 01; 05; 15 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm action: Acknowledge alarm | 24048 | 24049 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 2
Alarm action: Acknowledge alarm | 24049 | 24050 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 1
Alarm action: Acknowledge alarm | 24050 | 24051 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 2
Alarm action: Acknowledge alarm | 24051 | 24052 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 1
Alarm action: Acknowledge alarm | 24052 | 24053 | 01; 05; 15 | Generator > Power protections > Reverse power 2
Alarm action: Acknowledge alarm | 24053 | 24054 | 01; 05; 15 | Generator > Power protections > Reverse power 1
Alarm action: Acknowledge alarm | 24054 | 24055 | 01; 05; 15 | Generator > Power protections > Overload 2
Alarm action: Acknowledge alarm | 24055 | 24056 | 01; 05; 15 | Generator > Power protections > Overload 1
Alarm action: Acknowledge alarm | 24056 | 24057 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm action: Acknowledge alarm | 24057 | 24058 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm action: Acknowledge alarm | 24058 | 24059 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm action: Acknowledge alarm | 24059 | 24060 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm action: Acknowledge alarm | 24060 | 24061 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm action: Acknowledge alarm | 24061 | 24062 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm action: Acknowledge alarm | 24062 | 24063 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm action: Acknowledge alarm | 24063 | 24064 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm action: Acknowledge alarm | 24064 | 24065 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm action: Acknowledge alarm | 24065 | 24066 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm action: Acknowledge alarm | 24066 | 24067 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm action: Acknowledge alarm | 24067 | 24068 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm action: Acknowledge alarm | 24068 | 24069 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm action: Acknowledge alarm | 24069 | 24070 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm action: Acknowledge alarm | 24070 | 24071 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm action: Acknowledge alarm | 24071 | 24072 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm action: Acknowledge alarm | 24072 | 24073 | 01; 05; 15 | Generator > Current protections > Directional over-current 2
Alarm action: Acknowledge alarm | 24073 | 24074 | 01; 05; 15 | Generator > Current protections > Directional over-current 1
Alarm action: Acknowledge alarm | 24074 | 24075 | 01; 05; 15 | Generator > Current protections > Fast over-current 2
Alarm action: Acknowledge alarm | 24075 | 24076 | 01; 05; 15 | Generator > Current protections > Fast over-current 1
Alarm action: Acknowledge alarm | 24076 | 24077 | 01; 05; 15 | Generator > Current protections > Over-current 2
Alarm action: Acknowledge alarm | 24077 | 24078 | 01; 05; 15 | Generator > Current protections > Over-current 1
Alarm action: Acknowledge alarm | 24078 | 24079 | 01; 05; 15 | Generator > Current protections > Inverse time over-current
Alarm action: Acknowledge alarm | 24079 | 24080 | 01; 05; 15 | 4th current input > Current protections > Earth inverse time over-current
Alarm action: Acknowledge alarm | 24080 | 24081 | 01; 05; 15 | 4th current input > Current protections > Neutral inverse time over-current
Alarm action: Acknowledge alarm | 24081 | 24082 | 01; 05; 15 | System not OK
Alarm action: Acknowledge alarm | 24082 | 24083 | 01; 05; 15 | Parameter store delayed
Alarm action: Acknowledge alarm | 24095 | 24096 | 01; 05; 15 | Required IO card(s) not found
Alarm action: Acknowledge alarm | 24096 | 24097 | 01; 05; 15 | Software mismatch on hardware module(s)
Alarm action: Acknowledge alarm | 24100 | 24101 | 01; 05; 15 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm action: Acknowledge alarm | 24101 | 24102 | 01; 05; 15 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm action: Acknowledge alarm | 24102 | 24103 | 01; 05; 15 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm action: Acknowledge alarm | 24103 | 24104 | 01; 05; 15 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm action: Acknowledge alarm | 24104 | 24105 | 01; 05; 15 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm action: Acknowledge alarm | 24105 | 24106 | 01; 05; 15 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm action: Acknowledge alarm | 24106 | 24107 | 01; 05; 15 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm action: Acknowledge alarm | 24107 | 24108 | 01; 05; 15 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm action: Acknowledge alarm | 24116 | 24117 | 01; 05; 15 | Emergency stop
Alarm action: Acknowledge alarm | 24117 | 24118 | 01; 05; 15 | PCM clock battery failure
Alarm action: Acknowledge alarm | 24118 | 24119 | 01; 05; 15 | Controller temperature too high
Alarm action: Acknowledge alarm | 24119 | 24120 | 01; 05; 15 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm action: Acknowledge alarm | 24120 | 24121 | 01; 05; 15 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm action: Acknowledge alarm | 24121 | 24122 | 01; 05; 15 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm action: Acknowledge alarm | 24122 | 24123 | 01; 05; 15 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm action: Acknowledge alarm | 24123 | 24124 | 01; 05; 15 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm action: Acknowledge alarm | 24124 | 24125 | 01; 05; 15 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm action: Acknowledge alarm | 24125 | 24126 | 01; 05; 15 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm action: Acknowledge alarm | 24126 | 24127 | 01; 05; 15 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm action: Acknowledge alarm | 24208 | 24209 | 01; 05; 15 | Utility > Network > Ethernet redundancy broken
Alarm action: Acknowledge alarm | 24226 | 24227 | 01; 05; 15 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm action: Acknowledge alarm | 24227 | 24228 | 01; 05; 15 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm action: Acknowledge alarm | 24228 | 24229 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm action: Acknowledge alarm | 24229 | 24230 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm action: Acknowledge alarm | 24230 | 24231 | 01; 05; 15 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm action: Acknowledge alarm | 24231 | 24232 | 01; 05; 15 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm action: Acknowledge alarm | 24232 | 24233 | 01; 05; 15 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm action: Acknowledge alarm | 24233 | 24234 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm action: Acknowledge alarm | 24234 | 24235 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm action: Acknowledge alarm | 24235 | 24236 | 01; 05; 15 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm action: Acknowledge alarm | 24236 | 24237 | 01; 05; 15 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm action: Acknowledge alarm | 24237 | 24238 | 01; 05; 15 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm action: Acknowledge alarm | 24238 | 24239 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm action: Acknowledge alarm | 24239 | 24240 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm action: Acknowledge alarm | 24240 | 24241 | 01; 05; 15 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm action: Acknowledge alarm | 24246 | 24247 | 01; 05; 15 | Utility > Network > Modbus communication timeout
Alarm action: Acknowledge alarm | 25500 | 25501 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25501 | 25502 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25502 | 25503 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25503 | 25504 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25504 | 25505 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25505 | 25506 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25506 | 25507 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25507 | 25508 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25508 | 25509 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25509 | 25510 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25510 | 25511 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25511 | 25512 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25512 | 25513 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25513 | 25514 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25514 | 25515 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25515 | 25516 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25516 | 25517 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25517 | 25518 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25518 | 25519 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25519 | 25520 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25520 | 25521 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25521 | 25522 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25522 | 25523 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25523 | 25524 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25524 | 25525 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25525 | 25526 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25526 | 25527 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25527 | 25528 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25528 | 25529 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25529 | 25530 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25530 | 25531 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25531 | 25532 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25532 | 25533 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25533 | 25534 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25534 | 25535 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25535 | 25536 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25536 | 25537 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25537 | 25538 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25538 | 25539 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25539 | 25540 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25540 | 25541 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25541 | 25542 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25542 | 25543 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25543 | 25544 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25544 | 25545 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25545 | 25546 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25546 | 25547 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25547 | 25548 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25548 | 25549 | 01; 05; 15 | Digital custom alarm
Alarm action: Acknowledge alarm | 25549 | 25550 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 26000 | 26001 | 01; 05; 15 | Application initialisation error
Alarm action: Reset latch | 26012 | 26013 | 01; 05; 15 | Total running hours notification
Alarm action: Reset latch | 26016 | 26017 | 01; 05; 15 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm action: Reset latch | 26017 | 26018 | 01; 05; 15 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm action: Reset latch | 26018 | 26019 | 01; 05; 15 | Breakers > Generator breaker > Position failure > GB position failure
Alarm action: Reset latch | 26019 | 26020 | 01; 05; 15 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm action: Reset latch | 26020 | 26021 | 01; 05; 15 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm action: Reset latch | 26022 | 26023 | 01; 05; 15 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm action: Reset latch | 26023 | 26024 | 01; 05; 15 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm action: Reset latch | 26032 | 26033 | 01; 05; 15 | Synchronisation > Alarms > Vector mismatch
Alarm action: Reset latch | 26037 | 26038 | 01; 05; 15 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm action: Reset latch | 26038 | 26039 | 01; 05; 15 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm action: Reset latch | 26039 | 26040 | 01; 05; 15 | AC configuration > Generator > Voltage or frequency not OK
Alarm action: Reset latch | 26040 | 26041 | 01; 05; 15 | Generator > Current protections > Zero sequence current
Alarm action: Reset latch | 26041 | 26042 | 01; 05; 15 | Generator > Voltage protections > Zero sequence voltage
Alarm action: Reset latch | 26042 | 26043 | 01; 05; 15 | Generator > Current protections > Negative sequence current
Alarm action: Reset latch | 26043 | 26044 | 01; 05; 15 | Generator > Voltage protections > Negative sequence voltage
Alarm action: Reset latch | 26044 | 26045 | 01; 05; 15 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm action: Reset latch | 26045 | 26046 | 01; 05; 15 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm action: Reset latch | 26046 | 26047 | 01; 05; 15 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm action: Reset latch | 26047 | 26048 | 01; 05; 15 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm action: Reset latch | 26048 | 26049 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 2
Alarm action: Reset latch | 26049 | 26050 | 01; 05; 15 | Generator > Reactive power protections > Reactive power import 1
Alarm action: Reset latch | 26050 | 26051 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 2
Alarm action: Reset latch | 26051 | 26052 | 01; 05; 15 | Generator > Reactive power protections > Reactive power export 1
Alarm action: Reset latch | 26052 | 26053 | 01; 05; 15 | Generator > Power protections > Reverse power 2
Alarm action: Reset latch | 26053 | 26054 | 01; 05; 15 | Generator > Power protections > Reverse power 1
Alarm action: Reset latch | 26054 | 26055 | 01; 05; 15 | Generator > Power protections > Overload 2
Alarm action: Reset latch | 26055 | 26056 | 01; 05; 15 | Generator > Power protections > Overload 1
Alarm action: Reset latch | 26056 | 26057 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm action: Reset latch | 26057 | 26058 | 01; 05; 15 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm action: Reset latch | 26058 | 26059 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm action: Reset latch | 26059 | 26060 | 01; 05; 15 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm action: Reset latch | 26060 | 26061 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm action: Reset latch | 26061 | 26062 | 01; 05; 15 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm action: Reset latch | 26062 | 26063 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm action: Reset latch | 26063 | 26064 | 01; 05; 15 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm action: Reset latch | 26064 | 26065 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm action: Reset latch | 26065 | 26066 | 01; 05; 15 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm action: Reset latch | 26066 | 26067 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm action: Reset latch | 26067 | 26068 | 01; 05; 15 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm action: Reset latch | 26068 | 26069 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm action: Reset latch | 26069 | 26070 | 01; 05; 15 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm action: Reset latch | 26070 | 26071 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm action: Reset latch | 26071 | 26072 | 01; 05; 15 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm action: Reset latch | 26072 | 26073 | 01; 05; 15 | Generator > Current protections > Directional over-current 2
Alarm action: Reset latch | 26073 | 26074 | 01; 05; 15 | Generator > Current protections > Directional over-current 1
Alarm action: Reset latch | 26074 | 26075 | 01; 05; 15 | Generator > Current protections > Fast over-current 2
Alarm action: Reset latch | 26075 | 26076 | 01; 05; 15 | Generator > Current protections > Fast over-current 1
Alarm action: Reset latch | 26076 | 26077 | 01; 05; 15 | Generator > Current protections > Over-current 2
Alarm action: Reset latch | 26077 | 26078 | 01; 05; 15 | Generator > Current protections > Over-current 1
Alarm action: Reset latch | 26078 | 26079 | 01; 05; 15 | Generator > Current protections > Inverse time over-current
Alarm action: Reset latch | 26079 | 26080 | 01; 05; 15 | 4th current input > Current protections > Earth inverse time over-current
Alarm action: Reset latch | 26080 | 26081 | 01; 05; 15 | 4th current input > Current protections > Neutral inverse time over-current
Alarm action: Reset latch | 26081 | 26082 | 01; 05; 15 | System not OK
Alarm action: Reset latch | 26082 | 26083 | 01; 05; 15 | Parameter store delayed
Alarm action: Reset latch | 26095 | 26096 | 01; 05; 15 | Required IO card(s) not found
Alarm action: Reset latch | 26096 | 26097 | 01; 05; 15 | Software mismatch on hardware module(s)
Alarm action: Reset latch | 26100 | 26101 | 01; 05; 15 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm action: Reset latch | 26101 | 26102 | 01; 05; 15 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm action: Reset latch | 26102 | 26103 | 01; 05; 15 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm action: Reset latch | 26103 | 26104 | 01; 05; 15 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm action: Reset latch | 26104 | 26105 | 01; 05; 15 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm action: Reset latch | 26105 | 26106 | 01; 05; 15 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm action: Reset latch | 26106 | 26107 | 01; 05; 15 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm action: Reset latch | 26107 | 26108 | 01; 05; 15 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm action: Reset latch | 26116 | 26117 | 01; 05; 15 | Emergency stop
Alarm action: Reset latch | 26117 | 26118 | 01; 05; 15 | PCM clock battery failure
Alarm action: Reset latch | 26118 | 26119 | 01; 05; 15 | Controller temperature too high
Alarm action: Reset latch | 26119 | 26120 | 01; 05; 15 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm action: Reset latch | 26120 | 26121 | 01; 05; 15 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm action: Reset latch | 26121 | 26122 | 01; 05; 15 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm action: Reset latch | 26122 | 26123 | 01; 05; 15 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm action: Reset latch | 26123 | 26124 | 01; 05; 15 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm action: Reset latch | 26124 | 26125 | 01; 05; 15 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm action: Reset latch | 26125 | 26126 | 01; 05; 15 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm action: Reset latch | 26126 | 26127 | 01; 05; 15 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm action: Reset latch | 26208 | 26209 | 01; 05; 15 | Utility > Network > Ethernet redundancy broken
Alarm action: Reset latch | 26226 | 26227 | 01; 05; 15 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm action: Reset latch | 26227 | 26228 | 01; 05; 15 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm action: Reset latch | 26228 | 26229 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm action: Reset latch | 26229 | 26230 | 01; 05; 15 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm action: Reset latch | 26230 | 26231 | 01; 05; 15 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm action: Reset latch | 26231 | 26232 | 01; 05; 15 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm action: Reset latch | 26232 | 26233 | 01; 05; 15 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm action: Reset latch | 26233 | 26234 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm action: Reset latch | 26234 | 26235 | 01; 05; 15 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm action: Reset latch | 26235 | 26236 | 01; 05; 15 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm action: Reset latch | 26236 | 26237 | 01; 05; 15 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm action: Reset latch | 26237 | 26238 | 01; 05; 15 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm action: Reset latch | 26238 | 26239 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm action: Reset latch | 26239 | 26240 | 01; 05; 15 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm action: Reset latch | 26240 | 26241 | 01; 05; 15 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm action: Reset latch | 26246 | 26247 | 01; 05; 15 | Utility > Network > Modbus communication timeout
Alarm action: Reset latch | 27500 | 27501 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27501 | 27502 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27502 | 27503 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27503 | 27504 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27504 | 27505 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27505 | 27506 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27506 | 27507 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27507 | 27508 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27508 | 27509 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27509 | 27510 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27510 | 27511 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27511 | 27512 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27512 | 27513 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27513 | 27514 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27514 | 27515 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27515 | 27516 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27516 | 27517 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27517 | 27518 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27518 | 27519 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27519 | 27520 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27520 | 27521 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27521 | 27522 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27522 | 27523 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27523 | 27524 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27524 | 27525 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27525 | 27526 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27526 | 27527 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27527 | 27528 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27528 | 27529 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27529 | 27530 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27530 | 27531 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27531 | 27532 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27532 | 27533 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27533 | 27534 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27534 | 27535 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27535 | 27536 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27536 | 27537 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27537 | 27538 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27538 | 27539 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27539 | 27540 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27540 | 27541 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27541 | 27542 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27542 | 27543 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27543 | 27544 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27544 | 27545 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27545 | 27546 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27546 | 27547 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27547 | 27548 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27548 | 27549 | 01; 05; 15 | Digital custom alarm
Alarm action: Reset latch | 27549 | 27550 | 01; 05; 15 | Digital custom alarm
General parameter: Enable | 46307 | 46308 | 01; 05; 15 | Alarm horn > Horn 1 > De-energise when all alarms are acknowledged
General parameter: Enable | 46308 | 46309 | 01; 05; 15 | Alarm horn > Horn 1 > Reset when new alarm
General parameter: Enable | 46311 | 46312 | 01; 05; 15 | Alarm horn > Horn 2 > De-energise when all alarms are acknowledged
General parameter: Enable | 46312 | 46313 | 01; 05; 15 | Alarm horn > Horn 2 > Reset when new alarm
General parameter: Enable | 46315 | 46316 | 01; 05; 15 | Alarm horn > Horn 3 > De-energise when all alarms are acknowledged
General parameter: Enable | 46316 | 46317 | 01; 05; 15 | Alarm horn > Horn 3 > Reset when new alarm
General parameter: Enable | 46321 | 46322 | 01; 05; 15 | Utility > Custom logic > Enable
General parameter: Enable | 46495 | 46496 | 01; 05; 15 | Non-essential load trip > Trip 1 > Settings > Trip when breaker trips
General parameter: Enable | 46496 | 46497 | 01; 05; 15 | Non-essential load trip > Trip 2 > Settings > Trip when breaker trips
General parameter: Enable | 46497 | 46498 | 01; 05; 15 | Non-essential load trip > Trip 3 > Settings > Trip when breaker trips
Note on A4: Maarten van Bemmel: More information about each function group is available in the description sheet.
Note on D4: Maarten van Bemmel: 01 - Read single or multiple 05 - Write single 15 - Write multiple
Note on E4: Maarten van Bemmel: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name
Alarm status: Active | 20000 | 120001 | 02 | Application initialisation error
Alarm status: Active | 20012 | 120013 | 02 | Total running hours notification
Alarm status: Active | 20016 | 120017 | 02 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm status: Active | 20017 | 120018 | 02 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm status: Active | 20018 | 120019 | 02 | Breakers > Generator breaker > Position failure > GB position failure
Alarm status: Active | 20019 | 120020 | 02 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm status: Active | 20020 | 120021 | 02 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm status: Active | 20022 | 120023 | 02 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm status: Active | 20023 | 120024 | 02 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm status: Active | 20032 | 120033 | 02 | Synchronisation > Alarms > Vector mismatch
Alarm status: Active | 20037 | 120038 | 02 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm status: Active | 20038 | 120039 | 02 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm status: Active | 20039 | 120040 | 02 | AC configuration > Generator > Voltage or frequency not OK
Alarm status: Active | 20040 | 120041 | 02 | Generator > Current protections > Zero sequence current
Alarm status: Active | 20041 | 120042 | 02 | Generator > Voltage protections > Zero sequence voltage
Alarm status: Active | 20042 | 120043 | 02 | Generator > Current protections > Negative sequence current
Alarm status: Active | 20043 | 120044 | 02 | Generator > Voltage protections > Negative sequence voltage
Alarm status: Active | 20044 | 120045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm status: Active | 20045 | 120046 | 02 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm status: Active | 20046 | 120047 | 02 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm status: Active | 20047 | 120048 | 02 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm status: Active | 20048 | 120049 | 02 | Generator > Reactive power protections > Reactive power import 2
Alarm status: Active | 20049 | 120050 | 02 | Generator > Reactive power protections > Reactive power import 1
Alarm status: Active | 20050 | 120051 | 02 | Generator > Reactive power protections > Reactive power export 2
Alarm status: Active | 20051 | 120052 | 02 | Generator > Reactive power protections > Reactive power export 1
Alarm status: Active | 20052 | 120053 | 02 | Generator > Power protections > Reverse power 2
Alarm status: Active | 20053 | 120054 | 02 | Generator > Power protections > Reverse power 1
Alarm status: Active | 20054 | 120055 | 02 | Generator > Power protections > Overload 2
Alarm status: Active | 20055 | 120056 | 02 | Generator > Power protections > Overload 1
Alarm status: Active | 20056 | 120057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm status: Active | 20057 | 120058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm status: Active | 20058 | 120059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm status: Active | 20059 | 120060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm status: Active | 20060 | 120061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm status: Active | 20061 | 120062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm status: Active | 20062 | 120063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm status: Active | 20063 | 120064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm status: Active | 20064 | 120065 | 02 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm status: Active | 20065 | 120066 | 02 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm status: Active | 20066 | 120067 | 02 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm status: Active | 20067 | 120068 | 02 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm status: Active | 20068 | 120069 | 02 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm status: Active | 20069 | 120070 | 02 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm status: Active | 20070 | 120071 | 02 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm status: Active | 20071 | 120072 | 02 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm status: Active | 20072 | 120073 | 02 | Generator > Current protections > Directional over-current 2
Alarm status: Active | 20073 | 120074 | 02 | Generator > Current protections > Directional over-current 1
Alarm status: Active | 20074 | 120075 | 02 | Generator > Current protections > Fast over-current 2
Alarm status: Active | 20075 | 120076 | 02 | Generator > Current protections > Fast over-current 1
Alarm status: Active | 20076 | 120077 | 02 | Generator > Current protections > Over-current 2
Alarm status: Active | 20077 | 120078 | 02 | Generator > Current protections > Over-current 1
Alarm status: Active | 20078 | 120079 | 02 | Generator > Current protections > Inverse time over-current
Alarm status: Active | 20079 | 120080 | 02 | 4th current input > Current protections > Earth inverse time over-current
Alarm status: Active | 20080 | 120081 | 02 | 4th current input > Current protections > Neutral inverse time over-current
Alarm status: Active | 20081 | 120082 | 02 | System not OK
Alarm status: Active | 20082 | 120083 | 02 | Parameter store delayed
Alarm status: Active | 20095 | 120096 | 02 | Required IO card(s) not found
Alarm status: Active | 20096 | 120097 | 02 | Software mismatch on hardware module(s)
Alarm status: Active | 20100 | 120101 | 02 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm status: Active | 20101 | 120102 | 02 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm status: Active | 20102 | 120103 | 02 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm status: Active | 20103 | 120104 | 02 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm status: Active | 20104 | 120105 | 02 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm status: Active | 20105 | 120106 | 02 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm status: Active | 20106 | 120107 | 02 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm status: Active | 20107 | 120108 | 02 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm status: Active | 20116 | 120117 | 02 | Emergency stop
Alarm status: Active | 20117 | 120118 | 02 | PCM clock battery failure
Alarm status: Active | 20118 | 120119 | 02 | Controller temperature too high
Alarm status: Active | 20119 | 120120 | 02 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm status: Active | 20120 | 120121 | 02 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm status: Active | 20121 | 120122 | 02 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm status: Active | 20122 | 120123 | 02 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm status: Active | 20123 | 120124 | 02 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm status: Active | 20124 | 120125 | 02 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm status: Active | 20125 | 120126 | 02 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm status: Active | 20126 | 120127 | 02 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm status: Active | 20208 | 120209 | 02 | Utility > Network > Ethernet redundancy broken
Alarm status: Active | 20226 | 120227 | 02 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm status: Active | 20227 | 120228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm status: Active | 20228 | 120229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm status: Active | 20229 | 120230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm status: Active | 20230 | 120231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm status: Active | 20231 | 120232 | 02 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm status: Active | 20232 | 120233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm status: Active | 20233 | 120234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm status: Active | 20234 | 120235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm status: Active | 20235 | 120236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm status: Active | 20236 | 120237 | 02 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm status: Active | 20237 | 120238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm status: Active | 20238 | 120239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm status: Active | 20239 | 120240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm status: Active | 20240 | 120241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm status: Active | 20246 | 120247 | 02 | Utility > Network > Modbus communication timeout
Alarm status: Active | 21500 | 121501 | 02 | Digital custom alarm
Alarm status: Active | 21501 | 121502 | 02 | Digital custom alarm
Alarm status: Active | 21502 | 121503 | 02 | Digital custom alarm
Alarm status: Active | 21503 | 121504 | 02 | Digital custom alarm
Alarm status: Active | 21504 | 121505 | 02 | Digital custom alarm
Alarm status: Active | 21505 | 121506 | 02 | Digital custom alarm
Alarm status: Active | 21506 | 121507 | 02 | Digital custom alarm
Alarm status: Active | 21507 | 121508 | 02 | Digital custom alarm
Alarm status: Active | 21508 | 121509 | 02 | Digital custom alarm
Alarm status: Active | 21509 | 121510 | 02 | Digital custom alarm
Alarm status: Active | 21510 | 121511 | 02 | Digital custom alarm
Alarm status: Active | 21511 | 121512 | 02 | Digital custom alarm
Alarm status: Active | 21512 | 121513 | 02 | Digital custom alarm
Alarm status: Active | 21513 | 121514 | 02 | Digital custom alarm
Alarm status: Active | 21514 | 121515 | 02 | Digital custom alarm
Alarm status: Active | 21515 | 121516 | 02 | Digital custom alarm
Alarm status: Active | 21516 | 121517 | 02 | Digital custom alarm
Alarm status: Active | 21517 | 121518 | 02 | Digital custom alarm
Alarm status: Active | 21518 | 121519 | 02 | Digital custom alarm
Alarm status: Active | 21519 | 121520 | 02 | Digital custom alarm
Alarm status: Active | 21520 | 121521 | 02 | Digital custom alarm
Alarm status: Active | 21521 | 121522 | 02 | Digital custom alarm
Alarm status: Active | 21522 | 121523 | 02 | Digital custom alarm
Alarm status: Active | 21523 | 121524 | 02 | Digital custom alarm
Alarm status: Active | 21524 | 121525 | 02 | Digital custom alarm
Alarm status: Active | 21525 | 121526 | 02 | Digital custom alarm
Alarm status: Active | 21526 | 121527 | 02 | Digital custom alarm
Alarm status: Active | 21527 | 121528 | 02 | Digital custom alarm
Alarm status: Active | 21528 | 121529 | 02 | Digital custom alarm
Alarm status: Active | 21529 | 121530 | 02 | Digital custom alarm
Alarm status: Active | 21530 | 121531 | 02 | Digital custom alarm
Alarm status: Active | 21531 | 121532 | 02 | Digital custom alarm
Alarm status: Active | 21532 | 121533 | 02 | Digital custom alarm
Alarm status: Active | 21533 | 121534 | 02 | Digital custom alarm
Alarm status: Active | 21534 | 121535 | 02 | Digital custom alarm
Alarm status: Active | 21535 | 121536 | 02 | Digital custom alarm
Alarm status: Active | 21536 | 121537 | 02 | Digital custom alarm
Alarm status: Active | 21537 | 121538 | 02 | Digital custom alarm
Alarm status: Active | 21538 | 121539 | 02 | Digital custom alarm
Alarm status: Active | 21539 | 121540 | 02 | Digital custom alarm
Alarm status: Active | 21540 | 121541 | 02 | Digital custom alarm
Alarm status: Active | 21541 | 121542 | 02 | Digital custom alarm
Alarm status: Active | 21542 | 121543 | 02 | Digital custom alarm
Alarm status: Active | 21543 | 121544 | 02 | Digital custom alarm
Alarm status: Active | 21544 | 121545 | 02 | Digital custom alarm
Alarm status: Active | 21545 | 121546 | 02 | Digital custom alarm
Alarm status: Active | 21546 | 121547 | 02 | Digital custom alarm
Alarm status: Active | 21547 | 121548 | 02 | Digital custom alarm
Alarm status: Active | 21548 | 121549 | 02 | Digital custom alarm
Alarm status: Active | 21549 | 121550 | 02 | Digital custom alarm
Alarm status: Acknowledged | 22000 | 122001 | 02 | Application initialisation error
Alarm status: Acknowledged | 22012 | 122013 | 02 | Total running hours notification
Alarm status: Acknowledged | 22016 | 122017 | 02 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm status: Acknowledged | 22017 | 122018 | 02 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm status: Acknowledged | 22018 | 122019 | 02 | Breakers > Generator breaker > Position failure > GB position failure
Alarm status: Acknowledged | 22019 | 122020 | 02 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm status: Acknowledged | 22020 | 122021 | 02 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm status: Acknowledged | 22022 | 122023 | 02 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm status: Acknowledged | 22023 | 122024 | 02 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm status: Acknowledged | 22032 | 122033 | 02 | Synchronisation > Alarms > Vector mismatch
Alarm status: Acknowledged | 22037 | 122038 | 02 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm status: Acknowledged | 22038 | 122039 | 02 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm status: Acknowledged | 22039 | 122040 | 02 | AC configuration > Generator > Voltage or frequency not OK
Alarm status: Acknowledged | 22040 | 122041 | 02 | Generator > Current protections > Zero sequence current
Alarm status: Acknowledged | 22041 | 122042 | 02 | Generator > Voltage protections > Zero sequence voltage
Alarm status: Acknowledged | 22042 | 122043 | 02 | Generator > Current protections > Negative sequence current
Alarm status: Acknowledged | 22043 | 122044 | 02 | Generator > Voltage protections > Negative sequence voltage
Alarm status: Acknowledged | 22044 | 122045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm status: Acknowledged | 22045 | 122046 | 02 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm status: Acknowledged | 22046 | 122047 | 02 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm status: Acknowledged | 22047 | 122048 | 02 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm status: Acknowledged | 22048 | 122049 | 02 | Generator > Reactive power protections > Reactive power import 2
Alarm status: Acknowledged | 22049 | 122050 | 02 | Generator > Reactive power protections > Reactive power import 1
Alarm status: Acknowledged | 22050 | 122051 | 02 | Generator > Reactive power protections > Reactive power export 2
Alarm status: Acknowledged | 22051 | 122052 | 02 | Generator > Reactive power protections > Reactive power export 1
Alarm status: Acknowledged | 22052 | 122053 | 02 | Generator > Power protections > Reverse power 2
Alarm status: Acknowledged | 22053 | 122054 | 02 | Generator > Power protections > Reverse power 1
Alarm status: Acknowledged | 22054 | 122055 | 02 | Generator > Power protections > Overload 2
Alarm status: Acknowledged | 22055 | 122056 | 02 | Generator > Power protections > Overload 1
Alarm status: Acknowledged | 22056 | 122057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm status: Acknowledged | 22057 | 122058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm status: Acknowledged | 22058 | 122059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm status: Acknowledged | 22059 | 122060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm status: Acknowledged | 22060 | 122061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm status: Acknowledged | 22061 | 122062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm status: Acknowledged | 22062 | 122063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm status: Acknowledged | 22063 | 122064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm status: Acknowledged | 22064 | 122065 | 02 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm status: Acknowledged | 22065 | 122066 | 02 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm status: Acknowledged | 22066 | 122067 | 02 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm status: Acknowledged | 22067 | 122068 | 02 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm status: Acknowledged | 22068 | 122069 | 02 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm status: Acknowledged | 22069 | 122070 | 02 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm status: Acknowledged | 22070 | 122071 | 02 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm status: Acknowledged | 22071 | 122072 | 02 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm status: Acknowledged | 22072 | 122073 | 02 | Generator > Current protections > Directional over-current 2
Alarm status: Acknowledged | 22073 | 122074 | 02 | Generator > Current protections > Directional over-current 1
Alarm status: Acknowledged | 22074 | 122075 | 02 | Generator > Current protections > Fast over-current 2
Alarm status: Acknowledged | 22075 | 122076 | 02 | Generator > Current protections > Fast over-current 1
Alarm status: Acknowledged | 22076 | 122077 | 02 | Generator > Current protections > Over-current 2
Alarm status: Acknowledged | 22077 | 122078 | 02 | Generator > Current protections > Over-current 1
Alarm status: Acknowledged | 22078 | 122079 | 02 | Generator > Current protections > Inverse time over-current
Alarm status: Acknowledged | 22079 | 122080 | 02 | 4th current input > Current protections > Earth inverse time over-current
Alarm status: Acknowledged | 22080 | 122081 | 02 | 4th current input > Current protections > Neutral inverse time over-current
Alarm status: Acknowledged | 22081 | 122082 | 02 | System not OK
Alarm status: Acknowledged | 22082 | 122083 | 02 | Parameter store delayed
Alarm status: Acknowledged | 22095 | 122096 | 02 | Required IO card(s) not found
Alarm status: Acknowledged | 22096 | 122097 | 02 | Software mismatch on hardware module(s)
Alarm status: Acknowledged | 22100 | 122101 | 02 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm status: Acknowledged | 22101 | 122102 | 02 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm status: Acknowledged | 22102 | 122103 | 02 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm status: Acknowledged | 22103 | 122104 | 02 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm status: Acknowledged | 22104 | 122105 | 02 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm status: Acknowledged | 22105 | 122106 | 02 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm status: Acknowledged | 22106 | 122107 | 02 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm status: Acknowledged | 22107 | 122108 | 02 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm status: Acknowledged | 22116 | 122117 | 02 | Emergency stop
Alarm status: Acknowledged | 22117 | 122118 | 02 | PCM clock battery failure
Alarm status: Acknowledged | 22118 | 122119 | 02 | Controller temperature too high
Alarm status: Acknowledged | 22119 | 122120 | 02 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm status: Acknowledged | 22120 | 122121 | 02 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm status: Acknowledged | 22121 | 122122 | 02 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm status: Acknowledged | 22122 | 122123 | 02 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm status: Acknowledged | 22123 | 122124 | 02 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm status: Acknowledged | 22124 | 122125 | 02 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm status: Acknowledged | 22125 | 122126 | 02 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm status: Acknowledged | 22126 | 122127 | 02 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm status: Acknowledged | 22208 | 122209 | 02 | Utility > Network > Ethernet redundancy broken
Alarm status: Acknowledged | 22226 | 122227 | 02 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm status: Acknowledged | 22227 | 122228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm status: Acknowledged | 22228 | 122229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm status: Acknowledged | 22229 | 122230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm status: Acknowledged | 22230 | 122231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm status: Acknowledged | 22231 | 122232 | 02 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm status: Acknowledged | 22232 | 122233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm status: Acknowledged | 22233 | 122234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm status: Acknowledged | 22234 | 122235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm status: Acknowledged | 22235 | 122236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm status: Acknowledged | 22236 | 122237 | 02 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm status: Acknowledged | 22237 | 122238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm status: Acknowledged | 22238 | 122239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm status: Acknowledged | 22239 | 122240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm status: Acknowledged | 22240 | 122241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm status: Acknowledged | 22246 | 122247 | 02 | Utility > Network > Modbus communication timeout
Alarm status: Acknowledged | 23500 | 123501 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23501 | 123502 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23502 | 123503 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23503 | 123504 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23504 | 123505 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23505 | 123506 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23506 | 123507 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23507 | 123508 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23508 | 123509 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23509 | 123510 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23510 | 123511 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23511 | 123512 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23512 | 123513 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23513 | 123514 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23514 | 123515 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23515 | 123516 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23516 | 123517 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23517 | 123518 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23518 | 123519 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23519 | 123520 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23520 | 123521 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23521 | 123522 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23522 | 123523 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23523 | 123524 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23524 | 123525 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23525 | 123526 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23526 | 123527 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23527 | 123528 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23528 | 123529 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23529 | 123530 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23530 | 123531 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23531 | 123532 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23532 | 123533 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23533 | 123534 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23534 | 123535 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23535 | 123536 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23536 | 123537 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23537 | 123538 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23538 | 123539 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23539 | 123540 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23540 | 123541 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23541 | 123542 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23542 | 123543 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23543 | 123544 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23544 | 123545 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23545 | 123546 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23546 | 123547 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23547 | 123548 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23548 | 123549 | 02 | Digital custom alarm
Alarm status: Acknowledged | 23549 | 123550 | 02 | Digital custom alarm
Alarm status: Latched | 24000 | 124001 | 02 | Application initialisation error
Alarm status: Latched | 24012 | 124013 | 02 | Total running hours notification
Alarm status: Latched | 24016 | 124017 | 02 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm status: Latched | 24017 | 124018 | 02 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm status: Latched | 24018 | 124019 | 02 | Breakers > Generator breaker > Position failure > GB position failure
Alarm status: Latched | 24019 | 124020 | 02 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm status: Latched | 24020 | 124021 | 02 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm status: Latched | 24022 | 124023 | 02 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm status: Latched | 24023 | 124024 | 02 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm status: Latched | 24032 | 124033 | 02 | Synchronisation > Alarms > Vector mismatch
Alarm status: Latched | 24037 | 124038 | 02 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm status: Latched | 24038 | 124039 | 02 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm status: Latched | 24039 | 124040 | 02 | AC configuration > Generator > Voltage or frequency not OK
Alarm status: Latched | 24040 | 124041 | 02 | Generator > Current protections > Zero sequence current
Alarm status: Latched | 24041 | 124042 | 02 | Generator > Voltage protections > Zero sequence voltage
Alarm status: Latched | 24042 | 124043 | 02 | Generator > Current protections > Negative sequence current
Alarm status: Latched | 24043 | 124044 | 02 | Generator > Voltage protections > Negative sequence voltage
Alarm status: Latched | 24044 | 124045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm status: Latched | 24045 | 124046 | 02 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm status: Latched | 24046 | 124047 | 02 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm status: Latched | 24047 | 124048 | 02 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm status: Latched | 24048 | 124049 | 02 | Generator > Reactive power protections > Reactive power import 2
Alarm status: Latched | 24049 | 124050 | 02 | Generator > Reactive power protections > Reactive power import 1
Alarm status: Latched | 24050 | 124051 | 02 | Generator > Reactive power protections > Reactive power export 2
Alarm status: Latched | 24051 | 124052 | 02 | Generator > Reactive power protections > Reactive power export 1
Alarm status: Latched | 24052 | 124053 | 02 | Generator > Power protections > Reverse power 2
Alarm status: Latched | 24053 | 124054 | 02 | Generator > Power protections > Reverse power 1
Alarm status: Latched | 24054 | 124055 | 02 | Generator > Power protections > Overload 2
Alarm status: Latched | 24055 | 124056 | 02 | Generator > Power protections > Overload 1
Alarm status: Latched | 24056 | 124057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm status: Latched | 24057 | 124058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm status: Latched | 24058 | 124059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm status: Latched | 24059 | 124060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm status: Latched | 24060 | 124061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm status: Latched | 24061 | 124062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm status: Latched | 24062 | 124063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm status: Latched | 24063 | 124064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm status: Latched | 24064 | 124065 | 02 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm status: Latched | 24065 | 124066 | 02 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm status: Latched | 24066 | 124067 | 02 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm status: Latched | 24067 | 124068 | 02 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm status: Latched | 24068 | 124069 | 02 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm status: Latched | 24069 | 124070 | 02 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm status: Latched | 24070 | 124071 | 02 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm status: Latched | 24071 | 124072 | 02 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm status: Latched | 24072 | 124073 | 02 | Generator > Current protections > Directional over-current 2
Alarm status: Latched | 24073 | 124074 | 02 | Generator > Current protections > Directional over-current 1
Alarm status: Latched | 24074 | 124075 | 02 | Generator > Current protections > Fast over-current 2
Alarm status: Latched | 24075 | 124076 | 02 | Generator > Current protections > Fast over-current 1
Alarm status: Latched | 24076 | 124077 | 02 | Generator > Current protections > Over-current 2
Alarm status: Latched | 24077 | 124078 | 02 | Generator > Current protections > Over-current 1
Alarm status: Latched | 24078 | 124079 | 02 | Generator > Current protections > Inverse time over-current
Alarm status: Latched | 24079 | 124080 | 02 | 4th current input > Current protections > Earth inverse time over-current
Alarm status: Latched | 24080 | 124081 | 02 | 4th current input > Current protections > Neutral inverse time over-current
Alarm status: Latched | 24081 | 124082 | 02 | System not OK
Alarm status: Latched | 24082 | 124083 | 02 | Parameter store delayed
Alarm status: Latched | 24095 | 124096 | 02 | Required IO card(s) not found
Alarm status: Latched | 24096 | 124097 | 02 | Software mismatch on hardware module(s)
Alarm status: Latched | 24100 | 124101 | 02 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm status: Latched | 24101 | 124102 | 02 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm status: Latched | 24102 | 124103 | 02 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm status: Latched | 24103 | 124104 | 02 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm status: Latched | 24104 | 124105 | 02 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm status: Latched | 24105 | 124106 | 02 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm status: Latched | 24106 | 124107 | 02 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm status: Latched | 24107 | 124108 | 02 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm status: Latched | 24116 | 124117 | 02 | Emergency stop
Alarm status: Latched | 24117 | 124118 | 02 | PCM clock battery failure
Alarm status: Latched | 24118 | 124119 | 02 | Controller temperature too high
Alarm status: Latched | 24119 | 124120 | 02 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm status: Latched | 24120 | 124121 | 02 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm status: Latched | 24121 | 124122 | 02 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm status: Latched | 24122 | 124123 | 02 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm status: Latched | 24123 | 124124 | 02 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm status: Latched | 24124 | 124125 | 02 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm status: Latched | 24125 | 124126 | 02 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm status: Latched | 24126 | 124127 | 02 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm status: Latched | 24208 | 124209 | 02 | Utility > Network > Ethernet redundancy broken
Alarm status: Latched | 24226 | 124227 | 02 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm status: Latched | 24227 | 124228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm status: Latched | 24228 | 124229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm status: Latched | 24229 | 124230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm status: Latched | 24230 | 124231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm status: Latched | 24231 | 124232 | 02 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm status: Latched | 24232 | 124233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm status: Latched | 24233 | 124234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm status: Latched | 24234 | 124235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm status: Latched | 24235 | 124236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm status: Latched | 24236 | 124237 | 02 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm status: Latched | 24237 | 124238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm status: Latched | 24238 | 124239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm status: Latched | 24239 | 124240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm status: Latched | 24240 | 124241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm status: Latched | 24246 | 124247 | 02 | Utility > Network > Modbus communication timeout
Alarm status: Latched | 25500 | 125501 | 02 | Digital custom alarm
Alarm status: Latched | 25501 | 125502 | 02 | Digital custom alarm
Alarm status: Latched | 25502 | 125503 | 02 | Digital custom alarm
Alarm status: Latched | 25503 | 125504 | 02 | Digital custom alarm
Alarm status: Latched | 25504 | 125505 | 02 | Digital custom alarm
Alarm status: Latched | 25505 | 125506 | 02 | Digital custom alarm
Alarm status: Latched | 25506 | 125507 | 02 | Digital custom alarm
Alarm status: Latched | 25507 | 125508 | 02 | Digital custom alarm
Alarm status: Latched | 25508 | 125509 | 02 | Digital custom alarm
Alarm status: Latched | 25509 | 125510 | 02 | Digital custom alarm
Alarm status: Latched | 25510 | 125511 | 02 | Digital custom alarm
Alarm status: Latched | 25511 | 125512 | 02 | Digital custom alarm
Alarm status: Latched | 25512 | 125513 | 02 | Digital custom alarm
Alarm status: Latched | 25513 | 125514 | 02 | Digital custom alarm
Alarm status: Latched | 25514 | 125515 | 02 | Digital custom alarm
Alarm status: Latched | 25515 | 125516 | 02 | Digital custom alarm
Alarm status: Latched | 25516 | 125517 | 02 | Digital custom alarm
Alarm status: Latched | 25517 | 125518 | 02 | Digital custom alarm
Alarm status: Latched | 25518 | 125519 | 02 | Digital custom alarm
Alarm status: Latched | 25519 | 125520 | 02 | Digital custom alarm
Alarm status: Latched | 25520 | 125521 | 02 | Digital custom alarm
Alarm status: Latched | 25521 | 125522 | 02 | Digital custom alarm
Alarm status: Latched | 25522 | 125523 | 02 | Digital custom alarm
Alarm status: Latched | 25523 | 125524 | 02 | Digital custom alarm
Alarm status: Latched | 25524 | 125525 | 02 | Digital custom alarm
Alarm status: Latched | 25525 | 125526 | 02 | Digital custom alarm
Alarm status: Latched | 25526 | 125527 | 02 | Digital custom alarm
Alarm status: Latched | 25527 | 125528 | 02 | Digital custom alarm
Alarm status: Latched | 25528 | 125529 | 02 | Digital custom alarm
Alarm status: Latched | 25529 | 125530 | 02 | Digital custom alarm
Alarm status: Latched | 25530 | 125531 | 02 | Digital custom alarm
Alarm status: Latched | 25531 | 125532 | 02 | Digital custom alarm
Alarm status: Latched | 25532 | 125533 | 02 | Digital custom alarm
Alarm status: Latched | 25533 | 125534 | 02 | Digital custom alarm
Alarm status: Latched | 25534 | 125535 | 02 | Digital custom alarm
Alarm status: Latched | 25535 | 125536 | 02 | Digital custom alarm
Alarm status: Latched | 25536 | 125537 | 02 | Digital custom alarm
Alarm status: Latched | 25537 | 125538 | 02 | Digital custom alarm
Alarm status: Latched | 25538 | 125539 | 02 | Digital custom alarm
Alarm status: Latched | 25539 | 125540 | 02 | Digital custom alarm
Alarm status: Latched | 25540 | 125541 | 02 | Digital custom alarm
Alarm status: Latched | 25541 | 125542 | 02 | Digital custom alarm
Alarm status: Latched | 25542 | 125543 | 02 | Digital custom alarm
Alarm status: Latched | 25543 | 125544 | 02 | Digital custom alarm
Alarm status: Latched | 25544 | 125545 | 02 | Digital custom alarm
Alarm status: Latched | 25545 | 125546 | 02 | Digital custom alarm
Alarm status: Latched | 25546 | 125547 | 02 | Digital custom alarm
Alarm status: Latched | 25547 | 125548 | 02 | Digital custom alarm
Alarm status: Latched | 25548 | 125549 | 02 | Digital custom alarm
Alarm status: Latched | 25549 | 125550 | 02 | Digital custom alarm
Alarm status: Shelved | 26000 | 126001 | 02 | Application initialisation error
Alarm status: Shelved | 26012 | 126013 | 02 | Total running hours notification
Alarm status: Shelved | 26016 | 126017 | 02 | Breakers > Generator breaker > Closing failure > GB closing failure
Alarm status: Shelved | 26017 | 126018 | 02 | Breakers > Generator breaker > Opening failure > GB opening failure
Alarm status: Shelved | 26018 | 126019 | 02 | Breakers > Generator breaker > Position failure > GB position failure
Alarm status: Shelved | 26019 | 126020 | 02 | Breakers > Generator breaker > Configuration failure > GB configuration failure
Alarm status: Shelved | 26020 | 126021 | 02 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure
Alarm status: Shelved | 26022 | 126023 | 02 | Breakers > Generator breaker > Tripped (external) > GB tripped (external)
Alarm status: Shelved | 26023 | 126024 | 02 | Breakers > Generator breaker > Short circuit > GB short circuit
Alarm status: Shelved | 26032 | 126033 | 02 | Synchronisation > Alarms > Vector mismatch
Alarm status: Shelved | 26037 | 126038 | 02 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A
Alarm status: Shelved | 26038 | 126039 | 02 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B
Alarm status: Shelved | 26039 | 126040 | 02 | AC configuration > Generator > Voltage or frequency not OK
Alarm status: Shelved | 26040 | 126041 | 02 | Generator > Current protections > Zero sequence current
Alarm status: Shelved | 26041 | 126042 | 02 | Generator > Voltage protections > Zero sequence voltage
Alarm status: Shelved | 26042 | 126043 | 02 | Generator > Current protections > Negative sequence current
Alarm status: Shelved | 26043 | 126044 | 02 | Generator > Voltage protections > Negative sequence voltage
Alarm status: Shelved | 26044 | 126045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.)
Alarm status: Shelved | 26045 | 126046 | 02 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.)
Alarm status: Shelved | 26046 | 126047 | 02 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance
Alarm status: Shelved | 26047 | 126048 | 02 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance
Alarm status: Shelved | 26048 | 126049 | 02 | Generator > Reactive power protections > Reactive power import 2
Alarm status: Shelved | 26049 | 126050 | 02 | Generator > Reactive power protections > Reactive power import 1
Alarm status: Shelved | 26050 | 126051 | 02 | Generator > Reactive power protections > Reactive power export 2
Alarm status: Shelved | 26051 | 126052 | 02 | Generator > Reactive power protections > Reactive power export 1
Alarm status: Shelved | 26052 | 126053 | 02 | Generator > Power protections > Reverse power 2
Alarm status: Shelved | 26053 | 126054 | 02 | Generator > Power protections > Reverse power 1
Alarm status: Shelved | 26054 | 126055 | 02 | Generator > Power protections > Overload 2
Alarm status: Shelved | 26055 | 126056 | 02 | Generator > Power protections > Overload 1
Alarm status: Shelved | 26056 | 126057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2
Alarm status: Shelved | 26057 | 126058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1
Alarm status: Shelved | 26058 | 126059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2
Alarm status: Shelved | 26059 | 126060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1
Alarm status: Shelved | 26060 | 126061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2
Alarm status: Shelved | 26061 | 126062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1
Alarm status: Shelved | 26062 | 126063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2
Alarm status: Shelved | 26063 | 126064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1
Alarm status: Shelved | 26064 | 126065 | 02 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2
Alarm status: Shelved | 26065 | 126066 | 02 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1
Alarm status: Shelved | 26066 | 126067 | 02 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2
Alarm status: Shelved | 26067 | 126068 | 02 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1
Alarm status: Shelved | 26068 | 126069 | 02 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2
Alarm status: Shelved | 26069 | 126070 | 02 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1
Alarm status: Shelved | 26070 | 126071 | 02 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2
Alarm status: Shelved | 26071 | 126072 | 02 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1
Alarm status: Shelved | 26072 | 126073 | 02 | Generator > Current protections > Directional over-current 2
Alarm status: Shelved | 26073 | 126074 | 02 | Generator > Current protections > Directional over-current 1
Alarm status: Shelved | 26074 | 126075 | 02 | Generator > Current protections > Fast over-current 2
Alarm status: Shelved | 26075 | 126076 | 02 | Generator > Current protections > Fast over-current 1
Alarm status: Shelved | 26076 | 126077 | 02 | Generator > Current protections > Over-current 2
Alarm status: Shelved | 26077 | 126078 | 02 | Generator > Current protections > Over-current 1
Alarm status: Shelved | 26078 | 126079 | 02 | Generator > Current protections > Inverse time over-current
Alarm status: Shelved | 26079 | 126080 | 02 | 4th current input > Current protections > Earth inverse time over-current
Alarm status: Shelved | 26080 | 126081 | 02 | 4th current input > Current protections > Neutral inverse time over-current
Alarm status: Shelved | 26081 | 126082 | 02 | System not OK
Alarm status: Shelved | 26082 | 126083 | 02 | Parameter store delayed
Alarm status: Shelved | 26095 | 126096 | 02 | Required IO card(s) not found
Alarm status: Shelved | 26096 | 126097 | 02 | Software mismatch on hardware module(s)
Alarm status: Shelved | 26100 | 126101 | 02 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break
Alarm status: Shelved | 26101 | 126102 | 02 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break
Alarm status: Shelved | 26102 | 126103 | 02 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break
Alarm status: Shelved | 26103 | 126104 | 02 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break
Alarm status: Shelved | 26104 | 126105 | 02 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break
Alarm status: Shelved | 26105 | 126106 | 02 | AC configuration > Generator > L1 wire break > Generator L1 wire break
Alarm status: Shelved | 26106 | 126107 | 02 | AC configuration > Generator > L2 wire break > Generator L2 wire break
Alarm status: Shelved | 26107 | 126108 | 02 | AC configuration > Generator > L3 wire break > Generator L3 wire break
Alarm status: Shelved | 26116 | 126117 | 02 | Emergency stop
Alarm status: Shelved | 26117 | 126118 | 02 | PCM clock battery failure
Alarm status: Shelved | 26118 | 126119 | 02 | Controller temperature too high
Alarm status: Shelved | 26119 | 126120 | 02 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high
Alarm status: Shelved | 26120 | 126121 | 02 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low
Alarm status: Shelved | 26121 | 126122 | 02 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high
Alarm status: Shelved | 26122 | 126123 | 02 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low
Alarm status: Shelved | 26123 | 126124 | 02 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high
Alarm status: Shelved | 26124 | 126125 | 02 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low
Alarm status: Shelved | 26125 | 126126 | 02 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high
Alarm status: Shelved | 26126 | 126127 | 02 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low
Alarm status: Shelved | 26208 | 126209 | 02 | Utility > Network > Ethernet redundancy broken
Alarm status: Shelved | 26226 | 126227 | 02 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current
Alarm status: Shelved | 26227 | 126228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency
Alarm status: Shelved | 26228 | 126229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1
Alarm status: Shelved | 26229 | 126230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2
Alarm status: Shelved | 26230 | 126231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload
Alarm status: Shelved | 26231 | 126232 | 02 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current
Alarm status: Shelved | 26232 | 126233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency
Alarm status: Shelved | 26233 | 126234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1
Alarm status: Shelved | 26234 | 126235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2
Alarm status: Shelved | 26235 | 126236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload
Alarm status: Shelved | 26236 | 126237 | 02 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current
Alarm status: Shelved | 26237 | 126238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency
Alarm status: Shelved | 26238 | 126239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1
Alarm status: Shelved | 26239 | 126240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2
Alarm status: Shelved | 26240 | 126241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload
Alarm status: Shelved | 26246 | 126247 | 02 | Utility > Network > Modbus communication timeout
Alarm status: Shelved | 27500 | 127501 | 02 | Digital custom alarm
Alarm status: Shelved | 27501 | 127502 | 02 | Digital custom alarm
Alarm status: Shelved | 27502 | 127503 | 02 | Digital custom alarm
Alarm status: Shelved | 27503 | 127504 | 02 | Digital custom alarm
Alarm status: Shelved | 27504 | 127505 | 02 | Digital custom alarm
Alarm status: Shelved | 27505 | 127506 | 02 | Digital custom alarm
Alarm status: Shelved | 27506 | 127507 | 02 | Digital custom alarm
Alarm status: Shelved | 27507 | 127508 | 02 | Digital custom alarm
Alarm status: Shelved | 27508 | 127509 | 02 | Digital custom alarm
Alarm status: Shelved | 27509 | 127510 | 02 | Digital custom alarm
Alarm status: Shelved | 27510 | 127511 | 02 | Digital custom alarm
Alarm status: Shelved | 27511 | 127512 | 02 | Digital custom alarm
Alarm status: Shelved | 27512 | 127513 | 02 | Digital custom alarm
Alarm status: Shelved | 27513 | 127514 | 02 | Digital custom alarm
Alarm status: Shelved | 27514 | 127515 | 02 | Digital custom alarm
Alarm status: Shelved | 27515 | 127516 | 02 | Digital custom alarm
Alarm status: Shelved | 27516 | 127517 | 02 | Digital custom alarm
Alarm status: Shelved | 27517 | 127518 | 02 | Digital custom alarm
Alarm status: Shelved | 27518 | 127519 | 02 | Digital custom alarm
Alarm status: Shelved | 27519 | 127520 | 02 | Digital custom alarm
Alarm status: Shelved | 27520 | 127521 | 02 | Digital custom alarm
Alarm status: Shelved | 27521 | 127522 | 02 | Digital custom alarm
Alarm status: Shelved | 27522 | 127523 | 02 | Digital custom alarm
Alarm status: Shelved | 27523 | 127524 | 02 | Digital custom alarm
Alarm status: Shelved | 27524 | 127525 | 02 | Digital custom alarm
Alarm status: Shelved | 27525 | 127526 | 02 | Digital custom alarm
Alarm status: Shelved | 27526 | 127527 | 02 | Digital custom alarm
Alarm status: Shelved | 27527 | 127528 | 02 | Digital custom alarm
Alarm status: Shelved | 27528 | 127529 | 02 | Digital custom alarm
Alarm status: Shelved | 27529 | 127530 | 02 | Digital custom alarm
Alarm status: Shelved | 27530 | 127531 | 02 | Digital custom alarm
Alarm status: Shelved | 27531 | 127532 | 02 | Digital custom alarm
Alarm status: Shelved | 27532 | 127533 | 02 | Digital custom alarm
Alarm status: Shelved | 27533 | 127534 | 02 | Digital custom alarm
Alarm status: Shelved | 27534 | 127535 | 02 | Digital custom alarm
Alarm status: Shelved | 27535 | 127536 | 02 | Digital custom alarm
Alarm status: Shelved | 27536 | 127537 | 02 | Digital custom alarm
Alarm status: Shelved | 27537 | 127538 | 02 | Digital custom alarm
Alarm status: Shelved | 27538 | 127539 | 02 | Digital custom alarm
Alarm status: Shelved | 27539 | 127540 | 02 | Digital custom alarm
Alarm status: Shelved | 27540 | 127541 | 02 | Digital custom alarm
Alarm status: Shelved | 27541 | 127542 | 02 | Digital custom alarm
Alarm status: Shelved | 27542 | 127543 | 02 | Digital custom alarm
Alarm status: Shelved | 27543 | 127544 | 02 | Digital custom alarm
Alarm status: Shelved | 27544 | 127545 | 02 | Digital custom alarm
Alarm status: Shelved | 27545 | 127546 | 02 | Digital custom alarm
Alarm status: Shelved | 27546 | 127547 | 02 | Digital custom alarm
Alarm status: Shelved | 27547 | 127548 | 02 | Digital custom alarm
Alarm status: Shelved | 27548 | 127549 | 02 | Digital custom alarm
Alarm status: Shelved | 27549 | 127550 | 02 | Digital custom alarm
Alarm status: Delay timer runnning | 32016 | 132017 | 02 | Breakers > Generator breaker > Closing failure > Delay
Alarm status: Delay timer runnning | 32017 | 132018 | 02 | Breakers > Generator breaker > Opening failure > Delay
Alarm status: Delay timer runnning | 32018 | 132019 | 02 | Breakers > Generator breaker > Position failure > Delay
Alarm status: Delay timer runnning | 32019 | 132020 | 02 | Breakers > Generator breaker > Configuration failure > Delay
Alarm status: Delay timer runnning | 32020 | 132021 | 02 | Breakers > Generator breaker > Synchronisation failure > Delay
Alarm status: Delay timer runnning | 32022 | 132023 | 02 | Breakers > Generator breaker > Tripped (external) > Delay
Alarm status: Delay timer runnning | 32032 | 132033 | 02 | Synchronisation > Alarms > Vector mismatch > Delay
Alarm status: Delay timer runnning | 32037 | 132038 | 02 | AC configuration > Busbar > Phase sequence error > Delay
Alarm status: Delay timer runnning | 32038 | 132039 | 02 | AC configuration > Generator > Phase sequence error > Delay
Alarm status: Delay timer runnning | 32039 | 132040 | 02 | AC configuration > Generator > Voltage or frequency not OK > Delay
Alarm status: Delay timer runnning | 32040 | 132041 | 02 | Generator > Current protections > Zero sequence current > Delay
Alarm status: Delay timer runnning | 32041 | 132042 | 02 | Generator > Voltage protections > Zero sequence voltage > Delay
Alarm status: Delay timer runnning | 32042 | 132043 | 02 | Generator > Current protections > Negative sequence current > Delay
Alarm status: Delay timer runnning | 32043 | 132044 | 02 | Generator > Voltage protections > Negative sequence voltage > Delay
Alarm status: Delay timer runnning | 32044 | 132045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Delay
Alarm status: Delay timer runnning | 32045 | 132046 | 02 | Generator > Current protections > Current unbalance (average calc) > Delay
Alarm status: Delay timer runnning | 32046 | 132047 | 02 | Generator > Voltage protections > Voltage unbalance > Delay
Alarm status: Delay timer runnning | 32047 | 132048 | 02 | Busbar > Voltage protections > Voltage unbalance > Delay
Alarm status: Delay timer runnning | 32048 | 132049 | 02 | Generator > Reactive power protections > Reactive power import 2 > Delay
Alarm status: Delay timer runnning | 32049 | 132050 | 02 | Generator > Reactive power protections > Reactive power import 1 > Delay
Alarm status: Delay timer runnning | 32050 | 132051 | 02 | Generator > Reactive power protections > Reactive power export 2 > Delay
Alarm status: Delay timer runnning | 32051 | 132052 | 02 | Generator > Reactive power protections > Reactive power export 1 > Delay
Alarm status: Delay timer runnning | 32052 | 132053 | 02 | Generator > Power protections > Reverse power 2 > Delay
Alarm status: Delay timer runnning | 32053 | 132054 | 02 | Generator > Power protections > Reverse power 1 > Delay
Alarm status: Delay timer runnning | 32054 | 132055 | 02 | Generator > Power protections > Overload 2 > Delay
Alarm status: Delay timer runnning | 32055 | 132056 | 02 | Generator > Power protections > Overload 1 > Delay
Alarm status: Delay timer runnning | 32056 | 132057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Delay
Alarm status: Delay timer runnning | 32057 | 132058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Delay
Alarm status: Delay timer runnning | 32058 | 132059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Delay
Alarm status: Delay timer runnning | 32059 | 132060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Delay
Alarm status: Delay timer runnning | 32060 | 132061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Delay
Alarm status: Delay timer runnning | 32061 | 132062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Delay
Alarm status: Delay timer runnning | 32062 | 132063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Delay
Alarm status: Delay timer runnning | 32063 | 132064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Delay
Alarm status: Delay timer runnning | 32064 | 132065 | 02 | Generator > Frequency protections > Under-frequency 2 > Delay
Alarm status: Delay timer runnning | 32065 | 132066 | 02 | Generator > Frequency protections > Under-frequency 1 > Delay
Alarm status: Delay timer runnning | 32066 | 132067 | 02 | Generator > Frequency protections > Over-frequency 2 > Delay
Alarm status: Delay timer runnning | 32067 | 132068 | 02 | Generator > Frequency protections > Over-frequency 1 > Delay
Alarm status: Delay timer runnning | 32068 | 132069 | 02 | Generator > Voltage protections > Under-voltage 2 > Delay
Alarm status: Delay timer runnning | 32069 | 132070 | 02 | Generator > Voltage protections > Under-voltage 1 > Delay
Alarm status: Delay timer runnning | 32070 | 132071 | 02 | Generator > Voltage protections > Over-voltage 2 > Delay
Alarm status: Delay timer runnning | 32071 | 132072 | 02 | Generator > Voltage protections > Over-voltage 1 > Delay
Alarm status: Delay timer runnning | 32072 | 132073 | 02 | Generator > Current protections > Directional over-current 2 > Delay
Alarm status: Delay timer runnning | 32073 | 132074 | 02 | Generator > Current protections > Directional over-current 1 > Delay
Alarm status: Delay timer runnning | 32074 | 132075 | 02 | Generator > Current protections > Fast over-current 2 > Delay
Alarm status: Delay timer runnning | 32075 | 132076 | 02 | Generator > Current protections > Fast over-current 1 > Delay
Alarm status: Delay timer runnning | 32076 | 132077 | 02 | Generator > Current protections > Over-current 2 > Delay
Alarm status: Delay timer runnning | 32077 | 132078 | 02 | Generator > Current protections > Over-current 1 > Delay
Alarm status: Delay timer runnning | 32095 | 132096 | 02 | Required IO card(s) not found > Delay
Alarm status: Delay timer runnning | 32096 | 132097 | 02 | Software mismatch on hardware module(s) > Delay
Alarm status: Delay timer runnning | 32100 | 132101 | 02 | AC configuration > Busbar > Multiple phase wire break > Delay
Alarm status: Delay timer runnning | 32101 | 132102 | 02 | AC configuration > Generator > Multiple phase wire break > Delay
Alarm status: Delay timer runnning | 32102 | 132103 | 02 | AC configuration > Busbar > L1 wire break > Delay
Alarm status: Delay timer runnning | 32103 | 132104 | 02 | AC configuration > Busbar > L2 wire break > Delay
Alarm status: Delay timer runnning | 32104 | 132105 | 02 | AC configuration > Busbar > L3 wire break > Delay
Alarm status: Delay timer runnning | 32105 | 132106 | 02 | AC configuration > Generator > L1 wire break > Delay
Alarm status: Delay timer runnning | 32106 | 132107 | 02 | AC configuration > Generator > L2 wire break > Delay
Alarm status: Delay timer runnning | 32107 | 132108 | 02 | AC configuration > Generator > L3 wire break > Delay
Alarm status: Delay timer runnning | 32116 | 132117 | 02 | Emergency stop > Delay
Alarm status: Delay timer runnning | 32117 | 132118 | 02 | PCM clock battery failure > Delay
Alarm status: Delay timer runnning | 32118 | 132119 | 02 | Controller temperature too high > Delay
Alarm status: Delay timer runnning | 32119 | 132120 | 02 | Power supply > PSM 1 > High voltage alarm > Delay
Alarm status: Delay timer runnning | 32120 | 132121 | 02 | Power supply > PSM 1 > Low voltage alarm > Delay
Alarm status: Delay timer runnning | 32121 | 132122 | 02 | Power supply > PSM 2 > High voltage alarm > Delay
Alarm status: Delay timer runnning | 32122 | 132123 | 02 | Power supply > PSM 2 > Low voltage alarm > Delay
Alarm status: Delay timer runnning | 32123 | 132124 | 02 | Power supply > PSM 3 > High voltage alarm > Delay
Alarm status: Delay timer runnning | 32124 | 132125 | 02 | Power supply > PSM 3 > Low voltage alarm > Delay
Alarm status: Delay timer runnning | 32125 | 132126 | 02 | Power supply > PSM 4 > High voltage alarm > Delay
Alarm status: Delay timer runnning | 32126 | 132127 | 02 | Power supply > PSM 4 > Low voltage alarm > Delay
Alarm status: Delay timer runnning | 32226 | 132227 | 02 | Non-essential load trip > Trip 1 > Over-current > Delay
Alarm status: Delay timer runnning | 32227 | 132228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > Delay
Alarm status: Delay timer runnning | 32228 | 132229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > Delay
Alarm status: Delay timer runnning | 32229 | 132230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > Delay
Alarm status: Delay timer runnning | 32230 | 132231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > Delay
Alarm status: Delay timer runnning | 32231 | 132232 | 02 | Non-essential load trip > Trip 2 > Over-current > Delay
Alarm status: Delay timer runnning | 32232 | 132233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > Delay
Alarm status: Delay timer runnning | 32233 | 132234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > Delay
Alarm status: Delay timer runnning | 32234 | 132235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > Delay
Alarm status: Delay timer runnning | 32235 | 132236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > Delay
Alarm status: Delay timer runnning | 32236 | 132237 | 02 | Non-essential load trip > Trip 3 > Over-current > Delay
Alarm status: Delay timer runnning | 32237 | 132238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > Delay
Alarm status: Delay timer runnning | 32238 | 132239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > Delay
Alarm status: Delay timer runnning | 32239 | 132240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > Delay
Alarm status: Delay timer runnning | 32240 | 132241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > Delay
Alarm status: Delay timer runnning | 32246 | 132247 | 02 | Utility > Network > Modbus communication timeout > Delay
Alarm status: Delay timer runnning | 33500 | 133501 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33501 | 133502 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33502 | 133503 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33503 | 133504 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33504 | 133505 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33505 | 133506 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33506 | 133507 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33507 | 133508 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33508 | 133509 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33509 | 133510 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33510 | 133511 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33511 | 133512 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33512 | 133513 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33513 | 133514 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33514 | 133515 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33515 | 133516 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33516 | 133517 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33517 | 133518 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33518 | 133519 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33519 | 133520 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33520 | 133521 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33521 | 133522 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33522 | 133523 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33523 | 133524 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33524 | 133525 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33525 | 133526 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33526 | 133527 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33527 | 133528 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33528 | 133529 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33529 | 133530 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33530 | 133531 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33531 | 133532 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33532 | 133533 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33533 | 133534 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33534 | 133535 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33535 | 133536 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33536 | 133537 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33537 | 133538 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33538 | 133539 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33539 | 133540 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33540 | 133541 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33541 | 133542 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33542 | 133543 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33543 | 133544 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33544 | 133545 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33545 | 133546 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33546 | 133547 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33547 | 133548 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33548 | 133549 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer runnning | 33549 | 133550 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 34016 | 134017 | 02 | Breakers > Generator breaker > Closing failure > Delay
Alarm status: Delay timer expired | 34017 | 134018 | 02 | Breakers > Generator breaker > Opening failure > Delay
Alarm status: Delay timer expired | 34018 | 134019 | 02 | Breakers > Generator breaker > Position failure > Delay
Alarm status: Delay timer expired | 34019 | 134020 | 02 | Breakers > Generator breaker > Configuration failure > Delay
Alarm status: Delay timer expired | 34020 | 134021 | 02 | Breakers > Generator breaker > Synchronisation failure > Delay
Alarm status: Delay timer expired | 34022 | 134023 | 02 | Breakers > Generator breaker > Tripped (external) > Delay
Alarm status: Delay timer expired | 34032 | 134033 | 02 | Synchronisation > Alarms > Vector mismatch > Delay
Alarm status: Delay timer expired | 34037 | 134038 | 02 | AC configuration > Busbar > Phase sequence error > Delay
Alarm status: Delay timer expired | 34038 | 134039 | 02 | AC configuration > Generator > Phase sequence error > Delay
Alarm status: Delay timer expired | 34039 | 134040 | 02 | AC configuration > Generator > Voltage or frequency not OK > Delay
Alarm status: Delay timer expired | 34040 | 134041 | 02 | Generator > Current protections > Zero sequence current > Delay
Alarm status: Delay timer expired | 34041 | 134042 | 02 | Generator > Voltage protections > Zero sequence voltage > Delay
Alarm status: Delay timer expired | 34042 | 134043 | 02 | Generator > Current protections > Negative sequence current > Delay
Alarm status: Delay timer expired | 34043 | 134044 | 02 | Generator > Voltage protections > Negative sequence voltage > Delay
Alarm status: Delay timer expired | 34044 | 134045 | 02 | Generator > Current protections > Current unbalance (nominal calc) > Delay
Alarm status: Delay timer expired | 34045 | 134046 | 02 | Generator > Current protections > Current unbalance (average calc) > Delay
Alarm status: Delay timer expired | 34046 | 134047 | 02 | Generator > Voltage protections > Voltage unbalance > Delay
Alarm status: Delay timer expired | 34047 | 134048 | 02 | Busbar > Voltage protections > Voltage unbalance > Delay
Alarm status: Delay timer expired | 34048 | 134049 | 02 | Generator > Reactive power protections > Reactive power import 2 > Delay
Alarm status: Delay timer expired | 34049 | 134050 | 02 | Generator > Reactive power protections > Reactive power import 1 > Delay
Alarm status: Delay timer expired | 34050 | 134051 | 02 | Generator > Reactive power protections > Reactive power export 2 > Delay
Alarm status: Delay timer expired | 34051 | 134052 | 02 | Generator > Reactive power protections > Reactive power export 1 > Delay
Alarm status: Delay timer expired | 34052 | 134053 | 02 | Generator > Power protections > Reverse power 2 > Delay
Alarm status: Delay timer expired | 34053 | 134054 | 02 | Generator > Power protections > Reverse power 1 > Delay
Alarm status: Delay timer expired | 34054 | 134055 | 02 | Generator > Power protections > Overload 2 > Delay
Alarm status: Delay timer expired | 34055 | 134056 | 02 | Generator > Power protections > Overload 1 > Delay
Alarm status: Delay timer expired | 34056 | 134057 | 02 | Busbar > Frequency protections > Under-frequency 2 > Delay
Alarm status: Delay timer expired | 34057 | 134058 | 02 | Busbar > Frequency protections > Under-frequency 1 > Delay
Alarm status: Delay timer expired | 34058 | 134059 | 02 | Busbar > Frequency protections > Over-frequency 2 > Delay
Alarm status: Delay timer expired | 34059 | 134060 | 02 | Busbar > Frequency protections > Over-frequency 1 > Delay
Alarm status: Delay timer expired | 34060 | 134061 | 02 | Busbar > Voltage protections > Under-voltage 2 > Delay
Alarm status: Delay timer expired | 34061 | 134062 | 02 | Busbar > Voltage protections > Under-voltage 1 > Delay
Alarm status: Delay timer expired | 34062 | 134063 | 02 | Busbar > Voltage protections > Over-voltage 2 > Delay
Alarm status: Delay timer expired | 34063 | 134064 | 02 | Busbar > Voltage protections > Over-voltage 1 > Delay
Alarm status: Delay timer expired | 34064 | 134065 | 02 | Generator > Frequency protections > Under-frequency 2 > Delay
Alarm status: Delay timer expired | 34065 | 134066 | 02 | Generator > Frequency protections > Under-frequency 1 > Delay
Alarm status: Delay timer expired | 34066 | 134067 | 02 | Generator > Frequency protections > Over-frequency 2 > Delay
Alarm status: Delay timer expired | 34067 | 134068 | 02 | Generator > Frequency protections > Over-frequency 1 > Delay
Alarm status: Delay timer expired | 34068 | 134069 | 02 | Generator > Voltage protections > Under-voltage 2 > Delay
Alarm status: Delay timer expired | 34069 | 134070 | 02 | Generator > Voltage protections > Under-voltage 1 > Delay
Alarm status: Delay timer expired | 34070 | 134071 | 02 | Generator > Voltage protections > Over-voltage 2 > Delay
Alarm status: Delay timer expired | 34071 | 134072 | 02 | Generator > Voltage protections > Over-voltage 1 > Delay
Alarm status: Delay timer expired | 34072 | 134073 | 02 | Generator > Current protections > Directional over-current 2 > Delay
Alarm status: Delay timer expired | 34073 | 134074 | 02 | Generator > Current protections > Directional over-current 1 > Delay
Alarm status: Delay timer expired | 34074 | 134075 | 02 | Generator > Current protections > Fast over-current 2 > Delay
Alarm status: Delay timer expired | 34075 | 134076 | 02 | Generator > Current protections > Fast over-current 1 > Delay
Alarm status: Delay timer expired | 34076 | 134077 | 02 | Generator > Current protections > Over-current 2 > Delay
Alarm status: Delay timer expired | 34077 | 134078 | 02 | Generator > Current protections > Over-current 1 > Delay
Alarm status: Delay timer expired | 34095 | 134096 | 02 | Required IO card(s) not found > Delay
Alarm status: Delay timer expired | 34096 | 134097 | 02 | Software mismatch on hardware module(s) > Delay
Alarm status: Delay timer expired | 34100 | 134101 | 02 | AC configuration > Busbar > Multiple phase wire break > Delay
Alarm status: Delay timer expired | 34101 | 134102 | 02 | AC configuration > Generator > Multiple phase wire break > Delay
Alarm status: Delay timer expired | 34102 | 134103 | 02 | AC configuration > Busbar > L1 wire break > Delay
Alarm status: Delay timer expired | 34103 | 134104 | 02 | AC configuration > Busbar > L2 wire break > Delay
Alarm status: Delay timer expired | 34104 | 134105 | 02 | AC configuration > Busbar > L3 wire break > Delay
Alarm status: Delay timer expired | 34105 | 134106 | 02 | AC configuration > Generator > L1 wire break > Delay
Alarm status: Delay timer expired | 34106 | 134107 | 02 | AC configuration > Generator > L2 wire break > Delay
Alarm status: Delay timer expired | 34107 | 134108 | 02 | AC configuration > Generator > L3 wire break > Delay
Alarm status: Delay timer expired | 34116 | 134117 | 02 | Emergency stop > Delay
Alarm status: Delay timer expired | 34117 | 134118 | 02 | PCM clock battery failure > Delay
Alarm status: Delay timer expired | 34118 | 134119 | 02 | Controller temperature too high > Delay
Alarm status: Delay timer expired | 34119 | 134120 | 02 | Power supply > PSM 1 > High voltage alarm > Delay
Alarm status: Delay timer expired | 34120 | 134121 | 02 | Power supply > PSM 1 > Low voltage alarm > Delay
Alarm status: Delay timer expired | 34121 | 134122 | 02 | Power supply > PSM 2 > High voltage alarm > Delay
Alarm status: Delay timer expired | 34122 | 134123 | 02 | Power supply > PSM 2 > Low voltage alarm > Delay
Alarm status: Delay timer expired | 34123 | 134124 | 02 | Power supply > PSM 3 > High voltage alarm > Delay
Alarm status: Delay timer expired | 34124 | 134125 | 02 | Power supply > PSM 3 > Low voltage alarm > Delay
Alarm status: Delay timer expired | 34125 | 134126 | 02 | Power supply > PSM 4 > High voltage alarm > Delay
Alarm status: Delay timer expired | 34126 | 134127 | 02 | Power supply > PSM 4 > Low voltage alarm > Delay
Alarm status: Delay timer expired | 34226 | 134227 | 02 | Non-essential load trip > Trip 1 > Over-current > Delay
Alarm status: Delay timer expired | 34227 | 134228 | 02 | Non-essential load trip > Trip 1 > Under-frequency > Delay
Alarm status: Delay timer expired | 34228 | 134229 | 02 | Non-essential load trip > Trip 1 > Overload 1 > Delay
Alarm status: Delay timer expired | 34229 | 134230 | 02 | Non-essential load trip > Trip 1 > Overload 2 > Delay
Alarm status: Delay timer expired | 34230 | 134231 | 02 | Non-essential load trip > Trip 1 > Reactive overload > Delay
Alarm status: Delay timer expired | 34231 | 134232 | 02 | Non-essential load trip > Trip 2 > Over-current > Delay
Alarm status: Delay timer expired | 34232 | 134233 | 02 | Non-essential load trip > Trip 2 > Under-frequency > Delay
Alarm status: Delay timer expired | 34233 | 134234 | 02 | Non-essential load trip > Trip 2 > Overload 1 > Delay
Alarm status: Delay timer expired | 34234 | 134235 | 02 | Non-essential load trip > Trip 2 > Overload 2 > Delay
Alarm status: Delay timer expired | 34235 | 134236 | 02 | Non-essential load trip > Trip 2 > Reactive overload > Delay
Alarm status: Delay timer expired | 34236 | 134237 | 02 | Non-essential load trip > Trip 3 > Over-current > Delay
Alarm status: Delay timer expired | 34237 | 134238 | 02 | Non-essential load trip > Trip 3 > Under-frequency > Delay
Alarm status: Delay timer expired | 34238 | 134239 | 02 | Non-essential load trip > Trip 3 > Overload 1 > Delay
Alarm status: Delay timer expired | 34239 | 134240 | 02 | Non-essential load trip > Trip 3 > Overload 2 > Delay
Alarm status: Delay timer expired | 34240 | 134241 | 02 | Non-essential load trip > Trip 3 > Reactive overload > Delay
Alarm status: Delay timer expired | 34244 | 134245 | 02 | Different single-line configurations > Delay
Alarm status: Delay timer expired | 34246 | 134247 | 02 | Utility > Network > Modbus communication timeout > Delay
Alarm status: Delay timer expired | 35500 | 135501 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35501 | 135502 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35502 | 135503 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35503 | 135504 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35504 | 135505 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35505 | 135506 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35506 | 135507 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35507 | 135508 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35508 | 135509 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35509 | 135510 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35510 | 135511 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35511 | 135512 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35512 | 135513 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35513 | 135514 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35514 | 135515 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35515 | 135516 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35516 | 135517 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35517 | 135518 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35518 | 135519 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35519 | 135520 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35520 | 135521 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35521 | 135522 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35522 | 135523 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35523 | 135524 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35524 | 135525 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35525 | 135526 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35526 | 135527 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35527 | 135528 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35528 | 135529 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35529 | 135530 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35530 | 135531 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35531 | 135532 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35532 | 135533 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35533 | 135534 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35534 | 135535 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35535 | 135536 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35536 | 135537 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35537 | 135538 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35538 | 135539 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35539 | 135540 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35540 | 135541 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35541 | 135542 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35542 | 135543 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35543 | 135544 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35544 | 135545 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35545 | 135546 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35546 | 135547 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35547 | 135548 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35548 | 135549 | 02 | Digital custom alarm > Delay
Alarm status: Delay timer expired | 35549 | 135550 | 02 | Digital custom alarm > Delay
General parameter: Delay timer running | 46031 | 146032 | 02 | Breakers > Generator breaker > Configuration > Pulse time ON
General parameter: Delay timer running | 46032 | 146033 | 02 | Breakers > Generator breaker > Configuration > Pulse time OFF
General parameter: Delay timer running | 46033 | 146034 | 02 | Breakers > Generator breaker > Configuration > Spring load time
General parameter: Delay timer running | 46125 | 146126 | 02 | Generator > Energy counters > Active power export > Pulse length
General parameter: Delay timer running | 46127 | 146128 | 02 | Generator > Energy counters > Reactive power export > Pulse length
General parameter: Delay timer running | 46144 | 146145 | 02 | AC configuration > Busbar > Voltage and frequency OK > Frequency and voltage OK
General parameter: Delay timer running | 46152 | 146153 | 02 | AC configuration > Busbar > Blackout detection > Blackout delay
General parameter: Delay timer running | 46153 | 146154 | 02 | AC configuration > Generator > Voltage and frequency OK > Frequency and voltage OK
General parameter: Delay timer running | 46309 | 146310 | 02 | Alarm horn > Horn 1 > Minimum down time
General parameter: Delay timer running | 46310 | 146311 | 02 | Alarm horn > Horn 1 > Minimum up time
General parameter: Delay timer running | 46313 | 146314 | 02 | Alarm horn > Horn 2 > Minimum down time
General parameter: Delay timer running | 46314 | 146315 | 02 | Alarm horn > Horn 2 > Minimum up time
General parameter: Delay timer running | 46317 | 146318 | 02 | Alarm horn > Horn 3 > Minimum down time
General parameter: Delay timer running | 46318 | 146319 | 02 | Alarm horn > Horn 3 > Minimum up time
Note on A4: Maarten van Bemmel: More information about each function group is available in the description sheet.
Note on D4: Maarten van Bemmel: 02 - Read single or multiple
Note on E4: Maarten van Bemmel: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.

## Holding register (03;06;16)
Holding register (03; 06; 16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10-x)
Alarm parameter: Set point | 20032 |  | 420033 | 03; 06; 16 | Synchronisation > Alarms > Vector mismatch > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20040 |  | 420041 | 03; 06; 16 | Generator > Current protections > Zero sequence current > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20041 |  | 420042 | 03; 06; 16 | Generator > Voltage protections > Zero sequence voltage > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20042 |  | 420043 | 03; 06; 16 | Generator > Current protections > Negative sequence current > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20043 |  | 420044 | 03; 06; 16 | Generator > Voltage protections > Negative sequence voltage > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20044 |  | 420045 | 03; 06; 16 | Generator > Current protections > Current unbalance (nominal calc) > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20045 |  | 420046 | 03; 06; 16 | Generator > Current protections > Current unbalance (average calc) > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20046 |  | 420047 | 03; 06; 16 | Generator > Voltage protections > Voltage unbalance > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20047 |  | 420048 | 03; 06; 16 | Busbar > Voltage protections > Voltage unbalance > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20048 |  | 420049 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20049 |  | 420050 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20050 |  | 420051 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20051 |  | 420052 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20052 |  | 420053 | 03; 06; 16 | Generator > Power protections > Reverse power 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20053 |  | 420054 | 03; 06; 16 | Generator > Power protections > Reverse power 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20054 |  | 420055 | 03; 06; 16 | Generator > Power protections > Overload 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20055 |  | 420056 | 03; 06; 16 | Generator > Power protections > Overload 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20056 |  | 420057 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20057 |  | 420058 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20058 |  | 420059 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20059 |  | 420060 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20060 |  | 420061 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20061 |  | 420062 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20062 |  | 420063 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20063 |  | 420064 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20064 |  | 420065 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20065 |  | 420066 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20066 |  | 420067 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20067 |  | 420068 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20068 |  | 420069 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20069 |  | 420070 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20070 |  | 420071 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20071 |  | 420072 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20072 |  | 420073 | 03; 06; 16 | Generator > Current protections > Directional over-current 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20073 |  | 420074 | 03; 06; 16 | Generator > Current protections > Directional over-current 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20074 |  | 420075 | 03; 06; 16 | Generator > Current protections > Fast over-current 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20075 |  | 420076 | 03; 06; 16 | Generator > Current protections > Fast over-current 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20076 |  | 420077 | 03; 06; 16 | Generator > Current protections > Over-current 2 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20077 |  | 420078 | 03; 06; 16 | Generator > Current protections > Over-current 1 > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20119 |  | 420120 | 03; 06; 16 | Power supply > PSM 1 > High voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20120 |  | 420121 | 03; 06; 16 | Power supply > PSM 1 > Low voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20121 |  | 420122 | 03; 06; 16 | Power supply > PSM 2 > High voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20122 |  | 420123 | 03; 06; 16 | Power supply > PSM 2 > Low voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20123 |  | 420124 | 03; 06; 16 | Power supply > PSM 3 > High voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20124 |  | 420125 | 03; 06; 16 | Power supply > PSM 3 > Low voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20125 |  | 420126 | 03; 06; 16 | Power supply > PSM 4 > High voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20126 |  | 420127 | 03; 06; 16 | Power supply > PSM 4 > Low voltage alarm > Set point | INT16 | AB | 1
Alarm parameter: Set point | 20226 |  | 420227 | 03; 06; 16 | Non-essential load trip > Trip 1 > Over-current > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20227 |  | 420228 | 03; 06; 16 | Non-essential load trip > Trip 1 > Under-frequency > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20228 |  | 420229 | 03; 06; 16 | Non-essential load trip > Trip 1 > Overload 1 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20229 |  | 420230 | 03; 06; 16 | Non-essential load trip > Trip 1 > Overload 2 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20230 |  | 420231 | 03; 06; 16 | Non-essential load trip > Trip 1 > Reactive overload > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20231 |  | 420232 | 03; 06; 16 | Non-essential load trip > Trip 2 > Over-current > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20232 |  | 420233 | 03; 06; 16 | Non-essential load trip > Trip 2 > Under-frequency > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20233 |  | 420234 | 03; 06; 16 | Non-essential load trip > Trip 2 > Overload 1 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20234 |  | 420235 | 03; 06; 16 | Non-essential load trip > Trip 2 > Overload 2 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20235 |  | 420236 | 03; 06; 16 | Non-essential load trip > Trip 2 > Reactive overload > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20236 |  | 420237 | 03; 06; 16 | Non-essential load trip > Trip 3 > Over-current > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20237 |  | 420238 | 03; 06; 16 | Non-essential load trip > Trip 3 > Under-frequency > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20238 |  | 420239 | 03; 06; 16 | Non-essential load trip > Trip 3 > Overload 1 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20239 |  | 420240 | 03; 06; 16 | Non-essential load trip > Trip 3 > Overload 2 > Set point | INT16 | AB | 0
Alarm parameter: Set point | 20240 |  | 420241 | 03; 06; 16 | Non-essential load trip > Trip 3 > Reactive overload > Set point | INT16 | AB | 0
Alarm parameter: Reset ratio | 22040 |  | 422041 | 03; 06; 16 | Generator > Current protections > Zero sequence current > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22041 |  | 422042 | 03; 06; 16 | Generator > Voltage protections > Zero sequence voltage > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22042 |  | 422043 | 03; 06; 16 | Generator > Current protections > Negative sequence current > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22043 |  | 422044 | 03; 06; 16 | Generator > Voltage protections > Negative sequence voltage > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22044 |  | 422045 | 03; 06; 16 | Generator > Current protections > Current unbalance (nominal calc) > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22045 |  | 422046 | 03; 06; 16 | Generator > Current protections > Current unbalance (average calc) > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22046 |  | 422047 | 03; 06; 16 | Generator > Voltage protections > Voltage unbalance > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22047 |  | 422048 | 03; 06; 16 | Busbar > Voltage protections > Voltage unbalance > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22048 |  | 422049 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22049 |  | 422050 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22050 |  | 422051 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22051 |  | 422052 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22052 |  | 422053 | 03; 06; 16 | Generator > Power protections > Reverse power 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22053 |  | 422054 | 03; 06; 16 | Generator > Power protections > Reverse power 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22054 |  | 422055 | 03; 06; 16 | Generator > Power protections > Overload 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22055 |  | 422056 | 03; 06; 16 | Generator > Power protections > Overload 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22056 |  | 422057 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22057 |  | 422058 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22058 |  | 422059 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22059 |  | 422060 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22060 |  | 422061 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22061 |  | 422062 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22062 |  | 422063 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22063 |  | 422064 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22064 |  | 422065 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22065 |  | 422066 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22066 |  | 422067 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22067 |  | 422068 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22068 |  | 422069 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22069 |  | 422070 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22070 |  | 422071 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22071 |  | 422072 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22072 |  | 422073 | 03; 06; 16 | Generator > Current protections > Directional over-current 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22073 |  | 422074 | 03; 06; 16 | Generator > Current protections > Directional over-current 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22074 |  | 422075 | 03; 06; 16 | Generator > Current protections > Fast over-current 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22075 |  | 422076 | 03; 06; 16 | Generator > Current protections > Fast over-current 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22076 |  | 422077 | 03; 06; 16 | Generator > Current protections > Over-current 2 > Reset ratio | INT16 | AB | 1
Alarm parameter: Reset ratio | 22077 |  | 422078 | 03; 06; 16 | Generator > Current protections > Over-current 1 > Reset ratio | INT16 | AB | 1
Alarm parameter: Delay | 24016 |  | 424017 | 03; 06; 16 | Breakers > Generator breaker > Closing failure > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24017 |  | 424018 | 03; 06; 16 | Breakers > Generator breaker > Opening failure > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24018 |  | 424019 | 03; 06; 16 | Breakers > Generator breaker > Position failure > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24019 |  | 424020 | 03; 06; 16 | Breakers > Generator breaker > Configuration failure > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24020 |  | 424021 | 03; 06; 16 | Breakers > Generator breaker > Synchronisation failure > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24022 |  | 424023 | 03; 06; 16 | Breakers > Generator breaker > Tripped (external) > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24032 |  | 424033 | 03; 06; 16 | Synchronisation > Alarms > Vector mismatch > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24037 |  | 424038 | 03; 06; 16 | AC configuration > Busbar > Phase sequence error > Delay | INT16 | AB | 0
Alarm parameter: Delay | 24038 |  | 424039 | 03; 06; 16 | AC configuration > Generator > Phase sequence error > Delay | INT16 | AB | 0
Alarm parameter: Delay | 24039 |  | 424040 | 03; 06; 16 | AC configuration > Generator > Voltage or frequency not OK > Delay | INT16 | AB | 0
Alarm parameter: Delay | 24040 |  | 424041 | 03; 06; 16 | Generator > Current protections > Zero sequence current > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24041 |  | 424042 | 03; 06; 16 | Generator > Voltage protections > Zero sequence voltage > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24042 |  | 424043 | 03; 06; 16 | Generator > Current protections > Negative sequence current > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24043 |  | 424044 | 03; 06; 16 | Generator > Voltage protections > Negative sequence voltage > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24044 |  | 424045 | 03; 06; 16 | Generator > Current protections > Current unbalance (nominal calc) > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24045 |  | 424046 | 03; 06; 16 | Generator > Current protections > Current unbalance (average calc) > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24046 |  | 424047 | 03; 06; 16 | Generator > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24047 |  | 424048 | 03; 06; 16 | Busbar > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24048 |  | 424049 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24049 |  | 424050 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24050 |  | 424051 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24051 |  | 424052 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24052 |  | 424053 | 03; 06; 16 | Generator > Power protections > Reverse power 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24053 |  | 424054 | 03; 06; 16 | Generator > Power protections > Reverse power 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24054 |  | 424055 | 03; 06; 16 | Generator > Power protections > Overload 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24055 |  | 424056 | 03; 06; 16 | Generator > Power protections > Overload 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24056 |  | 424057 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24057 |  | 424058 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24058 |  | 424059 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24059 |  | 424060 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24060 |  | 424061 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24061 |  | 424062 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24062 |  | 424063 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24063 |  | 424064 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24064 |  | 424065 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24065 |  | 424066 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24066 |  | 424067 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24067 |  | 424068 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24068 |  | 424069 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24069 |  | 424070 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24070 |  | 424071 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24071 |  | 424072 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24072 |  | 424073 | 03; 06; 16 | Generator > Current protections > Directional over-current 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24073 |  | 424074 | 03; 06; 16 | Generator > Current protections > Directional over-current 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24074 |  | 424075 | 03; 06; 16 | Generator > Current protections > Fast over-current 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24075 |  | 424076 | 03; 06; 16 | Generator > Current protections > Fast over-current 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24076 |  | 424077 | 03; 06; 16 | Generator > Current protections > Over-current 2 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24077 |  | 424078 | 03; 06; 16 | Generator > Current protections > Over-current 1 > Delay | INT16 | AB | 2
Alarm parameter: Delay | 24100 |  | 424101 | 03; 06; 16 | AC configuration > Busbar > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24101 |  | 424102 | 03; 06; 16 | AC configuration > Generator > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24102 |  | 424103 | 03; 06; 16 | AC configuration > Busbar > L1 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24103 |  | 424104 | 03; 06; 16 | AC configuration > Busbar > L2 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24104 |  | 424105 | 03; 06; 16 | AC configuration > Busbar > L3 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24105 |  | 424106 | 03; 06; 16 | AC configuration > Generator > L1 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24106 |  | 424107 | 03; 06; 16 | AC configuration > Generator > L2 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24107 |  | 424108 | 03; 06; 16 | AC configuration > Generator > L3 wire break > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24119 |  | 424120 | 03; 06; 16 | Power supply > PSM 1 > High voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24120 |  | 424121 | 03; 06; 16 | Power supply > PSM 1 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24121 |  | 424122 | 03; 06; 16 | Power supply > PSM 2 > High voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24122 |  | 424123 | 03; 06; 16 | Power supply > PSM 2 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24123 |  | 424124 | 03; 06; 16 | Power supply > PSM 3 > High voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24124 |  | 424125 | 03; 06; 16 | Power supply > PSM 3 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24125 |  | 424126 | 03; 06; 16 | Power supply > PSM 4 > High voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24126 |  | 424127 | 03; 06; 16 | Power supply > PSM 4 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24226 |  | 424227 | 03; 06; 16 | Non-essential load trip > Trip 1 > Over-current > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24227 |  | 424228 | 03; 06; 16 | Non-essential load trip > Trip 1 > Under-frequency > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24228 |  | 424229 | 03; 06; 16 | Non-essential load trip > Trip 1 > Overload 1 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24229 |  | 424230 | 03; 06; 16 | Non-essential load trip > Trip 1 > Overload 2 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24230 |  | 424231 | 03; 06; 16 | Non-essential load trip > Trip 1 > Reactive overload > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24231 |  | 424232 | 03; 06; 16 | Non-essential load trip > Trip 2 > Over-current > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24232 |  | 424233 | 03; 06; 16 | Non-essential load trip > Trip 2 > Under-frequency > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24233 |  | 424234 | 03; 06; 16 | Non-essential load trip > Trip 2 > Overload 1 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24234 |  | 424235 | 03; 06; 16 | Non-essential load trip > Trip 2 > Overload 2 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24235 |  | 424236 | 03; 06; 16 | Non-essential load trip > Trip 2 > Reactive overload > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24236 |  | 424237 | 03; 06; 16 | Non-essential load trip > Trip 3 > Over-current > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24237 |  | 424238 | 03; 06; 16 | Non-essential load trip > Trip 3 > Under-frequency > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24238 |  | 424239 | 03; 06; 16 | Non-essential load trip > Trip 3 > Overload 1 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24239 |  | 424240 | 03; 06; 16 | Non-essential load trip > Trip 3 > Overload 2 > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24240 |  | 424241 | 03; 06; 16 | Non-essential load trip > Trip 3 > Reactive overload > Delay | INT16 | AB | 1
Alarm parameter: Delay | 24246 |  | 424247 | 03; 06; 16 | Utility > Network > Modbus communication timeout > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25500 |  | 425501 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25501 |  | 425502 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25502 |  | 425503 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25503 |  | 425504 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25504 |  | 425505 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25505 |  | 425506 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25506 |  | 425507 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25507 |  | 425508 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25508 |  | 425509 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25509 |  | 425510 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25510 |  | 425511 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25511 |  | 425512 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25512 |  | 425513 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25513 |  | 425514 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25514 |  | 425515 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25515 |  | 425516 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25516 |  | 425517 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25517 |  | 425518 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25518 |  | 425519 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25519 |  | 425520 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25520 |  | 425521 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25521 |  | 425522 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25522 |  | 425523 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25523 |  | 425524 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25524 |  | 425525 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25525 |  | 425526 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25526 |  | 425527 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25527 |  | 425528 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25528 |  | 425529 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25529 |  | 425530 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25530 |  | 425531 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25531 |  | 425532 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25532 |  | 425533 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25533 |  | 425534 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25534 |  | 425535 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25535 |  | 425536 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25536 |  | 425537 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25537 |  | 425538 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25538 |  | 425539 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25539 |  | 425540 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25540 |  | 425541 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25541 |  | 425542 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25542 |  | 425543 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25543 |  | 425544 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25544 |  | 425545 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25545 |  | 425546 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25546 |  | 425547 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25547 |  | 425548 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25548 |  | 425549 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Delay | 25549 |  | 425550 | 03; 06; 16 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm parameter: Inhibit | 30040 |  | 430041 | 03; 06; 16 | Breakers > Generator breaker > Synchronisation failure > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30044 |  | 430045 | 03; 06; 16 | Breakers > Generator breaker > Tripped (external) > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30046 |  | 430047 | 03; 06; 16 | Breakers > Generator breaker > Short circuit > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30064 |  | 430065 | 03; 06; 16 | Synchronisation > Alarms > Vector mismatch > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30074 |  | 430075 | 03; 06; 16 | AC configuration > Busbar > Phase sequence error > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30076 |  | 430077 | 03; 06; 16 | AC configuration > Generator > Phase sequence error > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30078 |  | 430079 | 03; 06; 16 | AC configuration > Generator > Voltage or frequency not OK > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30080 |  | 430081 | 03; 06; 16 | Generator > Current protections > Zero sequence current > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30082 |  | 430083 | 03; 06; 16 | Generator > Voltage protections > Zero sequence voltage > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30084 |  | 430085 | 03; 06; 16 | Generator > Current protections > Negative sequence current > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30086 |  | 430087 | 03; 06; 16 | Generator > Voltage protections > Negative sequence voltage > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30088 |  | 430089 | 03; 06; 16 | Generator > Current protections > Current unbalance (nominal calc) > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30090 |  | 430091 | 03; 06; 16 | Generator > Current protections > Current unbalance (average calc) > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30092 |  | 430093 | 03; 06; 16 | Generator > Voltage protections > Voltage unbalance > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30094 |  | 430095 | 03; 06; 16 | Busbar > Voltage protections > Voltage unbalance > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30096 |  | 430097 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30098 |  | 430099 | 03; 06; 16 | Generator > Reactive power protections > Reactive power import 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30100 |  | 430101 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30102 |  | 430103 | 03; 06; 16 | Generator > Reactive power protections > Reactive power export 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30104 |  | 430105 | 03; 06; 16 | Generator > Power protections > Reverse power 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30106 |  | 430107 | 03; 06; 16 | Generator > Power protections > Reverse power 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30108 |  | 430109 | 03; 06; 16 | Generator > Power protections > Overload 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30110 |  | 430111 | 03; 06; 16 | Generator > Power protections > Overload 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30112 |  | 430113 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30114 |  | 430115 | 03; 06; 16 | Busbar > Frequency protections > Under-frequency 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30116 |  | 430117 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30118 |  | 430119 | 03; 06; 16 | Busbar > Frequency protections > Over-frequency 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30120 |  | 430121 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30122 |  | 430123 | 03; 06; 16 | Busbar > Voltage protections > Under-voltage 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30124 |  | 430125 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30126 |  | 430127 | 03; 06; 16 | Busbar > Voltage protections > Over-voltage 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30128 |  | 430129 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30130 |  | 430131 | 03; 06; 16 | Generator > Frequency protections > Under-frequency 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30132 |  | 430133 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30134 |  | 430135 | 03; 06; 16 | Generator > Frequency protections > Over-frequency 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30136 |  | 430137 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30138 |  | 430139 | 03; 06; 16 | Generator > Voltage protections > Under-voltage 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30140 |  | 430141 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30142 |  | 430143 | 03; 06; 16 | Generator > Voltage protections > Over-voltage 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30144 |  | 430145 | 03; 06; 16 | Generator > Current protections > Directional over-current 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30146 |  | 430147 | 03; 06; 16 | Generator > Current protections > Directional over-current 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30148 |  | 430149 | 03; 06; 16 | Generator > Current protections > Fast over-current 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30150 |  | 430151 | 03; 06; 16 | Generator > Current protections > Fast over-current 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30152 |  | 430153 | 03; 06; 16 | Generator > Current protections > Over-current 2 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30154 |  | 430155 | 03; 06; 16 | Generator > Current protections > Over-current 1 > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30156 |  | 430157 | 03; 06; 16 | Generator > Current protections > Inverse time over-current > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30158 |  | 430159 | 03; 06; 16 | 4th current input > Current protections > Earth inverse time over-current > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30160 |  | 430161 | 03; 06; 16 | 4th current input > Current protections > Neutral inverse time over-current > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30238 |  | 430239 | 03; 06; 16 | Power supply > PSM 1 > High voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30240 |  | 430241 | 03; 06; 16 | Power supply > PSM 1 > Low voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30242 |  | 430243 | 03; 06; 16 | Power supply > PSM 2 > High voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30244 |  | 430245 | 03; 06; 16 | Power supply > PSM 2 > Low voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30246 |  | 430247 | 03; 06; 16 | Power supply > PSM 3 > High voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30248 |  | 430249 | 03; 06; 16 | Power supply > PSM 3 > Low voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30250 |  | 430251 | 03; 06; 16 | Power supply > PSM 4 > High voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30252 |  | 430253 | 03; 06; 16 | Power supply > PSM 4 > Low voltage alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 30492 |  | 430493 | 03; 06; 16 | Utility > Network > Modbus communication timeout > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33000 |  | 433001 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33002 |  | 433003 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33004 |  | 433005 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33006 |  | 433007 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33008 |  | 433009 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33010 |  | 433011 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33012 |  | 433013 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33014 |  | 433015 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33016 |  | 433017 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33018 |  | 433019 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33020 |  | 433021 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33022 |  | 433023 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33024 |  | 433025 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33026 |  | 433027 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33028 |  | 433029 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33030 |  | 433031 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33032 |  | 433033 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33034 |  | 433035 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33036 |  | 433037 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33038 |  | 433039 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33040 |  | 433041 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33042 |  | 433043 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33044 |  | 433045 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33046 |  | 433047 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33048 |  | 433049 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33050 |  | 433051 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33052 |  | 433053 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33054 |  | 433055 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33056 |  | 433057 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33058 |  | 433059 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33060 |  | 433061 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33062 |  | 433063 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33064 |  | 433065 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33066 |  | 433067 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33068 |  | 433069 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33070 |  | 433071 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33072 |  | 433073 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33074 |  | 433075 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33076 |  | 433077 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33078 |  | 433079 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33080 |  | 433081 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33082 |  | 433083 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33084 |  | 433085 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33086 |  | 433087 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33088 |  | 433089 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33090 |  | 433091 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33092 |  | 433093 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33094 |  | 433095 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33096 |  | 433097 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Alarm parameter: Inhibit | 33098 |  | 433099 | 03; 06; 16 | Digital custom alarm > Inhibit | INT32 | ABCD
Note on A4: Maarten van Bemmel: More information about each function group is available in the description sheet.
Note on C4: Maarten van Bemmel: Bit location of the function in the associated Modbus address.
Note on E4: Maarten van Bemmel: 03 - Read single or multiple 06 - Write single 16 - Write multiple
Note on F4: Maarten van Bemmel: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.
Note on G4: Maarten van Bemmel: Find the units of the associated function in the Designer's handbook.
Note on H4: Maarten van Bemmel: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I4: Maarten van Bemmel: Example: Scaling = 1 Read data = 266 Actual value = 26,6

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10-x)
[Controlled equiptment] ACM measurements | 1000 |  | 301001 | 04 | Generator > Voltage (V) > Generator ¦ L1-N | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1001 |  | 301002 | 04 | Generator > Voltage (V) > Generator ¦ L2-N | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1002 |  | 301003 | 04 | Generator > Voltage (V) > Generator ¦ L3-N | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1003 |  | 301004 | 04 | Generator > Voltage (V) > Generator ¦ N | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1004 |  | 301005 | 04 | Generator > Voltage (V) > Generator ¦ L-N min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1005 |  | 301006 | 04 | Generator > Voltage (V) > Generator ¦ L-N max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1006 |  | 301007 | 04 | Generator > Voltage (V) > Generator ¦ L-N unbalanced | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1007 |  | 301008 | 04 | Generator > Voltage (V) > Generator ¦ L1-L2 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1008 |  | 301009 | 04 | Generator > Voltage (V) > Generator ¦ L2-L3 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1009 |  | 301010 | 04 | Generator > Voltage (V) > Generator ¦ L3-L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1010 |  | 301011 | 04 | Generator > Voltage (V) > Generator ¦ L-L min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1011 |  | 301012 | 04 | Generator > Voltage (V) > Generator ¦ L-L max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1012 |  | 301013 | 04 | Generator > Voltage (V) > Generator ¦ L-L unbalanced | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1013 |  | 301014 | 04 | Generator > Frequency (f) (from voltage) > Generator ¦ L1 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1014 |  | 301015 | 04 | Generator > Frequency (f) (from voltage) > Generator ¦ L2 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1015 |  | 301016 | 04 | Generator > Frequency (f) (from voltage) > Generator ¦ L3 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1016 |  | 301017 | 04 | Generator > Frequency (f) (from voltage) > Generator ¦ Min. | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1017 |  | 301018 | 04 | Generator > Frequency (f) (from voltage) > Generator ¦ Max. | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1018 |  | 301019 | 04 | Generator > Frequency (f) (from current) > Generator ¦ Min. | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1019 |  | 301020 | 04 | Generator > Frequency (f) (from current) > Generator ¦ Max. | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1020 |  | 301021 | 04 | Generator > Phase angle > Generator ¦ Phase angle L1-L2 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1021 |  | 301022 | 04 | Generator > Phase angle > Generator ¦ Phase angle L2-L3 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1022 |  | 301023 | 04 | Generator > Phase angle > Generator ¦ Phase angle L3-L1 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1023 |  | 301024 | 04 | Generator > Phase angle > Generator ¦ A-B phase angle L1 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1024 |  | 301025 | 04 | Generator > Phase angle > Generator ¦ A-B phase angle L2 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1025 |  | 301026 | 04 | Generator > Phase angle > Generator ¦ A-B phase angle L3 | INT16 | AB | 1
[Controlled equiptment] ACM measurements | 1026 |  | 301027 | 04 | Generator > Current (I) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1027 |  | 301028 | 04 | Generator > Current (I) > Generator ¦ L2 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1028 |  | 301029 | 04 | Generator > Current (I) > Generator ¦ L3 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1029 |  | 301030 | 04 | Generator > Current (I) > Generator ¦ N | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1030 |  | 301031 | 04 | Generator > Current (I) > Generator ¦ Min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1031 |  | 301032 | 04 | Generator > Current (I) > Generator ¦ Max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1032 |  | 301033 | 04 | Generator > Current (I) > Generator ¦ Unbalanced nominal | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1033 |  | 301034 | 04 | Generator > Current (I) > Generator ¦ Unbalanced average | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1034 |  | 301035 | 04 | Generator > Frequency (f) (from current) > Generator ¦ L1 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1035 |  | 301036 | 04 | Generator > Frequency (f) (from current) > Generator ¦ L2 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1036 |  | 301037 | 04 | Generator > Frequency (f) (from current) > Generator ¦ L3 | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1037 |  | 301038 | 04 | Generator > Power (P) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1038 |  | 301039 | 04 | Generator > Power (P) > Generator ¦ L2 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1039 |  | 301040 | 04 | Generator > Power (P) > Generator ¦ L3 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1040 |  | 301041 | 04 | Generator > Power (P) > Generator ¦ Min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1041 |  | 301042 | 04 | Generator > Power (P) > Generator ¦ Max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1042 |  | 301043 | 04 | Generator > Power (P) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1043 |  | 301044 | 04 | Generator > Reactive power (Q) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1044 |  | 301045 | 04 | Generator > Reactive power (Q) > Generator ¦ L2 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1045 |  | 301046 | 04 | Generator > Reactive power (Q) > Generator ¦ L3 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1046 |  | 301047 | 04 | Generator > Reactive power (Q) > Generator ¦ Min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1047 |  | 301048 | 04 | Generator > Reactive power (Q) > Generator ¦ Max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1048 |  | 301049 | 04 | Generator > Reactive power (Q) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1049 |  | 301050 | 04 | Generator > Apparent power (S) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1050 |  | 301051 | 04 | Generator > Apparent power (S) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1051 |  | 301052 | 04 | Generator > Apparent power (S) > Generator ¦ L1 | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1052 |  | 301053 | 04 | Generator > Apparent power (S) > Generator ¦ Min. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1053 |  | 301054 | 04 | Generator > Apparent power (S) > Generator ¦ Max. | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1054 |  | 301055 | 04 | Generator > Apparent power (S) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1055 |  | 301056 | 04 | Generator > Power factor (PF) > Generator ¦ cos phi | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1056 |  | 301057 | 04 | Generator > Power factor (PF) > Generator ¦ Power factor | INT16 | AB | 2
[Controlled equiptment] ACM measurements | 1057 |  | 301058 | 04 | Generator > Voltage (V) > Generator ¦ Positive sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1058 |  | 301059 | 04 | Generator > Current (I) > Generator ¦ Positive sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1059 |  | 301060 | 04 | Generator > Voltage (V) > Generator ¦ Negative sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1060 |  | 301061 | 04 | Generator > Current (I) > Generator ¦ Negative sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1061 |  | 301062 | 04 | Generator > Voltage (V) > Generator ¦ Zero sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1062 |  | 301063 | 04 | Generator > Current (I) > Generator ¦ Zero sequence | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1063 |  | 301064 | 04 | Generator > Power (P) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1064 |  | 301065 | 04 | Generator > Reactive power (Q) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1065 |  | 301066 | 04 | Generator > Apparent power (S) > Generator ¦ Total | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1066 |  | 301067 | 04 | Generator > Power (P) > Generator ¦ Available | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1067 |  | 301068 | 04 | Generator > Reactive power (Q) > Generator ¦ Available | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1068 |  | 301069 | 04 | Generator > Apparent power (S) > Generator ¦ Available | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1069 |  | 301070 | 04 | Generator > Power (P) > Generator ¦ Available | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1070 |  | 301071 | 04 | Generator > Reactive power (Q) > Generator ¦ Available | INT16 | AB | 0
[Controlled equiptment] ACM measurements | 1071 |  | 301072 | 04 | Generator > Apparent power (S) > Generator ¦ Available | INT16 | AB | 0
[Busbar] ACM measurements | 1100 |  | 301101 | 04 | Busbar > Voltage (V) > Busbar ¦ L1-N | INT16 | AB | 0
[Busbar] ACM measurements | 1101 |  | 301102 | 04 | Busbar > Voltage (V) > Busbar ¦ L2-N | INT16 | AB | 0
[Busbar] ACM measurements | 1102 |  | 301103 | 04 | Busbar > Voltage (V) > Busbar ¦ L3-N | INT16 | AB | 0
[Busbar] ACM measurements | 1103 |  | 301104 | 04 | Busbar > Voltage (V) > Busbar ¦ N | INT16 | AB | 0
[Busbar] ACM measurements | 1104 |  | 301105 | 04 | Busbar > Voltage (V) > Busbar ¦ L-N min. | INT16 | AB | 0
[Busbar] ACM measurements | 1105 |  | 301106 | 04 | Busbar > Voltage (V) > Busbar ¦ L-N max. | INT16 | AB | 0
[Busbar] ACM measurements | 1106 |  | 301107 | 04 | Busbar > Voltage (V) > Busbar ¦ L-N unbalanced | INT16 | AB | 0
[Busbar] ACM measurements | 1107 |  | 301108 | 04 | Busbar > Voltage (V) > Busbar ¦ L1-L2 | INT16 | AB | 0
[Busbar] ACM measurements | 1108 |  | 301109 | 04 | Busbar > Voltage (V) > Busbar ¦ L2-L3 | INT16 | AB | 0
[Busbar] ACM measurements | 1109 |  | 301110 | 04 | Busbar > Voltage (V) > Busbar ¦ L3-L1 | INT16 | AB | 0
[Busbar] ACM measurements | 1110 |  | 301111 | 04 | Busbar > Voltage (V) > Busbar ¦ L-L min. | INT16 | AB | 0
[Busbar] ACM measurements | 1111 |  | 301112 | 04 | Busbar > Voltage (V) > Busbar ¦ L-L max. | INT16 | AB | 0
[Busbar] ACM measurements | 1112 |  | 301113 | 04 | Busbar > Voltage (V) > Busbar ¦ L-L unbalanced | INT16 | AB | 0
[Busbar] ACM measurements | 1113 |  | 301114 | 04 | Busbar > Frequency (f) > Busbar ¦ L1 | INT16 | AB | 2
[Busbar] ACM measurements | 1114 |  | 301115 | 04 | Busbar > Frequency (f) > Busbar ¦ L2 | INT16 | AB | 2
[Busbar] ACM measurements | 1115 |  | 301116 | 04 | Busbar > Frequency (f) > Busbar ¦ L3 | INT16 | AB | 2
[Busbar] ACM measurements | 1116 |  | 301117 | 04 | Busbar > Frequency (f) > Busbar ¦ Min. | INT16 | AB | 2
[Busbar] ACM measurements | 1117 |  | 301118 | 04 | Busbar > Frequency (f) > Busbar ¦ Max. | INT16 | AB | 2
[Busbar] ACM measurements | 1118 |  | 301119 | 04 | Busbar > Phase angle > Busbar ¦ Phase angle L1-L2 | INT16 | AB | 1
[Busbar] ACM measurements | 1119 |  | 301120 | 04 | Busbar > Phase angle > Busbar ¦ Phase angle L2-L3 | INT16 | AB | 1
[Busbar] ACM measurements | 1120 |  | 301121 | 04 | Busbar > Phase angle > Busbar ¦ Phase angle L3-L1 | INT16 | AB | 1
[Busbar] ACM measurements | 1121 |  | 301122 | 04 | Busbar > Voltage (V) > Busbar ¦ Positive sequence | INT16 | AB | 0
[Busbar] ACM measurements | 1122 |  | 301123 | 04 | Busbar > Voltage (V) > Busbar ¦ Negative sequence | INT16 | AB | 0
[Busbar] ACM measurements | 1123 |  | 301124 | 04 | Busbar > Voltage (V) > Busbar ¦ Zero sequence | INT16 | AB | 0
4th current ACM measurements | 1150 |  | 301151 | 04 | 4th current input > Current (I) > L4 | INT16 | AB | 0
4th current ACM measurements | 1151 |  | 301152 | 04 | 4th current input > Power (P) > L4 | INT16 | AB | 0
4th current ACM measurements | 1152 |  | 301153 | 04 | 4th current input > Reactive power (Q) > L4 | INT16 | AB | 0
4th current ACM measurements | 1153 |  | 301154 | 04 | 4th current input > Apparent power (S) > L4 | INT16 | AB | 0
4th current ACM measurements | 1154 |  | 301155 | 04 | 4th current input > Frequency (f) > L4 | INT16 | AB | 2
Alarm status: Operating value | 20000 |  | 320001 | 04 | Application initialisation error | INT16 | AB | 0
Alarm status: Operating value | 20012 |  | 320013 | 04 | Total running hours notification | INT16 | AB | 0
Alarm status: Operating value | 20016 |  | 320017 | 04 | Breakers > Generator breaker > Closing failure > GB closing failure | INT16 | AB | 0
Alarm status: Operating value | 20017 |  | 320018 | 04 | Breakers > Generator breaker > Opening failure > GB opening failure | INT16 | AB | 0
Alarm status: Operating value | 20018 |  | 320019 | 04 | Breakers > Generator breaker > Position failure > GB position failure | INT16 | AB | 0
Alarm status: Operating value | 20019 |  | 320020 | 04 | Breakers > Generator breaker > Configuration failure > GB configuration failure | INT16 | AB | 0
Alarm status: Operating value | 20020 |  | 320021 | 04 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure | INT16 | AB | 0
Alarm status: Operating value | 20022 |  | 320023 | 04 | Breakers > Generator breaker > Tripped (external) > GB tripped (external) | INT16 | AB | 0
Alarm status: Operating value | 20023 |  | 320024 | 04 | Breakers > Generator breaker > Short circuit > GB short circuit | INT16 | AB | 0
Alarm status: Operating value | 20032 |  | 320033 | 04 | Synchronisation > Alarms > Vector mismatch | INT16 | AB | 0
Alarm status: Operating value | 20037 |  | 320038 | 04 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A | INT16 | AB | 0
Alarm status: Operating value | 20038 |  | 320039 | 04 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B | INT16 | AB | 0
Alarm status: Operating value | 20039 |  | 320040 | 04 | AC configuration > Generator > Voltage or frequency not OK | INT16 | AB | 0
Alarm status: Operating value | 20040 |  | 320041 | 04 | Generator > Current protections > Zero sequence current | INT16 | AB | 1
Alarm status: Operating value | 20041 |  | 320042 | 04 | Generator > Voltage protections > Zero sequence voltage | INT16 | AB | 1
Alarm status: Operating value | 20042 |  | 320043 | 04 | Generator > Current protections > Negative sequence current | INT16 | AB | 1
Alarm status: Operating value | 20043 |  | 320044 | 04 | Generator > Voltage protections > Negative sequence voltage | INT16 | AB | 1
Alarm status: Operating value | 20044 |  | 320045 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.) | INT16 | AB | 1
Alarm status: Operating value | 20045 |  | 320046 | 04 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.) | INT16 | AB | 1
Alarm status: Operating value | 20046 |  | 320047 | 04 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance | INT16 | AB | 1
Alarm status: Operating value | 20047 |  | 320048 | 04 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance | INT16 | AB | 1
Alarm status: Operating value | 20048 |  | 320049 | 04 | Generator > Reactive power protections > Reactive power import 2 | INT16 | AB | 1
Alarm status: Operating value | 20049 |  | 320050 | 04 | Generator > Reactive power protections > Reactive power import 1 | INT16 | AB | 1
Alarm status: Operating value | 20050 |  | 320051 | 04 | Generator > Reactive power protections > Reactive power export 2 | INT16 | AB | 1
Alarm status: Operating value | 20051 |  | 320052 | 04 | Generator > Reactive power protections > Reactive power export 1 | INT16 | AB | 1
Alarm status: Operating value | 20052 |  | 320053 | 04 | Generator > Power protections > Reverse power 2 | INT16 | AB | 1
Alarm status: Operating value | 20053 |  | 320054 | 04 | Generator > Power protections > Reverse power 1 | INT16 | AB | 1
Alarm status: Operating value | 20054 |  | 320055 | 04 | Generator > Power protections > Overload 2 | INT16 | AB | 1
Alarm status: Operating value | 20055 |  | 320056 | 04 | Generator > Power protections > Overload 1 | INT16 | AB | 1
Alarm status: Operating value | 20056 |  | 320057 | 04 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2 | INT16 | AB | 1
Alarm status: Operating value | 20057 |  | 320058 | 04 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1 | INT16 | AB | 1
Alarm status: Operating value | 20058 |  | 320059 | 04 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2 | INT16 | AB | 1
Alarm status: Operating value | 20059 |  | 320060 | 04 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1 | INT16 | AB | 1
Alarm status: Operating value | 20060 |  | 320061 | 04 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2 | INT16 | AB | 1
Alarm status: Operating value | 20061 |  | 320062 | 04 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1 | INT16 | AB | 1
Alarm status: Operating value | 20062 |  | 320063 | 04 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2 | INT16 | AB | 1
Alarm status: Operating value | 20063 |  | 320064 | 04 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1 | INT16 | AB | 1
Alarm status: Operating value | 20064 |  | 320065 | 04 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2 | INT16 | AB | 1
Alarm status: Operating value | 20065 |  | 320066 | 04 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1 | INT16 | AB | 1
Alarm status: Operating value | 20066 |  | 320067 | 04 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2 | INT16 | AB | 1
Alarm status: Operating value | 20067 |  | 320068 | 04 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1 | INT16 | AB | 1
Alarm status: Operating value | 20068 |  | 320069 | 04 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2 | INT16 | AB | 1
Alarm status: Operating value | 20069 |  | 320070 | 04 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1 | INT16 | AB | 1
Alarm status: Operating value | 20070 |  | 320071 | 04 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2 | INT16 | AB | 1
Alarm status: Operating value | 20071 |  | 320072 | 04 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1 | INT16 | AB | 1
Alarm status: Operating value | 20072 |  | 320073 | 04 | Generator > Current protections > Directional over-current 2 | INT16 | AB | 1
Alarm status: Operating value | 20073 |  | 320074 | 04 | Generator > Current protections > Directional over-current 1 | INT16 | AB | 1
Alarm status: Operating value | 20074 |  | 320075 | 04 | Generator > Current protections > Fast over-current 2 | INT16 | AB | 1
Alarm status: Operating value | 20075 |  | 320076 | 04 | Generator > Current protections > Fast over-current 1 | INT16 | AB | 1
Alarm status: Operating value | 20076 |  | 320077 | 04 | Generator > Current protections > Over-current 2 | INT16 | AB | 1
Alarm status: Operating value | 20077 |  | 320078 | 04 | Generator > Current protections > Over-current 1 | INT16 | AB | 1
Alarm status: Operating value | 20078 |  | 320079 | 04 | Generator > Current protections > Inverse time over-current | INT16 | AB | 0
Alarm status: Operating value | 20079 |  | 320080 | 04 | 4th current input > Current protections > Earth inverse time over-current | INT16 | AB | 0
Alarm status: Operating value | 20080 |  | 320081 | 04 | 4th current input > Current protections > Neutral inverse time over-current | INT16 | AB | 0
Alarm status: Operating value | 20081 |  | 320082 | 04 | System not OK | INT16 | AB | 0
Alarm status: Operating value | 20082 |  | 320083 | 04 | Parameter store delayed | INT16 | AB | 0
Alarm status: Operating value | 20095 |  | 320096 | 04 | Required IO card(s) not found | INT16 | AB | 0
Alarm status: Operating value | 20096 |  | 320097 | 04 | Software mismatch on hardware module(s) | INT16 | AB | 0
Alarm status: Operating value | 20100 |  | 320101 | 04 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break | INT16 | AB | 0
Alarm status: Operating value | 20101 |  | 320102 | 04 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break | INT16 | AB | 0
Alarm status: Operating value | 20102 |  | 320103 | 04 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break | INT16 | AB | 0
Alarm status: Operating value | 20103 |  | 320104 | 04 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break | INT16 | AB | 0
Alarm status: Operating value | 20104 |  | 320105 | 04 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break | INT16 | AB | 0
Alarm status: Operating value | 20105 |  | 320106 | 04 | AC configuration > Generator > L1 wire break > Generator L1 wire break | INT16 | AB | 0
Alarm status: Operating value | 20106 |  | 320107 | 04 | AC configuration > Generator > L2 wire break > Generator L2 wire break | INT16 | AB | 0
Alarm status: Operating value | 20107 |  | 320108 | 04 | AC configuration > Generator > L3 wire break > Generator L3 wire break | INT16 | AB | 0
Alarm status: Operating value | 20116 |  | 320117 | 04 | Emergency stop | INT16 | AB | 0
Alarm status: Operating value | 20117 |  | 320118 | 04 | PCM clock battery failure | INT16 | AB | 0
Alarm status: Operating value | 20118 |  | 320119 | 04 | Controller temperature too high | INT16 | AB | 0
Alarm status: Operating value | 20119 |  | 320120 | 04 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high | INT16 | AB | 1
Alarm status: Operating value | 20120 |  | 320121 | 04 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low | INT16 | AB | 1
Alarm status: Operating value | 20121 |  | 320122 | 04 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high | INT16 | AB | 1
Alarm status: Operating value | 20122 |  | 320123 | 04 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low | INT16 | AB | 1
Alarm status: Operating value | 20123 |  | 320124 | 04 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high | INT16 | AB | 1
Alarm status: Operating value | 20124 |  | 320125 | 04 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low | INT16 | AB | 1
Alarm status: Operating value | 20125 |  | 320126 | 04 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high | INT16 | AB | 1
Alarm status: Operating value | 20126 |  | 320127 | 04 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low | INT16 | AB | 1
Alarm status: Operating value | 20208 |  | 320209 | 04 | Utility > Network > Ethernet redundancy broken | INT16 | AB | 0
Alarm status: Operating value | 20226 |  | 320227 | 04 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current | INT16 | AB | 0
Alarm status: Operating value | 20227 |  | 320228 | 04 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency | INT16 | AB | 0
Alarm status: Operating value | 20228 |  | 320229 | 04 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1 | INT16 | AB | 0
Alarm status: Operating value | 20229 |  | 320230 | 04 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2 | INT16 | AB | 0
Alarm status: Operating value | 20230 |  | 320231 | 04 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload | INT16 | AB | 0
Alarm status: Operating value | 20231 |  | 320232 | 04 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current | INT16 | AB | 0
Alarm status: Operating value | 20232 |  | 320233 | 04 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency | INT16 | AB | 0
Alarm status: Operating value | 20233 |  | 320234 | 04 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1 | INT16 | AB | 0
Alarm status: Operating value | 20234 |  | 320235 | 04 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2 | INT16 | AB | 0
Alarm status: Operating value | 20235 |  | 320236 | 04 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload | INT16 | AB | 0
Alarm status: Operating value | 20236 |  | 320237 | 04 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current | INT16 | AB | 0
Alarm status: Operating value | 20237 |  | 320238 | 04 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency | INT16 | AB | 0
Alarm status: Operating value | 20238 |  | 320239 | 04 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1 | INT16 | AB | 0
Alarm status: Operating value | 20239 |  | 320240 | 04 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2 | INT16 | AB | 0
Alarm status: Operating value | 20240 |  | 320241 | 04 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload | INT16 | AB | 0
Alarm status: Operating value | 20246 |  | 320247 | 04 | Utility > Network > Modbus communication timeout | INT16 | AB | 0
Alarm status: Operating value | 21500 |  | 321501 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21501 |  | 321502 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21502 |  | 321503 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21503 |  | 321504 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21504 |  | 321505 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21505 |  | 321506 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21506 |  | 321507 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21507 |  | 321508 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21508 |  | 321509 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21509 |  | 321510 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21510 |  | 321511 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21511 |  | 321512 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21512 |  | 321513 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21513 |  | 321514 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21514 |  | 321515 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21515 |  | 321516 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21516 |  | 321517 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21517 |  | 321518 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21518 |  | 321519 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21519 |  | 321520 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21520 |  | 321521 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21521 |  | 321522 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21522 |  | 321523 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21523 |  | 321524 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21524 |  | 321525 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21525 |  | 321526 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21526 |  | 321527 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21527 |  | 321528 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21528 |  | 321529 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21529 |  | 321530 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21530 |  | 321531 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21531 |  | 321532 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21532 |  | 321533 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21533 |  | 321534 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21534 |  | 321535 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21535 |  | 321536 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21536 |  | 321537 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21537 |  | 321538 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21538 |  | 321539 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21539 |  | 321540 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21540 |  | 321541 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21541 |  | 321542 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21542 |  | 321543 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21543 |  | 321544 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21544 |  | 321545 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21545 |  | 321546 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21546 |  | 321547 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21547 |  | 321548 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21548 |  | 321549 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Operating value | 21549 |  | 321550 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22016 |  | 322017 | 04 | Breakers > Generator breaker > Closing failure > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22017 |  | 322018 | 04 | Breakers > Generator breaker > Opening failure > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22018 |  | 322019 | 04 | Breakers > Generator breaker > Position failure > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22019 |  | 322020 | 04 | Breakers > Generator breaker > Configuration failure > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22020 |  | 322021 | 04 | Breakers > Generator breaker > Synchronisation failure > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22022 |  | 322023 | 04 | Breakers > Generator breaker > Tripped (external) > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22032 |  | 322033 | 04 | Synchronisation > Alarms > Vector mismatch > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22037 |  | 322038 | 04 | AC configuration > Busbar > Phase sequence error > Delay | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22038 |  | 322039 | 04 | AC configuration > Generator > Phase sequence error > Delay | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22039 |  | 322040 | 04 | AC configuration > Generator > Voltage or frequency not OK > Delay | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22040 |  | 322041 | 04 | Generator > Current protections > Zero sequence current > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22041 |  | 322042 | 04 | Generator > Voltage protections > Zero sequence voltage > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22042 |  | 322043 | 04 | Generator > Current protections > Negative sequence current > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22043 |  | 322044 | 04 | Generator > Voltage protections > Negative sequence voltage > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22044 |  | 322045 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22045 |  | 322046 | 04 | Generator > Current protections > Current unbalance (average calc) > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22046 |  | 322047 | 04 | Generator > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22047 |  | 322048 | 04 | Busbar > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22048 |  | 322049 | 04 | Generator > Reactive power protections > Reactive power import 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22049 |  | 322050 | 04 | Generator > Reactive power protections > Reactive power import 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22050 |  | 322051 | 04 | Generator > Reactive power protections > Reactive power export 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22051 |  | 322052 | 04 | Generator > Reactive power protections > Reactive power export 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22052 |  | 322053 | 04 | Generator > Power protections > Reverse power 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22053 |  | 322054 | 04 | Generator > Power protections > Reverse power 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22054 |  | 322055 | 04 | Generator > Power protections > Overload 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22055 |  | 322056 | 04 | Generator > Power protections > Overload 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22056 |  | 322057 | 04 | Busbar > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22057 |  | 322058 | 04 | Busbar > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22058 |  | 322059 | 04 | Busbar > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22059 |  | 322060 | 04 | Busbar > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22060 |  | 322061 | 04 | Busbar > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22061 |  | 322062 | 04 | Busbar > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22062 |  | 322063 | 04 | Busbar > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22063 |  | 322064 | 04 | Busbar > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22064 |  | 322065 | 04 | Generator > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22065 |  | 322066 | 04 | Generator > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22066 |  | 322067 | 04 | Generator > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22067 |  | 322068 | 04 | Generator > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22068 |  | 322069 | 04 | Generator > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22069 |  | 322070 | 04 | Generator > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22070 |  | 322071 | 04 | Generator > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22071 |  | 322072 | 04 | Generator > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22072 |  | 322073 | 04 | Generator > Current protections > Directional over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22073 |  | 322074 | 04 | Generator > Current protections > Directional over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22074 |  | 322075 | 04 | Generator > Current protections > Fast over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22075 |  | 322076 | 04 | Generator > Current protections > Fast over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22076 |  | 322077 | 04 | Generator > Current protections > Over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22077 |  | 322078 | 04 | Generator > Current protections > Over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer elapsed time | 22095 |  | 322096 | 04 | Required IO card(s) not found > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22096 |  | 322097 | 04 | Software mismatch on hardware module(s) > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22100 |  | 322101 | 04 | AC configuration > Busbar > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22101 |  | 322102 | 04 | AC configuration > Generator > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22102 |  | 322103 | 04 | AC configuration > Busbar > L1 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22103 |  | 322104 | 04 | AC configuration > Busbar > L2 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22104 |  | 322105 | 04 | AC configuration > Busbar > L3 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22105 |  | 322106 | 04 | AC configuration > Generator > L1 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22106 |  | 322107 | 04 | AC configuration > Generator > L2 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22107 |  | 322108 | 04 | AC configuration > Generator > L3 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22116 |  | 322117 | 04 | Emergency stop > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22117 |  | 322118 | 04 | PCM clock battery failure > Delay | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22118 |  | 322119 | 04 | Controller temperature too high > Delay | INT16 | AB | 0
Alarm status: Delay timer elapsed time | 22119 |  | 322120 | 04 | Power supply > PSM 1 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22120 |  | 322121 | 04 | Power supply > PSM 1 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22121 |  | 322122 | 04 | Power supply > PSM 2 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22122 |  | 322123 | 04 | Power supply > PSM 2 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22123 |  | 322124 | 04 | Power supply > PSM 3 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22124 |  | 322125 | 04 | Power supply > PSM 3 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22125 |  | 322126 | 04 | Power supply > PSM 4 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22126 |  | 322127 | 04 | Power supply > PSM 4 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22226 |  | 322227 | 04 | Non-essential load trip > Trip 1 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22227 |  | 322228 | 04 | Non-essential load trip > Trip 1 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22228 |  | 322229 | 04 | Non-essential load trip > Trip 1 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22229 |  | 322230 | 04 | Non-essential load trip > Trip 1 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22230 |  | 322231 | 04 | Non-essential load trip > Trip 1 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22231 |  | 322232 | 04 | Non-essential load trip > Trip 2 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22232 |  | 322233 | 04 | Non-essential load trip > Trip 2 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22233 |  | 322234 | 04 | Non-essential load trip > Trip 2 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22234 |  | 322235 | 04 | Non-essential load trip > Trip 2 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22235 |  | 322236 | 04 | Non-essential load trip > Trip 2 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22236 |  | 322237 | 04 | Non-essential load trip > Trip 3 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22237 |  | 322238 | 04 | Non-essential load trip > Trip 3 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22238 |  | 322239 | 04 | Non-essential load trip > Trip 3 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22239 |  | 322240 | 04 | Non-essential load trip > Trip 3 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22240 |  | 322241 | 04 | Non-essential load trip > Trip 3 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 22246 |  | 322247 | 04 | Utility > Network > Modbus communication timeout > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23500 |  | 323501 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23501 |  | 323502 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23502 |  | 323503 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23503 |  | 323504 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23504 |  | 323505 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23505 |  | 323506 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23506 |  | 323507 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23507 |  | 323508 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23508 |  | 323509 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23509 |  | 323510 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23510 |  | 323511 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23511 |  | 323512 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23512 |  | 323513 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23513 |  | 323514 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23514 |  | 323515 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23515 |  | 323516 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23516 |  | 323517 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23517 |  | 323518 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23518 |  | 323519 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23519 |  | 323520 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23520 |  | 323521 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23521 |  | 323522 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23522 |  | 323523 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23523 |  | 323524 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23524 |  | 323525 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23525 |  | 323526 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23526 |  | 323527 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23527 |  | 323528 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23528 |  | 323529 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23529 |  | 323530 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23530 |  | 323531 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23531 |  | 323532 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23532 |  | 323533 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23533 |  | 323534 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23534 |  | 323535 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23535 |  | 323536 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23536 |  | 323537 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23537 |  | 323538 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23538 |  | 323539 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23539 |  | 323540 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23540 |  | 323541 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23541 |  | 323542 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23542 |  | 323543 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23543 |  | 323544 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23544 |  | 323545 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23545 |  | 323546 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23546 |  | 323547 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23547 |  | 323548 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23548 |  | 323549 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer elapsed time | 23549 |  | 323550 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24016 |  | 324017 | 04 | Breakers > Generator breaker > Closing failure > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24017 |  | 324018 | 04 | Breakers > Generator breaker > Opening failure > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24018 |  | 324019 | 04 | Breakers > Generator breaker > Position failure > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24019 |  | 324020 | 04 | Breakers > Generator breaker > Configuration failure > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24020 |  | 324021 | 04 | Breakers > Generator breaker > Synchronisation failure > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24022 |  | 324023 | 04 | Breakers > Generator breaker > Tripped (external) > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24032 |  | 324033 | 04 | Synchronisation > Alarms > Vector mismatch > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24037 |  | 324038 | 04 | AC configuration > Busbar > Phase sequence error > Delay | INT16 | AB | 0
Alarm status: Delay timer remaining time | 24038 |  | 324039 | 04 | AC configuration > Generator > Phase sequence error > Delay | INT16 | AB | 0
Alarm status: Delay timer remaining time | 24039 |  | 324040 | 04 | AC configuration > Generator > Voltage or frequency not OK > Delay | INT16 | AB | 0
Alarm status: Delay timer remaining time | 24040 |  | 324041 | 04 | Generator > Current protections > Zero sequence current > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24041 |  | 324042 | 04 | Generator > Voltage protections > Zero sequence voltage > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24042 |  | 324043 | 04 | Generator > Current protections > Negative sequence current > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24043 |  | 324044 | 04 | Generator > Voltage protections > Negative sequence voltage > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24044 |  | 324045 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24045 |  | 324046 | 04 | Generator > Current protections > Current unbalance (average calc) > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24046 |  | 324047 | 04 | Generator > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24047 |  | 324048 | 04 | Busbar > Voltage protections > Voltage unbalance > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24048 |  | 324049 | 04 | Generator > Reactive power protections > Reactive power import 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24049 |  | 324050 | 04 | Generator > Reactive power protections > Reactive power import 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24050 |  | 324051 | 04 | Generator > Reactive power protections > Reactive power export 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24051 |  | 324052 | 04 | Generator > Reactive power protections > Reactive power export 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24052 |  | 324053 | 04 | Generator > Power protections > Reverse power 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24053 |  | 324054 | 04 | Generator > Power protections > Reverse power 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24054 |  | 324055 | 04 | Generator > Power protections > Overload 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24055 |  | 324056 | 04 | Generator > Power protections > Overload 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24056 |  | 324057 | 04 | Busbar > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24057 |  | 324058 | 04 | Busbar > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24058 |  | 324059 | 04 | Busbar > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24059 |  | 324060 | 04 | Busbar > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24060 |  | 324061 | 04 | Busbar > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24061 |  | 324062 | 04 | Busbar > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24062 |  | 324063 | 04 | Busbar > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24063 |  | 324064 | 04 | Busbar > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24064 |  | 324065 | 04 | Generator > Frequency protections > Under-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24065 |  | 324066 | 04 | Generator > Frequency protections > Under-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24066 |  | 324067 | 04 | Generator > Frequency protections > Over-frequency 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24067 |  | 324068 | 04 | Generator > Frequency protections > Over-frequency 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24068 |  | 324069 | 04 | Generator > Voltage protections > Under-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24069 |  | 324070 | 04 | Generator > Voltage protections > Under-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24070 |  | 324071 | 04 | Generator > Voltage protections > Over-voltage 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24071 |  | 324072 | 04 | Generator > Voltage protections > Over-voltage 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24072 |  | 324073 | 04 | Generator > Current protections > Directional over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24073 |  | 324074 | 04 | Generator > Current protections > Directional over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24074 |  | 324075 | 04 | Generator > Current protections > Fast over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24075 |  | 324076 | 04 | Generator > Current protections > Fast over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24076 |  | 324077 | 04 | Generator > Current protections > Over-current 2 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24077 |  | 324078 | 04 | Generator > Current protections > Over-current 1 > Delay | INT16 | AB | 2
Alarm status: Delay timer remaining time | 24095 |  | 324096 | 04 | Required IO card(s) not found > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24096 |  | 324097 | 04 | Software mismatch on hardware module(s) > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24100 |  | 324101 | 04 | AC configuration > Busbar > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24101 |  | 324102 | 04 | AC configuration > Generator > Multiple phase wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24102 |  | 324103 | 04 | AC configuration > Busbar > L1 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24103 |  | 324104 | 04 | AC configuration > Busbar > L2 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24104 |  | 324105 | 04 | AC configuration > Busbar > L3 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24105 |  | 324106 | 04 | AC configuration > Generator > L1 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24106 |  | 324107 | 04 | AC configuration > Generator > L2 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24107 |  | 324108 | 04 | AC configuration > Generator > L3 wire break > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24116 |  | 324117 | 04 | Emergency stop > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24117 |  | 324118 | 04 | PCM clock battery failure > Delay | INT16 | AB | 0
Alarm status: Delay timer remaining time | 24118 |  | 324119 | 04 | Controller temperature too high > Delay | INT16 | AB | 0
Alarm status: Delay timer remaining time | 24119 |  | 324120 | 04 | Power supply > PSM 1 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24120 |  | 324121 | 04 | Power supply > PSM 1 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24121 |  | 324122 | 04 | Power supply > PSM 2 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24122 |  | 324123 | 04 | Power supply > PSM 2 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24123 |  | 324124 | 04 | Power supply > PSM 3 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24124 |  | 324125 | 04 | Power supply > PSM 3 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24125 |  | 324126 | 04 | Power supply > PSM 4 > High voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24126 |  | 324127 | 04 | Power supply > PSM 4 > Low voltage alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24226 |  | 324227 | 04 | Non-essential load trip > Trip 1 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24227 |  | 324228 | 04 | Non-essential load trip > Trip 1 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24228 |  | 324229 | 04 | Non-essential load trip > Trip 1 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24229 |  | 324230 | 04 | Non-essential load trip > Trip 1 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24230 |  | 324231 | 04 | Non-essential load trip > Trip 1 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24231 |  | 324232 | 04 | Non-essential load trip > Trip 2 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24232 |  | 324233 | 04 | Non-essential load trip > Trip 2 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24233 |  | 324234 | 04 | Non-essential load trip > Trip 2 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24234 |  | 324235 | 04 | Non-essential load trip > Trip 2 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24235 |  | 324236 | 04 | Non-essential load trip > Trip 2 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24236 |  | 324237 | 04 | Non-essential load trip > Trip 3 > Over-current > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24237 |  | 324238 | 04 | Non-essential load trip > Trip 3 > Under-frequency > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24238 |  | 324239 | 04 | Non-essential load trip > Trip 3 > Overload 1 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24239 |  | 324240 | 04 | Non-essential load trip > Trip 3 > Overload 2 > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24240 |  | 324241 | 04 | Non-essential load trip > Trip 3 > Reactive overload > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 24246 |  | 324247 | 04 | Utility > Network > Modbus communication timeout > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25500 |  | 325501 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25501 |  | 325502 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25502 |  | 325503 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25503 |  | 325504 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25504 |  | 325505 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25505 |  | 325506 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25506 |  | 325507 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25507 |  | 325508 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25508 |  | 325509 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25509 |  | 325510 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25510 |  | 325511 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25511 |  | 325512 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25512 |  | 325513 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25513 |  | 325514 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25514 |  | 325515 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25515 |  | 325516 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25516 |  | 325517 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25517 |  | 325518 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25518 |  | 325519 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25519 |  | 325520 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25520 |  | 325521 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25521 |  | 325522 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25522 |  | 325523 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25523 |  | 325524 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25524 |  | 325525 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25525 |  | 325526 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25526 |  | 325527 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25527 |  | 325528 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25528 |  | 325529 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25529 |  | 325530 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25530 |  | 325531 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25531 |  | 325532 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25532 |  | 325533 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25533 |  | 325534 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25534 |  | 325535 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25535 |  | 325536 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25536 |  | 325537 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25537 |  | 325538 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25538 |  | 325539 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25539 |  | 325540 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25540 |  | 325541 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25541 |  | 325542 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25542 |  | 325543 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25543 |  | 325544 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25544 |  | 325545 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25545 |  | 325546 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25546 |  | 325547 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25547 |  | 325548 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25548 |  | 325549 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Delay timer remaining time | 25549 |  | 325550 | 04 | Digital custom alarm > Delay | INT16 | AB | 1
Alarm status: Alarm state | 26000 |  | 326001 | 04 | Application initialisation error | INT16 | AB | 0
Alarm status: Alarm state | 26012 |  | 326013 | 04 | Total running hours notification | INT16 | AB | 0
Alarm status: Alarm state | 26016 |  | 326017 | 04 | Breakers > Generator breaker > Closing failure > GB closing failure | INT16 | AB | 0
Alarm status: Alarm state | 26017 |  | 326018 | 04 | Breakers > Generator breaker > Opening failure > GB opening failure | INT16 | AB | 0
Alarm status: Alarm state | 26018 |  | 326019 | 04 | Breakers > Generator breaker > Position failure > GB position failure | INT16 | AB | 0
Alarm status: Alarm state | 26019 |  | 326020 | 04 | Breakers > Generator breaker > Configuration failure > GB configuration failure | INT16 | AB | 0
Alarm status: Alarm state | 26020 |  | 326021 | 04 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure | INT16 | AB | 0
Alarm status: Alarm state | 26022 |  | 326023 | 04 | Breakers > Generator breaker > Tripped (external) > GB tripped (external) | INT16 | AB | 0
Alarm status: Alarm state | 26023 |  | 326024 | 04 | Breakers > Generator breaker > Short circuit > GB short circuit | INT16 | AB | 0
Alarm status: Alarm state | 26032 |  | 326033 | 04 | Synchronisation > Alarms > Vector mismatch | INT16 | AB | 0
Alarm status: Alarm state | 26037 |  | 326038 | 04 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A | INT16 | AB | 0
Alarm status: Alarm state | 26038 |  | 326039 | 04 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B | INT16 | AB | 0
Alarm status: Alarm state | 26039 |  | 326040 | 04 | AC configuration > Generator > Voltage or frequency not OK | INT16 | AB | 0
Alarm status: Alarm state | 26040 |  | 326041 | 04 | Generator > Current protections > Zero sequence current | INT16 | AB | 0
Alarm status: Alarm state | 26041 |  | 326042 | 04 | Generator > Voltage protections > Zero sequence voltage | INT16 | AB | 0
Alarm status: Alarm state | 26042 |  | 326043 | 04 | Generator > Current protections > Negative sequence current | INT16 | AB | 0
Alarm status: Alarm state | 26043 |  | 326044 | 04 | Generator > Voltage protections > Negative sequence voltage | INT16 | AB | 0
Alarm status: Alarm state | 26044 |  | 326045 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.) | INT16 | AB | 0
Alarm status: Alarm state | 26045 |  | 326046 | 04 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.) | INT16 | AB | 0
Alarm status: Alarm state | 26046 |  | 326047 | 04 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance | INT16 | AB | 0
Alarm status: Alarm state | 26047 |  | 326048 | 04 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance | INT16 | AB | 0
Alarm status: Alarm state | 26048 |  | 326049 | 04 | Generator > Reactive power protections > Reactive power import 2 | INT16 | AB | 0
Alarm status: Alarm state | 26049 |  | 326050 | 04 | Generator > Reactive power protections > Reactive power import 1 | INT16 | AB | 0
Alarm status: Alarm state | 26050 |  | 326051 | 04 | Generator > Reactive power protections > Reactive power export 2 | INT16 | AB | 0
Alarm status: Alarm state | 26051 |  | 326052 | 04 | Generator > Reactive power protections > Reactive power export 1 | INT16 | AB | 0
Alarm status: Alarm state | 26052 |  | 326053 | 04 | Generator > Power protections > Reverse power 2 | INT16 | AB | 0
Alarm status: Alarm state | 26053 |  | 326054 | 04 | Generator > Power protections > Reverse power 1 | INT16 | AB | 0
Alarm status: Alarm state | 26054 |  | 326055 | 04 | Generator > Power protections > Overload 2 | INT16 | AB | 0
Alarm status: Alarm state | 26055 |  | 326056 | 04 | Generator > Power protections > Overload 1 | INT16 | AB | 0
Alarm status: Alarm state | 26056 |  | 326057 | 04 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2 | INT16 | AB | 0
Alarm status: Alarm state | 26057 |  | 326058 | 04 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1 | INT16 | AB | 0
Alarm status: Alarm state | 26058 |  | 326059 | 04 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2 | INT16 | AB | 0
Alarm status: Alarm state | 26059 |  | 326060 | 04 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1 | INT16 | AB | 0
Alarm status: Alarm state | 26060 |  | 326061 | 04 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2 | INT16 | AB | 0
Alarm status: Alarm state | 26061 |  | 326062 | 04 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1 | INT16 | AB | 0
Alarm status: Alarm state | 26062 |  | 326063 | 04 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2 | INT16 | AB | 0
Alarm status: Alarm state | 26063 |  | 326064 | 04 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1 | INT16 | AB | 0
Alarm status: Alarm state | 26064 |  | 326065 | 04 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2 | INT16 | AB | 0
Alarm status: Alarm state | 26065 |  | 326066 | 04 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1 | INT16 | AB | 0
Alarm status: Alarm state | 26066 |  | 326067 | 04 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2 | INT16 | AB | 0
Alarm status: Alarm state | 26067 |  | 326068 | 04 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1 | INT16 | AB | 0
Alarm status: Alarm state | 26068 |  | 326069 | 04 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2 | INT16 | AB | 0
Alarm status: Alarm state | 26069 |  | 326070 | 04 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1 | INT16 | AB | 0
Alarm status: Alarm state | 26070 |  | 326071 | 04 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2 | INT16 | AB | 0
Alarm status: Alarm state | 26071 |  | 326072 | 04 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1 | INT16 | AB | 0
Alarm status: Alarm state | 26072 |  | 326073 | 04 | Generator > Current protections > Directional over-current 2 | INT16 | AB | 0
Alarm status: Alarm state | 26073 |  | 326074 | 04 | Generator > Current protections > Directional over-current 1 | INT16 | AB | 0
Alarm status: Alarm state | 26074 |  | 326075 | 04 | Generator > Current protections > Fast over-current 2 | INT16 | AB | 0
Alarm status: Alarm state | 26075 |  | 326076 | 04 | Generator > Current protections > Fast over-current 1 | INT16 | AB | 0
Alarm status: Alarm state | 26076 |  | 326077 | 04 | Generator > Current protections > Over-current 2 | INT16 | AB | 0
Alarm status: Alarm state | 26077 |  | 326078 | 04 | Generator > Current protections > Over-current 1 | INT16 | AB | 0
Alarm status: Alarm state | 26078 |  | 326079 | 04 | Generator > Current protections > Inverse time over-current | INT16 | AB | 0
Alarm status: Alarm state | 26079 |  | 326080 | 04 | 4th current input > Current protections > Earth inverse time over-current | INT16 | AB | 0
Alarm status: Alarm state | 26080 |  | 326081 | 04 | 4th current input > Current protections > Neutral inverse time over-current | INT16 | AB | 0
Alarm status: Alarm state | 26081 |  | 326082 | 04 | System not OK | INT16 | AB | 0
Alarm status: Alarm state | 26082 |  | 326083 | 04 | Parameter store delayed | INT16 | AB | 0
Alarm status: Alarm state | 26095 |  | 326096 | 04 | Required IO card(s) not found | INT16 | AB | 0
Alarm status: Alarm state | 26096 |  | 326097 | 04 | Software mismatch on hardware module(s) | INT16 | AB | 0
Alarm status: Alarm state | 26100 |  | 326101 | 04 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26101 |  | 326102 | 04 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26102 |  | 326103 | 04 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26103 |  | 326104 | 04 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26104 |  | 326105 | 04 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26105 |  | 326106 | 04 | AC configuration > Generator > L1 wire break > Generator L1 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26106 |  | 326107 | 04 | AC configuration > Generator > L2 wire break > Generator L2 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26107 |  | 326108 | 04 | AC configuration > Generator > L3 wire break > Generator L3 wire break | INT16 | AB | 0
Alarm status: Alarm state | 26116 |  | 326117 | 04 | Emergency stop | INT16 | AB | 0
Alarm status: Alarm state | 26117 |  | 326118 | 04 | PCM clock battery failure | INT16 | AB | 0
Alarm status: Alarm state | 26118 |  | 326119 | 04 | Controller temperature too high | INT16 | AB | 0
Alarm status: Alarm state | 26119 |  | 326120 | 04 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high | INT16 | AB | 0
Alarm status: Alarm state | 26120 |  | 326121 | 04 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low | INT16 | AB | 0
Alarm status: Alarm state | 26121 |  | 326122 | 04 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high | INT16 | AB | 0
Alarm status: Alarm state | 26122 |  | 326123 | 04 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low | INT16 | AB | 0
Alarm status: Alarm state | 26123 |  | 326124 | 04 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high | INT16 | AB | 0
Alarm status: Alarm state | 26124 |  | 326125 | 04 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low | INT16 | AB | 0
Alarm status: Alarm state | 26125 |  | 326126 | 04 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high | INT16 | AB | 0
Alarm status: Alarm state | 26126 |  | 326127 | 04 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low | INT16 | AB | 0
Alarm status: Alarm state | 26208 |  | 326209 | 04 | Utility > Network > Ethernet redundancy broken | INT16 | AB | 0
Alarm status: Alarm state | 26226 |  | 326227 | 04 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current | INT16 | AB | 0
Alarm status: Alarm state | 26227 |  | 326228 | 04 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency | INT16 | AB | 0
Alarm status: Alarm state | 26228 |  | 326229 | 04 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1 | INT16 | AB | 0
Alarm status: Alarm state | 26229 |  | 326230 | 04 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2 | INT16 | AB | 0
Alarm status: Alarm state | 26230 |  | 326231 | 04 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload | INT16 | AB | 0
Alarm status: Alarm state | 26231 |  | 326232 | 04 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current | INT16 | AB | 0
Alarm status: Alarm state | 26232 |  | 326233 | 04 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency | INT16 | AB | 0
Alarm status: Alarm state | 26233 |  | 326234 | 04 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1 | INT16 | AB | 0
Alarm status: Alarm state | 26234 |  | 326235 | 04 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2 | INT16 | AB | 0
Alarm status: Alarm state | 26235 |  | 326236 | 04 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload | INT16 | AB | 0
Alarm status: Alarm state | 26236 |  | 326237 | 04 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current | INT16 | AB | 0
Alarm status: Alarm state | 26237 |  | 326238 | 04 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency | INT16 | AB | 0
Alarm status: Alarm state | 26238 |  | 326239 | 04 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1 | INT16 | AB | 0
Alarm status: Alarm state | 26239 |  | 326240 | 04 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2 | INT16 | AB | 0
Alarm status: Alarm state | 26240 |  | 326241 | 04 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload | INT16 | AB | 0
Alarm status: Alarm state | 26246 |  | 326247 | 04 | Utility > Network > Modbus communication timeout | INT16 | AB | 0
Alarm status: Alarm state | 27500 |  | 327501 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27501 |  | 327502 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27502 |  | 327503 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27503 |  | 327504 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27504 |  | 327505 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27505 |  | 327506 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27506 |  | 327507 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27507 |  | 327508 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27508 |  | 327509 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27509 |  | 327510 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27510 |  | 327511 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27511 |  | 327512 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27512 |  | 327513 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27513 |  | 327514 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27514 |  | 327515 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27515 |  | 327516 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27516 |  | 327517 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27517 |  | 327518 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27518 |  | 327519 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27519 |  | 327520 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27520 |  | 327521 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27521 |  | 327522 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27522 |  | 327523 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27523 |  | 327524 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27524 |  | 327525 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27525 |  | 327526 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27526 |  | 327527 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27527 |  | 327528 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27528 |  | 327529 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27529 |  | 327530 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27530 |  | 327531 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27531 |  | 327532 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27532 |  | 327533 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27533 |  | 327534 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27534 |  | 327535 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27535 |  | 327536 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27536 |  | 327537 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27537 |  | 327538 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27538 |  | 327539 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27539 |  | 327540 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27540 |  | 327541 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27541 |  | 327542 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27542 |  | 327543 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27543 |  | 327544 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27544 |  | 327545 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27545 |  | 327546 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27546 |  | 327547 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27547 |  | 327548 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27548 |  | 327549 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm state | 27549 |  | 327550 | 04 | Digital custom alarm | INT16 | AB | 0
Alarm status: Alarm active | 28000 | 0 | 328001 | 04 | Application initialisation error | BOOL | AB
Alarm status: Alarm active | 28000 | 12 | 328001 | 04 | Total running hours notification | BOOL | AB
Alarm status: Alarm active | 28001 | 0 | 328002 | 04 | Breakers > Generator breaker > Closing failure > GB closing failure | BOOL | AB
Alarm status: Alarm active | 28001 | 1 | 328002 | 04 | Breakers > Generator breaker > Opening failure > GB opening failure | BOOL | AB
Alarm status: Alarm active | 28001 | 2 | 328002 | 04 | Breakers > Generator breaker > Position failure > GB position failure | BOOL | AB
Alarm status: Alarm active | 28001 | 3 | 328002 | 04 | Breakers > Generator breaker > Configuration failure > GB configuration failure | BOOL | AB
Alarm status: Alarm active | 28001 | 4 | 328002 | 04 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure | BOOL | AB
Alarm status: Alarm active | 28001 | 6 | 328002 | 04 | Breakers > Generator breaker > Tripped (external) > GB tripped (external) | BOOL | AB
Alarm status: Alarm active | 28001 | 7 | 328002 | 04 | Breakers > Generator breaker > Short circuit > GB short circuit | BOOL | AB
Alarm status: Alarm active | 28002 | 0 | 328003 | 04 | Synchronisation > Alarms > Vector mismatch | BOOL | AB
Alarm status: Alarm active | 28002 | 5 | 328003 | 04 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A | BOOL | AB
Alarm status: Alarm active | 28002 | 6 | 328003 | 04 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B | BOOL | AB
Alarm status: Alarm active | 28002 | 7 | 328003 | 04 | AC configuration > Generator > Voltage or frequency not OK | BOOL | AB
Alarm status: Alarm active | 28002 | 8 | 328003 | 04 | Generator > Current protections > Zero sequence current | BOOL | AB
Alarm status: Alarm active | 28002 | 9 | 328003 | 04 | Generator > Voltage protections > Zero sequence voltage | BOOL | AB
Alarm status: Alarm active | 28002 | 10 | 328003 | 04 | Generator > Current protections > Negative sequence current | BOOL | AB
Alarm status: Alarm active | 28002 | 11 | 328003 | 04 | Generator > Voltage protections > Negative sequence voltage | BOOL | AB
Alarm status: Alarm active | 28002 | 12 | 328003 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.) | BOOL | AB
Alarm status: Alarm active | 28002 | 13 | 328003 | 04 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.) | BOOL | AB
Alarm status: Alarm active | 28002 | 14 | 328003 | 04 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance | BOOL | AB
Alarm status: Alarm active | 28002 | 15 | 328003 | 04 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance | BOOL | AB
Alarm status: Alarm active | 28003 | 0 | 328004 | 04 | Generator > Reactive power protections > Reactive power import 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 1 | 328004 | 04 | Generator > Reactive power protections > Reactive power import 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 2 | 328004 | 04 | Generator > Reactive power protections > Reactive power export 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 3 | 328004 | 04 | Generator > Reactive power protections > Reactive power export 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 4 | 328004 | 04 | Generator > Power protections > Reverse power 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 5 | 328004 | 04 | Generator > Power protections > Reverse power 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 6 | 328004 | 04 | Generator > Power protections > Overload 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 7 | 328004 | 04 | Generator > Power protections > Overload 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 8 | 328004 | 04 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 9 | 328004 | 04 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 10 | 328004 | 04 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 11 | 328004 | 04 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 12 | 328004 | 04 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 13 | 328004 | 04 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1 | BOOL | AB
Alarm status: Alarm active | 28003 | 14 | 328004 | 04 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2 | BOOL | AB
Alarm status: Alarm active | 28003 | 15 | 328004 | 04 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 0 | 328005 | 04 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 1 | 328005 | 04 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 2 | 328005 | 04 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 3 | 328005 | 04 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 4 | 328005 | 04 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 5 | 328005 | 04 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 6 | 328005 | 04 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 7 | 328005 | 04 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 8 | 328005 | 04 | Generator > Current protections > Directional over-current 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 9 | 328005 | 04 | Generator > Current protections > Directional over-current 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 10 | 328005 | 04 | Generator > Current protections > Fast over-current 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 11 | 328005 | 04 | Generator > Current protections > Fast over-current 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 12 | 328005 | 04 | Generator > Current protections > Over-current 2 | BOOL | AB
Alarm status: Alarm active | 28004 | 13 | 328005 | 04 | Generator > Current protections > Over-current 1 | BOOL | AB
Alarm status: Alarm active | 28004 | 14 | 328005 | 04 | Generator > Current protections > Inverse time over-current | BOOL | AB
Alarm status: Alarm active | 28004 | 15 | 328005 | 04 | 4th current input > Current protections > Earth inverse time over-current | BOOL | AB
Alarm status: Alarm active | 28005 | 0 | 328006 | 04 | 4th current input > Current protections > Neutral inverse time over-current | BOOL | AB
Alarm status: Alarm active | 28005 | 1 | 328006 | 04 | System not OK | BOOL | AB
Alarm status: Alarm active | 28005 | 2 | 328006 | 04 | Parameter store delayed | BOOL | AB
Alarm status: Alarm active | 28005 | 15 | 328006 | 04 | Required IO card(s) not found | BOOL | AB
Alarm status: Alarm active | 28006 | 0 | 328007 | 04 | Software mismatch on hardware module(s) | BOOL | AB
Alarm status: Alarm active | 28006 | 4 | 328007 | 04 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 5 | 328007 | 04 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 6 | 328007 | 04 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 7 | 328007 | 04 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 8 | 328007 | 04 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 9 | 328007 | 04 | AC configuration > Generator > L1 wire break > Generator L1 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 10 | 328007 | 04 | AC configuration > Generator > L2 wire break > Generator L2 wire break | BOOL | AB
Alarm status: Alarm active | 28006 | 11 | 328007 | 04 | AC configuration > Generator > L3 wire break > Generator L3 wire break | BOOL | AB
Alarm status: Alarm active | 28007 | 4 | 328008 | 04 | Emergency stop | BOOL | AB
Alarm status: Alarm active | 28007 | 5 | 328008 | 04 | PCM clock battery failure | BOOL | AB
Alarm status: Alarm active | 28007 | 6 | 328008 | 04 | Controller temperature too high | BOOL | AB
Alarm status: Alarm active | 28007 | 7 | 328008 | 04 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high | BOOL | AB
Alarm status: Alarm active | 28007 | 8 | 328008 | 04 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low | BOOL | AB
Alarm status: Alarm active | 28007 | 9 | 328008 | 04 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high | BOOL | AB
Alarm status: Alarm active | 28007 | 10 | 328008 | 04 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low | BOOL | AB
Alarm status: Alarm active | 28007 | 11 | 328008 | 04 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high | BOOL | AB
Alarm status: Alarm active | 28007 | 12 | 328008 | 04 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low | BOOL | AB
Alarm status: Alarm active | 28007 | 13 | 328008 | 04 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high | BOOL | AB
Alarm status: Alarm active | 28007 | 14 | 328008 | 04 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low | BOOL | AB
Alarm status: Alarm active | 28013 | 0 | 328014 | 04 | Utility > Network > Ethernet redundancy broken | BOOL | AB
Alarm status: Alarm active | 28014 | 2 | 328015 | 04 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current | BOOL | AB
Alarm status: Alarm active | 28014 | 3 | 328015 | 04 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency | BOOL | AB
Alarm status: Alarm active | 28014 | 4 | 328015 | 04 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1 | BOOL | AB
Alarm status: Alarm active | 28014 | 5 | 328015 | 04 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2 | BOOL | AB
Alarm status: Alarm active | 28014 | 6 | 328015 | 04 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload | BOOL | AB
Alarm status: Alarm active | 28014 | 7 | 328015 | 04 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current | BOOL | AB
Alarm status: Alarm active | 28014 | 8 | 328015 | 04 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency | BOOL | AB
Alarm status: Alarm active | 28014 | 9 | 328015 | 04 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1 | BOOL | AB
Alarm status: Alarm active | 28014 | 10 | 328015 | 04 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2 | BOOL | AB
Alarm status: Alarm active | 28014 | 11 | 328015 | 04 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload | BOOL | AB
Alarm status: Alarm active | 28014 | 12 | 328015 | 04 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current | BOOL | AB
Alarm status: Alarm active | 28014 | 13 | 328015 | 04 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency | BOOL | AB
Alarm status: Alarm active | 28014 | 14 | 328015 | 04 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1 | BOOL | AB
Alarm status: Alarm active | 28014 | 15 | 328015 | 04 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2 | BOOL | AB
Alarm status: Alarm active | 28015 | 0 | 328016 | 04 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload | BOOL | AB
Alarm status: Alarm active | 28015 | 6 | 328016 | 04 | Utility > Network > Modbus communication timeout | BOOL | AB
Alarm status: Alarm active | 28093 | 12 | 328094 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28093 | 13 | 328094 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28093 | 14 | 328094 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28093 | 15 | 328094 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 0 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 1 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 2 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 3 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 4 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 5 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 6 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 7 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 8 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 9 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 10 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 11 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 12 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 13 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 14 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28094 | 15 | 328095 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 0 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 1 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 2 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 3 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 4 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 5 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 6 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 7 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 8 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 9 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 10 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 11 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 12 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 13 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 14 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28095 | 15 | 328096 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 0 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 1 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 2 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 3 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 4 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 5 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 6 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 7 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 8 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 9 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 10 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 11 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 12 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm active | 28096 | 13 | 328097 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28125 | 0 | 328126 | 04 | Application initialisation error | BOOL | AB
Alarm status: Alarm acknowledged | 28125 | 12 | 328126 | 04 | Total running hours notification | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 0 | 328127 | 04 | Breakers > Generator breaker > Closing failure > GB closing failure | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 1 | 328127 | 04 | Breakers > Generator breaker > Opening failure > GB opening failure | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 2 | 328127 | 04 | Breakers > Generator breaker > Position failure > GB position failure | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 3 | 328127 | 04 | Breakers > Generator breaker > Configuration failure > GB configuration failure | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 4 | 328127 | 04 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 6 | 328127 | 04 | Breakers > Generator breaker > Tripped (external) > GB tripped (external) | BOOL | AB
Alarm status: Alarm acknowledged | 28126 | 7 | 328127 | 04 | Breakers > Generator breaker > Short circuit > GB short circuit | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 0 | 328128 | 04 | Synchronisation > Alarms > Vector mismatch | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 5 | 328128 | 04 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 6 | 328128 | 04 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 7 | 328128 | 04 | AC configuration > Generator > Voltage or frequency not OK | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 8 | 328128 | 04 | Generator > Current protections > Zero sequence current | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 9 | 328128 | 04 | Generator > Voltage protections > Zero sequence voltage | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 10 | 328128 | 04 | Generator > Current protections > Negative sequence current | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 11 | 328128 | 04 | Generator > Voltage protections > Negative sequence voltage | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 12 | 328128 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.) | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 13 | 328128 | 04 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.) | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 14 | 328128 | 04 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance | BOOL | AB
Alarm status: Alarm acknowledged | 28127 | 15 | 328128 | 04 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 0 | 328129 | 04 | Generator > Reactive power protections > Reactive power import 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 1 | 328129 | 04 | Generator > Reactive power protections > Reactive power import 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 2 | 328129 | 04 | Generator > Reactive power protections > Reactive power export 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 3 | 328129 | 04 | Generator > Reactive power protections > Reactive power export 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 4 | 328129 | 04 | Generator > Power protections > Reverse power 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 5 | 328129 | 04 | Generator > Power protections > Reverse power 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 6 | 328129 | 04 | Generator > Power protections > Overload 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 7 | 328129 | 04 | Generator > Power protections > Overload 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 8 | 328129 | 04 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 9 | 328129 | 04 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 10 | 328129 | 04 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 11 | 328129 | 04 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 12 | 328129 | 04 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 13 | 328129 | 04 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 14 | 328129 | 04 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28128 | 15 | 328129 | 04 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 0 | 328130 | 04 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 1 | 328130 | 04 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 2 | 328130 | 04 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 3 | 328130 | 04 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 4 | 328130 | 04 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 5 | 328130 | 04 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 6 | 328130 | 04 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 7 | 328130 | 04 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 8 | 328130 | 04 | Generator > Current protections > Directional over-current 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 9 | 328130 | 04 | Generator > Current protections > Directional over-current 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 10 | 328130 | 04 | Generator > Current protections > Fast over-current 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 11 | 328130 | 04 | Generator > Current protections > Fast over-current 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 12 | 328130 | 04 | Generator > Current protections > Over-current 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 13 | 328130 | 04 | Generator > Current protections > Over-current 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 14 | 328130 | 04 | Generator > Current protections > Inverse time over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28129 | 15 | 328130 | 04 | 4th current input > Current protections > Earth inverse time over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28130 | 0 | 328131 | 04 | 4th current input > Current protections > Neutral inverse time over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28130 | 1 | 328131 | 04 | System not OK | BOOL | AB
Alarm status: Alarm acknowledged | 28130 | 2 | 328131 | 04 | Parameter store delayed | BOOL | AB
Alarm status: Alarm acknowledged | 28130 | 15 | 328131 | 04 | Required IO card(s) not found | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 0 | 328132 | 04 | Software mismatch on hardware module(s) | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 4 | 328132 | 04 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 5 | 328132 | 04 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 6 | 328132 | 04 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 7 | 328132 | 04 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 8 | 328132 | 04 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 9 | 328132 | 04 | AC configuration > Generator > L1 wire break > Generator L1 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 10 | 328132 | 04 | AC configuration > Generator > L2 wire break > Generator L2 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28131 | 11 | 328132 | 04 | AC configuration > Generator > L3 wire break > Generator L3 wire break | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 4 | 328133 | 04 | Emergency stop | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 5 | 328133 | 04 | PCM clock battery failure | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 6 | 328133 | 04 | Controller temperature too high | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 7 | 328133 | 04 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 8 | 328133 | 04 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 9 | 328133 | 04 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 10 | 328133 | 04 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 11 | 328133 | 04 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 12 | 328133 | 04 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 13 | 328133 | 04 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high | BOOL | AB
Alarm status: Alarm acknowledged | 28132 | 14 | 328133 | 04 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low | BOOL | AB
Alarm status: Alarm acknowledged | 28138 | 0 | 328139 | 04 | Utility > Network > Ethernet redundancy broken | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 2 | 328140 | 04 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 3 | 328140 | 04 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 4 | 328140 | 04 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 5 | 328140 | 04 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 6 | 328140 | 04 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 7 | 328140 | 04 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 8 | 328140 | 04 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 9 | 328140 | 04 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 10 | 328140 | 04 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 11 | 328140 | 04 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 12 | 328140 | 04 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 13 | 328140 | 04 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 14 | 328140 | 04 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1 | BOOL | AB
Alarm status: Alarm acknowledged | 28139 | 15 | 328140 | 04 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2 | BOOL | AB
Alarm status: Alarm acknowledged | 28140 | 0 | 328141 | 04 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload | BOOL | AB
Alarm status: Alarm acknowledged | 28140 | 6 | 328141 | 04 | Utility > Network > Modbus communication timeout | BOOL | AB
Alarm status: Alarm acknowledged | 28218 | 12 | 328219 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28218 | 13 | 328219 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28218 | 14 | 328219 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28218 | 15 | 328219 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 0 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 1 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 2 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 3 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 4 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 5 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 6 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 7 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 8 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 9 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 10 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 11 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 12 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 13 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 14 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28219 | 15 | 328220 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 0 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 1 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 2 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 3 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 4 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 5 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 6 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 7 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 8 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 9 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 10 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 11 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 12 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 13 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 14 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28220 | 15 | 328221 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 0 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 1 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 2 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 3 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 4 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 5 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 6 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 7 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 8 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 9 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 10 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 11 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 12 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm acknowledged | 28221 | 13 | 328222 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28250 | 0 | 328251 | 04 | Application initialisation error | BOOL | AB
Alarm status: Alarm latched | 28250 | 12 | 328251 | 04 | Total running hours notification | BOOL | AB
Alarm status: Alarm latched | 28251 | 0 | 328252 | 04 | Breakers > Generator breaker > Closing failure > GB closing failure | BOOL | AB
Alarm status: Alarm latched | 28251 | 1 | 328252 | 04 | Breakers > Generator breaker > Opening failure > GB opening failure | BOOL | AB
Alarm status: Alarm latched | 28251 | 2 | 328252 | 04 | Breakers > Generator breaker > Position failure > GB position failure | BOOL | AB
Alarm status: Alarm latched | 28251 | 3 | 328252 | 04 | Breakers > Generator breaker > Configuration failure > GB configuration failure | BOOL | AB
Alarm status: Alarm latched | 28251 | 4 | 328252 | 04 | Breakers > Generator breaker > Synchronisation failure > GB synchronisation failure | BOOL | AB
Alarm status: Alarm latched | 28251 | 6 | 328252 | 04 | Breakers > Generator breaker > Tripped (external) > GB tripped (external) | BOOL | AB
Alarm status: Alarm latched | 28251 | 7 | 328252 | 04 | Breakers > Generator breaker > Short circuit > GB short circuit | BOOL | AB
Alarm status: Alarm latched | 28252 | 0 | 328253 | 04 | Synchronisation > Alarms > Vector mismatch | BOOL | AB
Alarm status: Alarm latched | 28252 | 5 | 328253 | 04 | AC configuration > Busbar > Phase sequence error > Phase sequence error terminal A | BOOL | AB
Alarm status: Alarm latched | 28252 | 6 | 328253 | 04 | AC configuration > Generator > Phase sequence error > Phase sequence error terminal B | BOOL | AB
Alarm status: Alarm latched | 28252 | 7 | 328253 | 04 | AC configuration > Generator > Voltage or frequency not OK | BOOL | AB
Alarm status: Alarm latched | 28252 | 8 | 328253 | 04 | Generator > Current protections > Zero sequence current | BOOL | AB
Alarm status: Alarm latched | 28252 | 9 | 328253 | 04 | Generator > Voltage protections > Zero sequence voltage | BOOL | AB
Alarm status: Alarm latched | 28252 | 10 | 328253 | 04 | Generator > Current protections > Negative sequence current | BOOL | AB
Alarm status: Alarm latched | 28252 | 11 | 328253 | 04 | Generator > Voltage protections > Negative sequence voltage | BOOL | AB
Alarm status: Alarm latched | 28252 | 12 | 328253 | 04 | Generator > Current protections > Current unbalance (nominal calc) > Current unbalance (nominal calc.) | BOOL | AB
Alarm status: Alarm latched | 28252 | 13 | 328253 | 04 | Generator > Current protections > Current unbalance (average calc) > Current unbalance (average calc.) | BOOL | AB
Alarm status: Alarm latched | 28252 | 14 | 328253 | 04 | Generator > Voltage protections > Voltage unbalance > Generator voltage unbalance | BOOL | AB
Alarm status: Alarm latched | 28252 | 15 | 328253 | 04 | Busbar > Voltage protections > Voltage unbalance > Busbar voltage unbalance | BOOL | AB
Alarm status: Alarm latched | 28253 | 0 | 328254 | 04 | Generator > Reactive power protections > Reactive power import 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 1 | 328254 | 04 | Generator > Reactive power protections > Reactive power import 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 2 | 328254 | 04 | Generator > Reactive power protections > Reactive power export 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 3 | 328254 | 04 | Generator > Reactive power protections > Reactive power export 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 4 | 328254 | 04 | Generator > Power protections > Reverse power 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 5 | 328254 | 04 | Generator > Power protections > Reverse power 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 6 | 328254 | 04 | Generator > Power protections > Overload 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 7 | 328254 | 04 | Generator > Power protections > Overload 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 8 | 328254 | 04 | Busbar > Frequency protections > Under-frequency 2 > Busbar under-frequency 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 9 | 328254 | 04 | Busbar > Frequency protections > Under-frequency 1 > Busbar under-frequency 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 10 | 328254 | 04 | Busbar > Frequency protections > Over-frequency 2 > Busbar over-frequency 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 11 | 328254 | 04 | Busbar > Frequency protections > Over-frequency 1 > Busbar over-frequency 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 12 | 328254 | 04 | Busbar > Voltage protections > Under-voltage 2 > Busbar under-voltage 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 13 | 328254 | 04 | Busbar > Voltage protections > Under-voltage 1 > Busbar under-voltage 1 | BOOL | AB
Alarm status: Alarm latched | 28253 | 14 | 328254 | 04 | Busbar > Voltage protections > Over-voltage 2 > Busbar over-voltage 2 | BOOL | AB
Alarm status: Alarm latched | 28253 | 15 | 328254 | 04 | Busbar > Voltage protections > Over-voltage 1 > Busbar over-voltage 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 0 | 328255 | 04 | Generator > Frequency protections > Under-frequency 2 > Generator under-frequency 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 1 | 328255 | 04 | Generator > Frequency protections > Under-frequency 1 > Generator under-frequency 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 2 | 328255 | 04 | Generator > Frequency protections > Over-frequency 2 > Generator over-frequency 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 3 | 328255 | 04 | Generator > Frequency protections > Over-frequency 1 > Generator over-frequency 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 4 | 328255 | 04 | Generator > Voltage protections > Under-voltage 2 > Generator under-voltage 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 5 | 328255 | 04 | Generator > Voltage protections > Under-voltage 1 > Generator under-voltage 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 6 | 328255 | 04 | Generator > Voltage protections > Over-voltage 2 > Generator over-voltage 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 7 | 328255 | 04 | Generator > Voltage protections > Over-voltage 1 > Generator over-voltage 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 8 | 328255 | 04 | Generator > Current protections > Directional over-current 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 9 | 328255 | 04 | Generator > Current protections > Directional over-current 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 10 | 328255 | 04 | Generator > Current protections > Fast over-current 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 11 | 328255 | 04 | Generator > Current protections > Fast over-current 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 12 | 328255 | 04 | Generator > Current protections > Over-current 2 | BOOL | AB
Alarm status: Alarm latched | 28254 | 13 | 328255 | 04 | Generator > Current protections > Over-current 1 | BOOL | AB
Alarm status: Alarm latched | 28254 | 14 | 328255 | 04 | Generator > Current protections > Inverse time over-current | BOOL | AB
Alarm status: Alarm latched | 28254 | 15 | 328255 | 04 | 4th current input > Current protections > Earth inverse time over-current | BOOL | AB
Alarm status: Alarm latched | 28255 | 0 | 328256 | 04 | 4th current input > Current protections > Neutral inverse time over-current | BOOL | AB
Alarm status: Alarm latched | 28255 | 1 | 328256 | 04 | System not OK | BOOL | AB
Alarm status: Alarm latched | 28255 | 2 | 328256 | 04 | Parameter store delayed | BOOL | AB
Alarm status: Alarm latched | 28255 | 15 | 328256 | 04 | Required IO card(s) not found | BOOL | AB
Alarm status: Alarm latched | 28256 | 0 | 328257 | 04 | Software mismatch on hardware module(s) | BOOL | AB
Alarm status: Alarm latched | 28256 | 4 | 328257 | 04 | AC configuration > Busbar > Multiple phase wire break > Busbar L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 5 | 328257 | 04 | AC configuration > Generator > Multiple phase wire break > Generator L1-L2-L3 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 6 | 328257 | 04 | AC configuration > Busbar > L1 wire break > Busbar L1 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 7 | 328257 | 04 | AC configuration > Busbar > L2 wire break > Busbar L2 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 8 | 328257 | 04 | AC configuration > Busbar > L3 wire break > Busbar L3 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 9 | 328257 | 04 | AC configuration > Generator > L1 wire break > Generator L1 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 10 | 328257 | 04 | AC configuration > Generator > L2 wire break > Generator L2 wire break | BOOL | AB
Alarm status: Alarm latched | 28256 | 11 | 328257 | 04 | AC configuration > Generator > L3 wire break > Generator L3 wire break | BOOL | AB
Alarm status: Alarm latched | 28257 | 4 | 328258 | 04 | Emergency stop | BOOL | AB
Alarm status: Alarm latched | 28257 | 5 | 328258 | 04 | PCM clock battery failure | BOOL | AB
Alarm status: Alarm latched | 28257 | 6 | 328258 | 04 | Controller temperature too high | BOOL | AB
Alarm status: Alarm latched | 28257 | 7 | 328258 | 04 | Power supply > PSM 1 > High voltage alarm > PSM 1 supply voltage high | BOOL | AB
Alarm status: Alarm latched | 28257 | 8 | 328258 | 04 | Power supply > PSM 1 > Low voltage alarm > PSM 1 supply voltage low | BOOL | AB
Alarm status: Alarm latched | 28257 | 9 | 328258 | 04 | Power supply > PSM 2 > High voltage alarm > PSM 2 supply voltage high | BOOL | AB
Alarm status: Alarm latched | 28257 | 10 | 328258 | 04 | Power supply > PSM 2 > Low voltage alarm > PSM 2 supply voltage low | BOOL | AB
Alarm status: Alarm latched | 28257 | 11 | 328258 | 04 | Power supply > PSM 3 > High voltage alarm > PSM 3 supply voltage high | BOOL | AB
Alarm status: Alarm latched | 28257 | 12 | 328258 | 04 | Power supply > PSM 3 > Low voltage alarm > PSM 3 supply voltage low | BOOL | AB
Alarm status: Alarm latched | 28257 | 13 | 328258 | 04 | Power supply > PSM 4 > High voltage alarm > PSM 4 supply voltage high | BOOL | AB
Alarm status: Alarm latched | 28257 | 14 | 328258 | 04 | Power supply > PSM 4 > Low voltage alarm > PSM 4 supply voltage low | BOOL | AB
Alarm status: Alarm latched | 28263 | 0 | 328264 | 04 | Utility > Network > Ethernet redundancy broken | BOOL | AB
Alarm status: Alarm latched | 28264 | 2 | 328265 | 04 | Non-essential load trip > Trip 1 > Over-current > NEL 1 over-current | BOOL | AB
Alarm status: Alarm latched | 28264 | 3 | 328265 | 04 | Non-essential load trip > Trip 1 > Under-frequency > NEL 1 under-frequency | BOOL | AB
Alarm status: Alarm latched | 28264 | 4 | 328265 | 04 | Non-essential load trip > Trip 1 > Overload 1 > NEL 1 overload 1 | BOOL | AB
Alarm status: Alarm latched | 28264 | 5 | 328265 | 04 | Non-essential load trip > Trip 1 > Overload 2 > NEL 1 overload 2 | BOOL | AB
Alarm status: Alarm latched | 28264 | 6 | 328265 | 04 | Non-essential load trip > Trip 1 > Reactive overload > NEL 1 reactive overload | BOOL | AB
Alarm status: Alarm latched | 28264 | 7 | 328265 | 04 | Non-essential load trip > Trip 2 > Over-current > NEL 2 over-current | BOOL | AB
Alarm status: Alarm latched | 28264 | 8 | 328265 | 04 | Non-essential load trip > Trip 2 > Under-frequency > NEL 2 under-frequency | BOOL | AB
Alarm status: Alarm latched | 28264 | 9 | 328265 | 04 | Non-essential load trip > Trip 2 > Overload 1 > NEL 2 overload 1 | BOOL | AB
Alarm status: Alarm latched | 28264 | 10 | 328265 | 04 | Non-essential load trip > Trip 2 > Overload 2 > NEL 2 overload 2 | BOOL | AB
Alarm status: Alarm latched | 28264 | 11 | 328265 | 04 | Non-essential load trip > Trip 2 > Reactive overload > NEL 2 reactive overload | BOOL | AB
Alarm status: Alarm latched | 28264 | 12 | 328265 | 04 | Non-essential load trip > Trip 3 > Over-current > NEL 3 over-current | BOOL | AB
Alarm status: Alarm latched | 28264 | 13 | 328265 | 04 | Non-essential load trip > Trip 3 > Under-frequency > NEL 3 under-frequency | BOOL | AB
Alarm status: Alarm latched | 28264 | 14 | 328265 | 04 | Non-essential load trip > Trip 3 > Overload 1 > NEL 3 overload 1 | BOOL | AB
Alarm status: Alarm latched | 28264 | 15 | 328265 | 04 | Non-essential load trip > Trip 3 > Overload 2 > NEL 3 overload 2 | BOOL | AB
Alarm status: Alarm latched | 28265 | 0 | 328266 | 04 | Non-essential load trip > Trip 3 > Reactive overload > NEL 3 reactive overload | BOOL | AB
Alarm status: Alarm latched | 28265 | 6 | 328266 | 04 | Utility > Network > Modbus communication timeout | BOOL | AB
Alarm status: Alarm latched | 28343 | 12 | 328344 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28343 | 13 | 328344 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28343 | 14 | 328344 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28343 | 15 | 328344 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 0 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 1 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 2 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 3 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 4 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 5 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 6 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 7 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 8 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 9 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 10 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 11 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 12 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 13 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 14 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28344 | 15 | 328345 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 0 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 1 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 2 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 3 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 4 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 5 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 6 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 7 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 8 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 9 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 10 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 11 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 12 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 13 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 14 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28345 | 15 | 328346 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 0 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 1 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 2 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 3 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 4 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 5 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 6 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 7 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 8 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 9 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 10 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 11 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 12 | 328347 | 04 | Digital custom alarm | BOOL | AB
Alarm status: Alarm latched | 28346 | 13 | 328347 | 04 | Digital custom alarm | BOOL | AB
General parameter: Delay timer elapsed time | 40125 |  | 340126 | 04 | Generator > Energy counters > Active power export > Pulse length | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40127 |  | 340128 | 04 | Generator > Energy counters > Reactive power export > Pulse length | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40144 |  | 340145 | 04 | AC configuration > Busbar > Voltage and frequency OK > Frequency and voltage OK | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40152 |  | 340153 | 04 | AC configuration > Busbar > Blackout detection > Blackout delay | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40153 |  | 340154 | 04 | AC configuration > Generator > Voltage and frequency OK > Frequency and voltage OK | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40309 |  | 340310 | 04 | Alarm horn > Horn 1 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40310 |  | 340311 | 04 | Alarm horn > Horn 1 > Minimum up time | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40313 |  | 340314 | 04 | Alarm horn > Horn 2 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40314 |  | 340315 | 04 | Alarm horn > Horn 2 > Minimum up time | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40317 |  | 340318 | 04 | Alarm horn > Horn 3 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer elapsed time | 40318 |  | 340319 | 04 | Alarm horn > Horn 3 > Minimum up time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46125 |  | 346126 | 04 | Generator > Energy counters > Active power export > Pulse length | INT16 | AB | 1
General parameter: Delay timer remaining time | 46127 |  | 346128 | 04 | Generator > Energy counters > Reactive power export > Pulse length | INT16 | AB | 1
General parameter: Delay timer remaining time | 46144 |  | 346145 | 04 | AC configuration > Busbar > Voltage and frequency OK > Frequency and voltage OK | INT16 | AB | 1
General parameter: Delay timer remaining time | 46152 |  | 346153 | 04 | AC configuration > Busbar > Blackout detection > Blackout delay | INT16 | AB | 1
General parameter: Delay timer remaining time | 46153 |  | 346154 | 04 | AC configuration > Generator > Voltage and frequency OK > Frequency and voltage OK | INT16 | AB | 1
General parameter: Delay timer remaining time | 46309 |  | 346310 | 04 | Alarm horn > Horn 1 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46310 |  | 346311 | 04 | Alarm horn > Horn 1 > Minimum up time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46313 |  | 346314 | 04 | Alarm horn > Horn 2 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46314 |  | 346315 | 04 | Alarm horn > Horn 2 > Minimum up time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46317 |  | 346318 | 04 | Alarm horn > Horn 3 > Minimum down time | INT16 | AB | 1
General parameter: Delay timer remaining time | 46318 |  | 346319 | 04 | Alarm horn > Horn 3 > Minimum up time | INT16 | AB | 1
Note on A4: Maarten van Bemmel: More information about each function group is available in the description sheet.
Note on C4: Maarten van Bemmel: Bit location of the function in the associated Modbus address.
Note on E4: Maarten van Bemmel: 04 - Read single or multiple
Note on F4: Maarten van Bemmel: The controller function name shows the path to the parameter in PICUS. If the function is not visible in PICUS, only the function name is displayed.
Note on G4: Maarten van Bemmel: Find the units of the associated function in the Designer's handbook.
Note on H4: Maarten van Bemmel: AB - Most significant byte first ABCD - Most significant byte first and most significant word first
Note on I4: Maarten van Bemmel: Example: Scaling = 1 Read data = 266 Actual value = 26,6