## About
iE 250 Power management Parameter lists
Software version
The information contained in these parameter lists (Revision B) are applicable to software version 2.0.18.x of the iE 250 Power management.
Controller types
This document includes the parameter and I/O function lists for these controller types:
SINGLE genset controller (with GB and MB)
GENSET controller
MAINS controller (with MB and TB)
BUS TIE breaker controller
See the iE 250 Power management Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
Custom parameters and Custom alarm are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include Fieldbus and Communication settings. These are not included in the parameter lists.
Input/output functions
The input/output function lists are based on the functions that can be selected in PICUS, under Configure > Input/ouput.
If you cannot find an input/output function in PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Path = The location of the input/output function.
Name = The name of the input/output function.
IO type = The type of the input/output function.
DI = Digital input function DO = Digital output function AI = Analogue input function AO = Analogue output function
Unit = The default unit of measurement for the input/output function.*
Data type = The data type for the input/output function.
Minimum = The default minimum value of the input/output function.*
Maximum = The default maximum value of the input/output function.*
Decimals = The number of decimal places for the value.*
Hidden = To see this input/output function, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
[User defined] is used where part of the path is configurable.

## SINGLE genset parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 600 | 1
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 600 | 1
Engine > Start sequence > Run coil | During start attempts | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 99 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 100 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 7 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 0
Engine > Start sequence > Crank failure | Delay | FLOAT | 2 | s | 0 | 20 | 1
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Start sequence > Run detection not reached | Run detection not reached | FLOAT | 10 | s | 1 | 1200 | 0
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run start > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 0 | 9900 | 0
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 99 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 10 | 120 | 1
Engine > Stop sequence > Stop failure | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Stop sequence > Externally stopped | Delay | FLOAT | 10 | s | 1 | 1200 | 0
Engine > Stop sequence > Externally stopped | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Idle run stop > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run stop > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Service timer > Service timer 1 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 2 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 3 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 4 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2 |  | X
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Fault ride through active
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Fault ride through active
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active, Fault ride through active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open, Mains breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Mains > AC setup > Mains power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
Mains > AC setup > Connection point voltage measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: External, 2: Analogue input
Mains > AC setup > Connection point voltage measurement | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Mains > AC setup > Voltage and frequency OK | Measurement configuration | INT32 | Phase-phase |  |  |  |  | 0: Phase-phase, 1: Phase-neutral, 2: Phase-phase or phase-neutral
Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Mains > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Over-voltage 1 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Over-voltage 2 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Over-voltage 3 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Under-voltage 1 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Under-voltage 2 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Under-voltage 3 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Under-voltage 4 | Inhibit |  | Fault ride through active
Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Additional protections > Vector shift | AC setup | INT32 | Mains |  |  |  |  | 34: Mains, 35: Generator
Mains > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Mains > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Mains > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
Mains > Additional protections > ROCOF | AC setup | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
Mains > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Mains > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Mains > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Mains > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Mains > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Mains > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0
Regulators > GOV > General configuration > Frequency recovery | Frequency recovery | INT32 | Off |  |  |  |  | 0: Off, 1: Volvo Penta EMS 2.4, 2: Frequency measurement
Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery limit | FLOAT | 3 | Hz | 0 | 20 | 1
Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery duration | FLOAT | 1 | s | 0 | 10 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Base load | Return mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto
Regulators > GOV > Regulation set points > Base load | Base load | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Base load | Set point | FLOAT | 90 | % | 10 | 120 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Warm up set point | FLOAT | 10 | % | 0.1 | 100 | 1
Regulators > GOV > Regulation set points > Active power ramp configuration | Island ramping | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Enter operation ramp enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Deload ramp enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 2 | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 3 | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Enable operation ramp 4 | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 0.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 3 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2500 | ms | 250 | 32500 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 500 | ms | 10 | 6500 | 0
Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Relay, 1: Analogue / Digital AVR
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 3
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Capacitive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 3
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Reactive power operation ramp | Enable ramping | INT32 | Linear |  |  |  |  | 1: Linear, 2: Time constant
Regulators > AVR > Regulation set points > Reactive power operation ramp | Time constant | FLOAT | 2 | s | 1 | 30 | 1 |  | X
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 500 | ms | 50 | 15000 | 0
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 100 | ms | 10 | 3000 | 0
Regulators > AVR > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Close before excitation > Configuration | Breaker close set point | FLOAT | 400 | RPM | 0 | 4000 | 0
Breakers > Close before excitation > Configuration | Timer crank release to AVR on | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Breakers > Close before excitation > Configuration | Breakers to close | INT32 | Close GB |  |  |  |  | 0: Close GB, 1: Close GB and TB
Breakers > Close before excitation > Configuration | Soft-start timer | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > Configuration | Minimum RPM for excitation | FLOAT | 1450 | RPM | 0 | 4000 | 0
Breakers > Close before excitation > Configuration | Voltage discharge timer for GB close | FLOAT | 5 | s | 1 | 20 | 1
Breakers > Close before excitation > Configuration | Maximum rerun voltage for GB close | FLOAT | 30 | % | 30 | 100 | 0
Breakers > Close before excitation > Configuration | Excitation control during cooldown | INT32 | Excitation follow U busbar |  |  |  |  | 0: Excitation follow U busbar, 1: Excitation constant ON, 2: Excitation OFF
Breakers > Close before excitation > CBE failure | Delay | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > CBE failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Close before excitation > CBE rerun failure | Delay | FLOAT | 120 | s | 0 | 999 | 1
Breakers > Close before excitation > CBE rerun failure | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Mains breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine, 2: Open MB at ready engine
Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1
Local power management > Genset test > Settings | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
Local power management > Genset test > Settings | Base load | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Genset test > Settings | Mode | INT32 | No mode change |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change, 3: No regulation
Local power management > Genset test > Settings | Test time | FLOAT | 300 | s | 0 | 59940 | 0
Power management rules > Plant/genset mode > Modes | Genset mode | INT32 | Power management |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over, 6: Power management
Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
Power management rules > Mains power > Peak shaving | Start generator | FLOAT | 80 | % | 5 | 100 | 0
Power management rules > Mains power > Peak shaving | Minimum load | FLOAT | 5 | % | 0 | 100 | 0
Power management rules > Mains power > Peak shaving | Stop generator | FLOAT | 60 | % | 0 | 80 | 0
Power management rules > Mains power > Peak shaving | Start delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Mains power > Peak shaving | Stop delay | FLOAT | 30 | s | 0 | 990 | 1
Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Common power factor control | Controller settings Q | FLOAT | 0 | % | -100 | 100 | 0
Power management rules > Mains power > Common power factor control | Controller settings cos phi or Q | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 3: Superior, 4: Fixed Q
Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Ground relay > Enable | Ground relay | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Ground relay > Ground relay configuration | Relay type | INT32 | Continuous |  |  |  |  | 0: Continuous, 1: Pulse | X
Power management rules > Ground relay > Ground relay configuration | Close configuration | INT32 | Hz/V OK |  |  |  |  | 0: Hz/V OK, 1: RPM MPU level, 2: RPM EIC level, 3: Start active | X
Power management rules > Ground relay > Ground relay configuration | Open configuration | INT32 | After cooldown |  |  |  |  | 0: After cooldown, 1: After extended stop | X
Power management rules > Ground relay > Ground relay configuration | RPM level | FLOAT | 1000 | RPM | 0 | 4000 | 0 |  | X
Power management rules > Ground relay > Ground relay general failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
Power management rules > Ground relay > Ground relay general failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Power management rules > Ground relay > Ground relay open failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
Power management rules > Ground relay > Ground relay open failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Power management rules > Ground relay > Ground relay close failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
Power management rules > Ground relay > Ground relay close failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Power management rules > Ground relay > Ground relay position failure | Delay | FLOAT | 1 | s | 1 | 30 | 1 |  | X
Power management rules > Ground relay > Ground relay position failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Power management rules > Number of gensets connected > Minimum set 1 | Set point | FLOAT | 1 |  | 0 | 32 | 0
Power management rules > Number of gensets connected > Minimum set 2 | Set point | FLOAT | 1 |  | 0 | 32 | 0
Power management rules > Number of gensets connected > Automatic start | Multi-start set 1 | INT32 | Auto calculation |  |  |  |  | 0: Auto calculation, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined], 9: [User defined], 10: [User defined], 11: [User defined], 12: [User defined], 13: [User defined], 14: [User defined], 15: [User defined], 16: [User defined], 17: [User defined], 18: [User defined], 19: [User defined], 20: [User defined], 21: [User defined], 22: [User defined], 23: [User defined], 24: [User defined], 25: [User defined], 26: [User defined], 27: [User defined], 28: [User defined], 29: [User defined], 30: [User defined], 31: [User defined], 32: [User defined]
Power management rules > Number of gensets connected > Automatic start | Multi-start set 2 | INT32 | [User defined] |  |  |  |  | 0: Auto calculation, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined], 9: [User defined], 10: [User defined], 11: [User defined], 12: [User defined], 13: [User defined], 14: [User defined], 15: [User defined], 16: [User defined], 17: [User defined], 18: [User defined], 19: [User defined], 20: [User defined], 21: [User defined], 22: [User defined], 23: [User defined], 24: [User defined], 25: [User defined], 26: [User defined], 27: [User defined], 28: [User defined], 29: [User defined], 30: [User defined], 31: [User defined], 32: [User defined]
Power management rules > Number of gensets connected > Selection | Multi-start selection | INT32 | Multi-start set 1 |  |  |  |  | 0: Multi-start set 1, 1: Multi-start set 2
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0
Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA
Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1
Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1
Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0
Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined]
System power management > Priority > Selection | Method | INT32 | Manual absolute |  |  |  |  | 0: Manual absolute, 1: Total running hours, 2: Fuel optimisation, 3: Manual relative, 4: Running hours relative, 5: Fuel optimisation + running hours | X
System power management > Priority > Selection | Transmit | INT32 | Off |  |  |  |  | 0: Off, 2: Running hours | X
System power management > Priority > Running hours | Activate priority update | FLOAT | 175 | h | 1 | 20000 | 0 |  | X
System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Mode while controller missing | Mode | INT32 | No regulation |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
System > Plant > Update | Application to broadcast | FLOAT | [User defined] |  |  |  |  | 1: [User defined]
System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Capability curve > Protections > Import protection | Delay | FLOAT | 1 | s | 0.1 | 300 | 2
Grid code > Capability curve > Protections > Import protection | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Capability curve > Protections > Import protection | Inhibit |  | Engine not running, Generator breaker open, Mains not in parallel
Grid code > Capability curve > Protections > Export protection | Delay | FLOAT | 1 | s | 0.1 | 300 | 2
Grid code > Capability curve > Protections > Export protection | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Capability curve > Protections > Export protection | Inhibit |  | Engine not running, Generator breaker open, Mains not in parallel
Grid code > Capability curve > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Capability curve > Configuration | Capability margin | FLOAT | 95 | % | 0 | 100 | 1
Grid code > Capability curve > Configuration | y-axis nominal select | INT32 | Power (P) |  |  |  |  | 0: Apparent power (S), 1: Power (P)
Grid code > Capability curve > Engine limit | Enable | INT32 | 1 |  | 0 | 1 | 0
Grid code > Capability curve > Engine limit | Set point | INT32 | 100 | % | 0 | 100 | 0
Grid code > Remote sensing > Power (P) | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Remote sensing > Reactive power (Q) | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Remote sensing > Voltage (V) | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Voltage deadband | FLOAT | 0 | % | 0 | 5 | 2
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Reference voltage at Q=0 | FLOAT | 1 |  | 0.5 | 1.5 | 2
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Maximum voltage at Q max | FLOAT | 1.04 |  | 0.5 | 1.5 | 2
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Maximum Q during over-voltage | FLOAT | 0.33 |  | 0 | 0.4 | 2
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Minimum Q during under-voltage | FLOAT | -0.33 |  | -0.4 | 0 | 2
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | Reference voltage offset value | FLOAT | 0 |  | -0.2 | 0.2 | 3
Grid code > Reactive power regulation > Variants > Variant A: Q(U) U-shift | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
Grid code > Reactive power regulation > Variants > Variant C: Q(U) Q-shift | Q/Pnom offset | FLOAT | 0 |  | -0.4 | 0.4 | 2
Grid code > Reactive power regulation > Variants > Variant C: Q(U) Q-shift | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi set point | FLOAT | 1 |  | 0.9 | 1 | 3
Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | Cos phi offset | FLOAT | 0 |  | -0.1 | 0.1 | 3
Grid code > Reactive power regulation > Variants > Variant D: Cos phi fixed | External control | INT32 | PICUS/Modbus |  |  |  |  | 0: PICUS/Modbus, 1: Analogue
Grid code > Reactive power regulation > Variants > Variant E: Q fixed | Q set point | FLOAT | 0 | % | -100 | 100 | 1
Grid code > Reactive power regulation > Configuration | Type selection | INT32 | Default |  |  |  |  | 0: Default, 1: Variant A: Q(U) U-shift, 2: Variant B: Q(P) curve, 3: Variant C: Q(U) Q-shift, 4: Variant D: Cos phi fixed, 5: Variant E: Q fixed
Grid code > Reactive power regulation > Configuration | Ramp switch timer | FLOAT | 240 | s | 0 | 600 | 0
Grid code > Reactive power regulation > Configuration | Limit Q under-excited | INT32 | 0 |  | 0 | 1 | 0
Grid code > Reactive power regulation > Configuration | Limit Q over-excited | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Frequency-dependent active power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -0.5 | % | -100 | 0 | 2
Grid code > Droop curve > Frequency-dependent active power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 0.5 | % | 0 | 100 | 2
Grid code > Droop curve > Frequency-dependent active power droop > Hysteresis > Frequency | Hysteresis low limit | FLOAT | -0.25 | Hz | -100 | 0 | 2 |  | X
Grid code > Droop curve > Frequency-dependent active power droop > Hysteresis > Frequency | Hysteresis high limit | FLOAT | 0.25 | Hz | 0 | 100 | 2 |  | X
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Adjustment source | INT32 | Nominal power |  |  |  |  | 0: Active power snapshot, 1: Nominal power
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Dependency | INT32 | Frequency |  |  |  |  | 0: Frequency, 1: Voltage
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Recovery delay | FLOAT | 600 | s | 0 | 3600 | 1
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Ramp 3 activation delay | FLOAT | 5 | s | 0 | 10 | 1
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Frequency-dependent active power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Voltage-dependent active power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -0.5 | % | -100 | 0 | 2 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 0.5 | % | 0 | 100 | 2 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -2 | V | -1500000 | 0 | 1 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 2 | V | 0 | 1500000 | 1 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Configuration | Adjustment source | INT32 | Nominal power |  |  |  |  | 0: Active power snapshot, 1: Nominal power | X
Grid code > Droop curve > Voltage-dependent active power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute | X
Grid code > Droop curve > Voltage-dependent active power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent active power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -2.1 | % | -100 | 0 | 2 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 2.1 | % | 0 | 100 | 2 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -8.4 | V | -1500000 | 0 | 1 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 8.4 | V | 0 | 1500000 | 1 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Configuration | Adjustment source | INT32 | Nominal reactive power |  |  |  |  | 0: Reactive power snapshot, 1: Nominal reactive power | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent reactive power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -2.1 | % | -100 | 0 | 1 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 2.1 | % | 0 | 100 | 1 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Hysteresis > Active power | Hysteresis low limit | FLOAT | -21 | kW | -900000 | 0 | 1 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Hysteresis > Active power | Hysteresis high limit | FLOAT | 21 | kW | 0 | 900000 | 1 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Configuration | Adjustment source | INT32 | Nominal reactive power |  |  |  |  | 0: Reactive power snapshot, 1: Nominal reactive power | X
Grid code > Droop curve > Active power-dependent reactive power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute | X
Grid code > Droop curve > Active power-dependent reactive power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Active power-dependent reactive power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -2.1 | % | -100 | 0 | 2
Grid code > Droop curve > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 2.1 | % | 0 | 100 | 2
Grid code > Droop curve > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -8.4 | V | -1500000 | 0 | 2 |  | X
Grid code > Droop curve > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 8.4 | V | 0 | 1500000 | 2 |  | X
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Curve output | INT32 | Cos phi |  |  |  |  | 0: Cos phi, 1: Reactive power
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Dependency | INT32 | Voltage |  |  |  |  | 0: Voltage, 1: Active power
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Voltage-dependent cos phi droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Droop curve > Active power-dependent cos phi droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -2.1 | % | -100 | 0 | 2 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 2.1 | % | 0 | 100 | 2 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Hysteresis > Active power | Hysteresis low limit | FLOAT | -21 | kW | -900000 | 0 | 1 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Hysteresis > Active power | Hysteresis high limit | FLOAT | 21 | kW | 0 | 900000 | 1 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute | X
Grid code > Droop curve > Active power-dependent cos phi droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Droop curve > Active power-dependent cos phi droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 0: One phase-phase, 1: Two phase-phase, 2: Three phase-phase, 3: Any phase-phase, 4: One phase-neutral, 5: Two phase-neutral, 6: Three phase-neutral, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 9: Symmetrical phase-phase, 10: Asymmetrical phase-phase, 11: Symmetrical asymmetrical any phase-phase, 12: Symmetrical phase-neutral, 13: Asymmetrical phase-neutral, 14: Symmetrical asymmetrical any phase-neutral
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Recovery threshold | FLOAT | 95 | % | 0 | 100 | 1
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Low voltage ride through 1 | Inhibit |  | Mains not in parallel
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 0: One phase-phase, 1: Two phase-phase, 2: Three phase-phase, 3: Any phase-phase, 4: One phase-neutral, 5: Two phase-neutral, 6: Three phase-neutral, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 9: Symmetrical phase-phase, 10: Asymmetrical phase-phase, 11: Symmetrical asymmetrical any phase-phase, 12: Symmetrical phase-neutral, 13: Asymmetrical phase-neutral, 14: Symmetrical asymmetrical any phase-neutral
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Recovery threshold | FLOAT | 95 | % | 0 | 100 | 1
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Low voltage ride through 2 | Inhibit |  | Mains not in parallel
Grid code > Fault ride through > Protections > High voltage ride through 1 | Activation phase type | INT32 | Any phase-phase |  |  |  |  | 3: Any phase-phase, 7: Any phase-neutral, 8: Any phase-phase or phase-neutral, 11: Symmetrical asymmetrical any phase-phase, 14: Symmetrical asymmetrical any phase-neutral
Grid code > Fault ride through > Protections > High voltage ride through 1 | Recovery threshold | FLOAT | 105 | % | 100 | 130 | 1
Grid code > Fault ride through > Protections > High voltage ride through 1 | Recovery delay | FLOAT | 1 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > High voltage ride through 1 | Link configuration | INT32 | 0 |  | 0 | 1 | 0
Grid code > Fault ride through > Protections > High voltage ride through 1 | Minimum activation time | FLOAT | 0 | s | 0 | 100 | 2
Grid code > Fault ride through > Protections > High voltage ride through 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > High voltage ride through 1 | Inhibit |  | Mains not in parallel
Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Activation alarm LVRT1 | Inhibit |  | Engine not running, Generator breaker open
Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Activation alarm LVRT2 | Inhibit |  | Engine not running, Generator breaker open
Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Activation alarm HVRT1 | Inhibit |  | Engine not running, Generator breaker open
Grid code > Fault ride through > Protections > Consecutive disturbance | Minimum time between disturbances | FLOAT | 20 | s | 0 | 86400 | 1
Grid code > Fault ride through > Protections > Consecutive disturbance | Disturbance reset time | FLOAT | 3600 | s | 1 | 86400 | 1
Grid code > Fault ride through > Protections > Consecutive disturbance | Number of consecutive disturbances | INT32 | 5 |  | 1 | 10 | 0
Grid code > Fault ride through > Protections > Consecutive disturbance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Fault ride through > Protections > Consecutive disturbance | Inhibit |  | Mains not in parallel
Grid code > Fault ride through > Preset all parameters | Preset to | INT32 | [5 empty] | 0: , 1: VDE 2025
Grid code > Fault ride through > Suspend regulation | GOV enable | INT32 | 1 |  | 0 | 1 | 0
Grid code > Fault ride through > Suspend regulation | GOV timeout | FLOAT | 10 | s | 0 | 120 | 2
Grid code > Fault ride through > Suspend regulation | AVR enable | INT32 | 1 |  | 0 | 1 | 0
Grid code > Fault ride through > Suspend regulation | AVR timeout | FLOAT | 10 | s | 0 | 120 | 2
Grid code > Power feed in management > Contractual limit > Percentage | Contractual limit | FLOAT | 0 | % | 0 | 110 | 1
Grid code > Power feed in management > Contractual limit > Percentage | Contractual limit margin | FLOAT | 0 | % | 0 | 100 | 1
Grid code > Power feed in management > Contractual limit > Absolute | Contractual limit | FLOAT | 0 | kW | 0 | 900000 | 1 |  | X
Grid code > Power feed in management > Contractual limit > Absolute | Contractual limit margin | FLOAT | 0 | kW | 0 | 900000 | 1 |  | X
Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Delay | FLOAT | 1.6 | s | 0 | 7200 | 2
Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Set point | FLOAT | 90 | % | 0 | 110 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Power feed in management > Protections > Grid contractual alarm 1 | Inhibit |  | Engine not running, Mains not in parallel
Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Delay | FLOAT | 4 | s | 0 | 7200 | 2
Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Set point | FLOAT | 15 | % | 0 | 110 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Power feed in management > Protections > Grid contractual alarm 2 | Inhibit |  | Engine not running, Mains not in parallel
Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Delay | FLOAT | 11 | s | 0 | 7200 | 2
Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Set point | FLOAT | 5 | % | 0 | 110 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Set point addition | FLOAT | 0 | kW | 0 | 900000 | 1
Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > Power feed in management > Protections > Grid contractual alarm 3 | Inhibit |  | Engine not running, Mains not in parallel
Grid code > Power feed in management > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Power feed in management > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Grid code > Power feed in management > Ramp | Curve type | INT32 | Exponential |  |  |  |  | 0: Exponential, 1: Linear
Grid code > Power feed in management > Ramp | Start delay | FLOAT | 0 | s | 0 | 300 | 1
Grid code > Power feed in management > Ramp | End time | FLOAT | 40 | s | 0 | 3600 | 1 |  | X
Grid code > Power feed in management > Ramp | Decay factor | FLOAT | 1.05 |  | 0.01 | 2 | 2
Grid code > ROCOF > Preset all parameters | Preset to | INT32 | [5 empty] | 0: , 1: VDE 2025
Grid code > ROCOF > ROCOF 1 | Measurement source | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
Grid code > ROCOF > ROCOF 1 | Set point positive | FLOAT | 2 | Hz/s | 0.1 | 50 | 2 |  | X
Grid code > ROCOF > ROCOF 1 | Set point negative | FLOAT | -2 | Hz/s | -50 | -0.1 | 2 |  | X
Grid code > ROCOF > ROCOF 1 | Averaging time | FLOAT | 0.5 | s | 0.09 | 2 | 2 |  | X
Grid code > ROCOF > ROCOF 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > ROCOF > ROCOF 1 | Inhibit |  | Mains not in parallel
Grid code > ROCOF > ROCOF 2 | Measurement source | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
Grid code > ROCOF > ROCOF 2 | Set point positive | FLOAT | 1.5 | Hz/s | 0.1 | 50 | 2 |  | X
Grid code > ROCOF > ROCOF 2 | Set point negative | FLOAT | -1.5 | Hz/s | -50 | -0.1 | 2 |  | X
Grid code > ROCOF > ROCOF 2 | Averaging time | FLOAT | 1 | s | 0.09 | 2 | 2 |  | X
Grid code > ROCOF > ROCOF 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > ROCOF > ROCOF 2 | Inhibit |  | Mains not in parallel
Grid code > ROCOF > ROCOF 3 | Measurement source | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
Grid code > ROCOF > ROCOF 3 | Set point positive | FLOAT | 1.25 | Hz/s | 0.1 | 50 | 2 |  | X
Grid code > ROCOF > ROCOF 3 | Set point negative | FLOAT | -1.25 | Hz/s | -50 | -0.1 | 2 |  | X
Grid code > ROCOF > ROCOF 3 | Averaging time | FLOAT | 2 | s | 0.09 | 2 | 2 |  | X
Grid code > ROCOF > ROCOF 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Grid code > ROCOF > ROCOF 3 | Inhibit |  | Mains not in parallel
Grid code > Feed forward | Reactive power gain | FLOAT | 10 |  | 0 | 50 | 2
Grid code > Feed forward | Reactive power enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Feed forward | Active power gain | FLOAT | 12.5 |  | 0 | 50 | 2
Grid code > Feed forward | Active power enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > RRCR | Inputs enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > RRCR | Outputs enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Frequency offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
Grid code > Frequency offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
Grid code > Mains sync inhibit | Voltage low limit | FLOAT | 85 | % | 80 | 100 | 0
Grid code > Mains sync inhibit | Voltage high limit | FLOAT | 110 | % | 100 | 120 | 0
Grid code > Mains sync inhibit | Frequency low limit | FLOAT | 95 | % | 90 | 100 | 1
Grid code > Mains sync inhibit | Frequency high limit | FLOAT | 101 | % | 100 | 110 | 1
Grid code > Mains sync inhibit | Recovery delay select | FLOAT | 1 |  | 1 | 1 | 0 |  | X
Grid code > Mains sync inhibit | Recovery delay select time | FLOAT | 3 | s | 0 | 20 | 1
Grid code > Mains sync inhibit | Recovery delay 1 | FLOAT | 1 |  | 1 | 1 | 0 |  | X
Grid code > Mains sync inhibit | Recovery delay 1 time | FLOAT | 5 | s | 0 | 60 | 1
Grid code > Mains sync inhibit | Recovery delay 2 | FLOAT | 1 |  | 1 | 1 | 0 |  | X
Grid code > Mains sync inhibit | Recovery delay 2 time | FLOAT | 600 | s | 0 | 2000 | 1
Grid code > Mains sync inhibit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop

## SINGLE genset IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
11080048 | Engine > Command | Crank delay | DI |  | BOOL_NUM | 0 | 1 | 0
11080049 | Engine > Command | Warm up delay | DI |  | BOOL_NUM | 0 | 1 | 0
11080050 | Engine > Command | Cooldown abort | DI |  | BOOL_NUM | 0 | 1 | 0
11080051 | Engine > Command | De-load genset | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Command | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180004 | Engine > Idle run | Low speed | DI |  | BOOL_NUM | 0 | 1 | 0
11180005 | Engine > Idle run | Temperature control | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
110100030 | Mains > External set points | Activate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100031 | Mains > External set points | Deactivate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100024 | Mains > Set point offsets > Active power | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100025 | Mains > Set point offsets > Active power | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100026 | Mains > Set point offsets > Active power | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110100027 | Mains > Set point offsets > Cos phi | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100028 | Mains > Set point offsets > Cos phi | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100029 | Mains > Set point offsets > Cos phi | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Generator breaker > Command | GB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Generator breaker > Command | GB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
20280028 | Breakers > Mains breaker > Command | MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280029 | Breakers > Mains breaker > Command | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280031 | Breakers > Mains breaker > Command | Block MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280000 | Breakers > Mains breaker > Feedback | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280001 | Breakers > Mains breaker > Feedback | MB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20280004 | Breakers > Mains breaker > Feedback | MB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20280012 | Breakers > Mains breaker > Feedback | MB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
60000510 | Local > Mode | Block | DI |  | BOOL_NUM | 0 | 1 | 0
60000511 | Local > Mode | Test | DI |  | BOOL_NUM | 0 | 1 | 0
60000512 | Local > Mode | No regulation | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
90130017 | System power management > Automatic start | Auto start/stop | DI |  | BOOL_NUM | 0 | 1 | 0
32200002 | System power management > Ground relay | Ground relay position feedback A | DI |  | BOOL_NUM | 0 | 1 | 0
32200003 | System power management > Ground relay | Ground relay position feedback B | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
86010006 | Grid code > RRCR | RRCR input 1 | DI |  | BOOL_NUM | 0 | 1 | 0
86010007 | Grid code > RRCR | RRCR input 2 | DI |  | BOOL_NUM | 0 | 1 | 0
86010008 | Grid code > RRCR | RRCR input 3 | DI |  | BOOL_NUM | 0 | 1 | 0
86010009 | Grid code > RRCR | RRCR input 4 | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0
11080059 | Engine > State | Running indicator | DO |  | BOOL_NUM | 0 | 1 | 0
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Mains > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Mains > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90820001 | Mains > Supervision | Mains error | DO |  | BOOL_NUM | 0 | 1 | 0
90820002 | Mains > Supervision | Mains recovery fast | DO |  | BOOL_NUM | 0 | 1 | 0
90820003 | Mains > Supervision | Mains recovery slow | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70350002 | Regulators > GOV > State | Enter operation ramp active | DO |  | BOOL_NUM | 0 | 1 | 0
70350003 | Regulators > GOV > State | Operation ramp 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
70350004 | Regulators > GOV > State | Deload ramp active | DO |  | BOOL_NUM | 0 | 1 | 0
70350005 | Regulators > GOV > State | Operation ramp 2 active | DO |  | BOOL_NUM | 0 | 1 | 0
70350006 | Regulators > GOV > State | Operation ramp 3 active | DO |  | BOOL_NUM | 0 | 1 | 0
70350007 | Regulators > GOV > State | Operation ramp 4 active | DO |  | BOOL_NUM | 0 | 1 | 0
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
20280002 | Breakers > Mains breaker > Controls | MB open | DO |  | BOOL_NUM | 0 | 1 | 0
20280003 | Breakers > Mains breaker > Controls | MB close | DO |  | BOOL_NUM | 0 | 1 | 0
20280014 | Breakers > Mains breaker > State | MB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20280015 | Breakers > Mains breaker > State | MB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20280024 | Breakers > Mains breaker > State | MB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20280025 | Breakers > Mains breaker > State | MB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20280026 | Breakers > Mains breaker > State | MB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
32200000 | Auxiliary > Ground relay | Ground relay A | DO |  | BOOL_NUM | 0 | 1 | 0 | X
32200001 | Auxiliary > Ground relay | Ground relay B | DO |  | BOOL_NUM | 0 | 1 | 0 | X
33020000 | Auxiliary > Close before excitation | CBE AVR relay | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035019 | Alarm system > State | Any MB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035027 | Alarm system > State | Any controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
86010010 | Grid code > RRCR | RRCR output 1 | DO | Undefined | BOOL_NUM | 0 | 1 | 0
86010011 | Grid code > RRCR | RRCR output 2 | DO | Undefined | BOOL_NUM | 0 | 1 | 0
86010012 | Grid code > RRCR | RRCR output 3 | DO | Undefined | BOOL_NUM | 0 | 1 | 0
86010013 | Grid code > RRCR | RRCR output 4 | DO | Undefined | BOOL_NUM | 0 | 1 | 0
86090001 | Grid code > Mains sync inhibit | Recovery delay 1 | DO |  | BOOL_NUM | 0 | 1 | 0
86090002 | Grid code > Mains sync inhibit | Recovery delay 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
40140000 | Mains > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1
40140001 | Mains > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1
40140002 | Mains > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1
86037500 | Mains > Analogue | Connection point voltage measurement | AI | V | FLOAT | -32768 | 32767 | 1
70100035 | Mains > External set points | Power set point | AI | % | FLOAT | 0 | 100 | 0
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
86070000 | Grid code > Reactive power regulation | Ramp switch timer | AI | s | FLOAT | 0 | 600 | 1
86070001 | Grid code > Reactive power regulation | External control U-shift | AI |  | FLOAT | -0.2 | 0.2 | 3
86070002 | Grid code > Reactive power regulation | External control Q-shift | AI |  | FLOAT | -0.4 | 0.4 | 2
86070003 | Grid code > Reactive power regulation | External control fixed cos phi | AI |  | FLOAT | -0.1 | 0.1 | 3
70100034 | Grid code > Frequency offset | Frequency offset | AI | Hz | FLOAT | -2.5 | 2.5 | 1
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Mains > Voltage (V) | Mains ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Mains > Voltage (V) | Mains ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Mains > Voltage (V) | Mains ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Mains > Voltage (V) | Mains ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Mains > Voltage (V) | Mains ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Mains > Voltage (V) | Mains ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Mains > Voltage (V) | Mains ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Mains > Voltage (V) | Mains ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Mains > Voltage (V) | Mains ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Mains > Voltage (V) | Mains ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Mains > Voltage (V) | Mains ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Mains > Voltage (V) | Mains ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Mains > Voltage (V) | Mains ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Mains > Voltage (V) | Mains ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Mains > Voltage (V) | Mains ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Mains > Voltage (V) | Mains ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Mains > Frequency (f) (from voltage) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Mains > Frequency (f) (from voltage) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Mains > Frequency (f) (from voltage) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Mains > Frequency (f) (from voltage) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Mains > Frequency (f) (from voltage) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Mains > Frequency (f) (from voltage) | Mains ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100024 | Mains > Power (P) | Mains ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100025 | Mains > Power (P) | Mains ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100026 | Mains > Power (P) | Mains ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100027 | Mains > Reactive power (Q) | Mains ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100028 | Mains > Reactive power (Q) | Mains ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100029 | Mains > Reactive power (Q) | Mains ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100030 | Mains > Apparent power (S) | Mains ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100031 | Mains > Apparent power (S) | Mains ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100032 | Mains > Apparent power (S) | Mains ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100018 | Mains > Phase angle | Mains ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Mains > Phase angle | Mains ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Mains > Phase angle | Mains ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100024 | Regulators > GOV | GOV regulator reference | AO | kW | FLOAT | 0 | 10000 | 2
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
70100029 | Regulators > AVR | AVR regulator reference | AO | kvar | FLOAT | -10000 | -10000 | 2
70100067 | Regulators > AVR | Cos phi reference | AO |  | FLOAT | -1 | 1 | 2
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | System power management > Monitoring > Plant | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000000 | 2
110100101 | System power management > Monitoring > Plant | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000000 | 2
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
86070000 | Grid code > Reactive power regulation | Ramp switch timer | AO | s | FLOAT | 0 | 600 | 1

## GENSET parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 1: Engine speed
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 600 | 1
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 600 | 1
Engine > Start sequence > Run coil | During start attempts | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 99 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 100 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 7 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 0
Engine > Start sequence > Crank failure | Delay | FLOAT | 2 | s | 0 | 20 | 1
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Start sequence > Run detection not reached | Run detection not reached | FLOAT | 10 | s | 1 | 1200 | 0
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run start > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 0 | 9900 | 0
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 99 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 10 | 120 | 1
Engine > Stop sequence > Stop failure | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Stop sequence > Externally stopped | Delay | FLOAT | 10 | s | 1 | 1200 | 0
Engine > Stop sequence > Externally stopped | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Idle run stop > Minimum | Use | INT32 | 0 |  | 0 | 1 | 0
Engine > Idle run stop > Minimum | Delay | FLOAT | 18000 | s | 0 | 59940 | 0
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Service timer > Service timer 1 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 2 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 3 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > Maintenance > Service timer > Service timer 4 | Set point | FLOAT | 500 |  | 0 | 9000 | 0
Engine > Maintenance > Service timer > Service timer 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2 |  | X
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2 |  | X
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage, ACM wire break
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Under-voltage 4 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Over-frequency 3 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Under-frequency 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Frequency protections > Under-frequency 4 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Generator
Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Generator
Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Busbar > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0
Regulators > GOV > General configuration > Frequency recovery | Frequency recovery | INT32 | Off |  |  |  |  | 0: Off, 1: Volvo Penta EMS 2.4, 2: Frequency measurement
Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery limit | FLOAT | 3 | Hz | 0 | 20 | 1
Regulators > GOV > General configuration > Frequency recovery limit | Frequency recovery duration | FLOAT | 1 | s | 0 | 10 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Base load | Return mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto
Regulators > GOV > Regulation set points > Base load | Base load | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Base load | Set point | FLOAT | 90 | % | 10 | 120 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Warm up set point | FLOAT | 10 | % | 0.1 | 100 | 1
Regulators > GOV > Regulation set points > Active power ramp configuration | Island ramping | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Enter operation ramp enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Active power ramp configuration | Deload ramp enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 0.5 |  | 0 | 60 | 2
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 3 | s | 0 | 60 | 2
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2500 | ms | 250 | 32500 | 0
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 500 | ms | 10 | 6500 | 0
Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Relay, 1: Analogue / Digital AVR
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 3
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Capacitive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 3
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 60 | 2
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 2 | 2
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 500 | ms | 50 | 15000 | 0
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 100 | ms | 10 | 3000 | 0
Regulators > AVR > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 300 | 1
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Close before excitation > Configuration | Breaker close set point | FLOAT | 400 | RPM | 0 | 4000 | 0
Breakers > Close before excitation > Configuration | Timer crank release to AVR on | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Breakers > Close before excitation > Configuration | Breakers to close | INT32 | Close GB |  |  |  |  | 0: Close GB, 1: Close GB and TB
Breakers > Close before excitation > Configuration | Soft-start timer | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > Configuration | Minimum RPM for excitation | FLOAT | 1450 | RPM | 0 | 4000 | 0
Breakers > Close before excitation > Configuration | Voltage discharge timer for GB close | FLOAT | 5 | s | 1 | 20 | 1
Breakers > Close before excitation > Configuration | Maximum rerun voltage for GB close | FLOAT | 30 | % | 30 | 100 | 0
Breakers > Close before excitation > Configuration | Excitation control during cooldown | INT32 | Excitation follow U busbar |  |  |  |  | 0: Excitation follow U busbar, 1: Excitation constant ON, 2: Excitation OFF
Breakers > Close before excitation > CBE failure | Delay | FLOAT | 5 | s | 0 | 999 | 1
Breakers > Close before excitation > CBE failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Close before excitation > CBE rerun failure | Delay | FLOAT | 120 | s | 0 | 999 | 1
Breakers > Close before excitation > CBE rerun failure | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine, 2: Open MB at ready engine
Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1
Local power management > Genset test > Settings | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
Local power management > Genset test > Settings | Base load | FLOAT | 80 | % | 1 | 100 | 0
Local power management > Genset test > Settings | Mode | INT32 | No mode change |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change, 3: No regulation
Local power management > Genset test > Settings | Test time | FLOAT | 300 | s | 0 | 59940 | 0
Power management rules > Plant/genset mode > Modes | Genset mode | INT32 | Power management |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over, 6: Power management
Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
Power management rules > Mains power > Peak shaving | Start generator | FLOAT | 80 | % | 5 | 100 | 0
Power management rules > Mains power > Peak shaving | Minimum load | FLOAT | 5 | % | 0 | 100 | 0
Power management rules > Mains power > Peak shaving | Stop generator | FLOAT | 60 | % | 0 | 80 | 0
Power management rules > Mains power > Peak shaving | Start delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Mains power > Peak shaving | Stop delay | FLOAT | 30 | s | 0 | 990 | 1
Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Common power factor control | Controller settings Q | FLOAT | 0 | % | -100 | 100 | 0
Power management rules > Mains power > Common power factor control | Controller settings cos phi or Q | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 3: Superior, 4: Fixed Q
Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Ground relay > Enable | Ground relay | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Ground relay > Ground relay configuration | Relay type | INT32 | Continuous |  |  |  |  | 0: Continuous, 1: Pulse
Power management rules > Ground relay > Ground relay configuration | Close configuration | INT32 | Hz/V OK |  |  |  |  | 0: Hz/V OK, 1: RPM MPU level, 2: RPM EIC level, 3: Start active
Power management rules > Ground relay > Ground relay configuration | Open configuration | INT32 | After cooldown |  |  |  |  | 0: After cooldown, 1: After extended stop
Power management rules > Ground relay > Ground relay configuration | RPM level | FLOAT | 1000 | RPM | 0 | 4000 | 0
Power management rules > Ground relay > Ground relay general failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
Power management rules > Ground relay > Ground relay general failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Ground relay > Ground relay open failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
Power management rules > Ground relay > Ground relay open failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Ground relay > Ground relay close failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
Power management rules > Ground relay > Ground relay close failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Ground relay > Ground relay position failure | Delay | FLOAT | 1 | s | 1 | 30 | 1
Power management rules > Ground relay > Ground relay position failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Power management rules > Number of gensets connected > Minimum set 1 | Set point | FLOAT | 1 |  | 0 | 32 | 0
Power management rules > Number of gensets connected > Minimum set 2 | Set point | FLOAT | 1 |  | 0 | 32 | 0
Power management rules > Number of gensets connected > Automatic start | Multi-start set 1 | INT32 | Auto calculation |  |  |  |  | 0: Auto calculation, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined], 9: [User defined], 10: [User defined], 11: [User defined], 12: [User defined], 13: [User defined], 14: [User defined], 15: [User defined], 16: [User defined], 17: [User defined], 18: [User defined], 19: [User defined], 20: [User defined], 21: [User defined], 22: [User defined], 23: [User defined], 24: [User defined], 25: [User defined], 26: [User defined], 27: [User defined], 28: [User defined], 29: [User defined], 30: [User defined], 31: [User defined], 32: [User defined]
Power management rules > Number of gensets connected > Automatic start | Multi-start set 2 | INT32 | [User defined] |  |  |  |  | 0: Auto calculation, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined], 9: [User defined], 10: [User defined], 11: [User defined], 12: [User defined], 13: [User defined], 14: [User defined], 15: [User defined], 16: [User defined], 17: [User defined], 18: [User defined], 19: [User defined], 20: [User defined], 21: [User defined], 22: [User defined], 23: [User defined], 24: [User defined], 25: [User defined], 26: [User defined], 27: [User defined], 28: [User defined], 29: [User defined], 30: [User defined], 31: [User defined], 32: [User defined]
Power management rules > Number of gensets connected > Selection | Multi-start selection | INT32 | Multi-start set 1 |  |  |  |  | 0: Multi-start set 1, 1: Multi-start set 2
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0
Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA
Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1
Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1
Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0
Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1
Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0
Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined]
System power management > Priority > Selection | Method | INT32 | Manual absolute |  |  |  |  | 0: Manual absolute, 1: Total running hours, 2: Fuel optimisation, 3: Manual relative, 4: Running hours relative, 5: Fuel optimisation + running hours
System power management > Priority > Selection | Transmit | INT32 | Off |  |  |  |  | 0: Off, 2: Running hours
System power management > Priority > Running hours | Activate priority update | FLOAT | 175 | h | 1 | 20000 | 0
System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled
System power management > Store common settings > Settings | Store common settings | INT32 | 0 |  | 0 | 1 | 0
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > Mode while controller missing | Mode | INT32 | No regulation |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1
System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
System > Plant > Update | Application to broadcast | FLOAT | [User defined] |  |  |  |  | 1: [User defined]
System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 13: Controlled stop

## GENSET IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
11080048 | Engine > Command | Crank delay | DI |  | BOOL_NUM | 0 | 1 | 0
11080049 | Engine > Command | Warm up delay | DI |  | BOOL_NUM | 0 | 1 | 0
11080050 | Engine > Command | Cooldown abort | DI |  | BOOL_NUM | 0 | 1 | 0
11080051 | Engine > Command | De-load genset | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Command | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180004 | Engine > Idle run | Low speed | DI |  | BOOL_NUM | 0 | 1 | 0
11180005 | Engine > Idle run | Temperature control | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
110100030 | Mains > External set points | Activate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100031 | Mains > External set points | Deactivate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100024 | Mains > Set point offsets > Active power | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100025 | Mains > Set point offsets > Active power | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100026 | Mains > Set point offsets > Active power | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110100027 | Mains > Set point offsets > Cos phi | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100028 | Mains > Set point offsets > Cos phi | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100029 | Mains > Set point offsets > Cos phi | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Generator breaker > Command | GB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Generator breaker > Command | GB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
60000510 | Local > Mode | Block | DI |  | BOOL_NUM | 0 | 1 | 0
60000511 | Local > Mode | Test | DI |  | BOOL_NUM | 0 | 1 | 0
60000512 | Local > Mode | No regulation | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
90130017 | System power management > Automatic start | Auto start/stop | DI |  | BOOL_NUM | 0 | 1 | 0
90230005 | System power management > Priority | 1st priority | DI |  | BOOL_NUM | 0 | 1 | 0
32200002 | System power management > Ground relay | Ground relay position feedback A | DI |  | BOOL_NUM | 0 | 1 | 0
32200003 | System power management > Ground relay | Ground relay position feedback B | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0
11080059 | Engine > State | Running indicator | DO |  | BOOL_NUM | 0 | 1 | 0
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70350002 | Regulators > GOV > State | Enter operation ramp active | DO |  | BOOL_NUM | 0 | 1 | 0
70350003 | Regulators > GOV > State | Operation ramp 1 active | DO |  | BOOL_NUM | 0 | 1 | 0
70350004 | Regulators > GOV > State | Deload ramp active | DO |  | BOOL_NUM | 0 | 1 | 0
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
32200000 | Auxiliary > Ground relay | Ground relay A | DO |  | BOOL_NUM | 0 | 1 | 0
32200001 | Auxiliary > Ground relay | Ground relay B | DO |  | BOOL_NUM | 0 | 1 | 0
33020000 | Auxiliary > Close before excitation | CBE AVR relay | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035007 | Alarm system > State | Any PMS-controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035027 | Alarm system > State | Any controlled stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
70100035 | Mains > External set points | Power set point | AI | % | FLOAT | 0 | 100 | 0
40140000 | Busbar > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1 | X
40140001 | Busbar > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1 | X
40140002 | Busbar > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1 | X
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100024 | Regulators > GOV | GOV regulator reference | AO | kW | FLOAT | 0 | 10000 | 2
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
70100029 | Regulators > AVR | AVR regulator reference | AO | kvar | FLOAT | -10000 | -10000 | 2
70100067 | Regulators > AVR | Cos phi reference | AO |  | FLOAT | -1 | 1 | 2
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | System power management > Monitoring > Plant | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000000 | 2
110100101 | System power management > Monitoring > Plant | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000000 | 2
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## MAINS parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Mains breaker open, Tie breaker open | [5 empty] | X
Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Mains > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Mains > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Mains > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
Mains > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1 |  | X
Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0 |  | X
Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0 |  | X
Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2 |  | X
Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2 |  | X
Mains > AC setup > Voltage and frequency OK | Measurement configuration | INT32 | Phase-phase |  |  |  |  | 0: Phase-phase, 1: Phase-neutral, 2: Phase-phase or phase-neutral
Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Mains > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Mains > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Mains > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Mains > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Mains > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Mains > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Mains > Emergency stop > Emergency stop | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Voltage unbalance | Inhibit |  | No mains voltage
Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Mains > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Mains > Current protections > Fast over-current 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Mains > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Mains > Current protections > Fast over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Mains > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Mains > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Mains > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Mains > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Mains > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Mains > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Mains > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Mains > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Mains > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Mains > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Mains > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Mains > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Mains > Current protections > Inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Mains > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Mains > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Mains > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Mains > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 5 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Mains > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Reverse power 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Mains > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Power protections > Reverse power 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
Mains > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Mains > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Mains > Additional protections > V< and Q< 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
Mains > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Mains > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Mains > Additional protections > V< and Q< 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
Mains > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Mains > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Mains > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Mains > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
Mains > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Mains > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Mains > Additional protections > Average over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Mains > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Mains
Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar > Additional protections > Vector shift | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Mains
Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar > Additional protections > ROCOF | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Busbar > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Mains side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU | X
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1 |  | X
Breakers > Close before excitation > Configuration | Breaker close set point | FLOAT | 400 | RPM | 0 | 4000 | 0 |  | X
Breakers > Close before excitation > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Breakers > Short-time parallel > Configuration | Maximum overlap time | FLOAT | 0.3 | s | 0.1 | 99.9 | 2
Breakers > Short-time parallel > Configuration | Overlap | INT32 | Off |  |  |  |  | 0: Off, 1: On
Breakers > Tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Tie breaker normally open/closed | INT32 | Normally open |  |  |  |  | 0: Normally open, 1: Normally closed
Breakers > Tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Tie breaker configuration > Synchronisation failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Closing failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Breakers > Tie breaker monitoring > Tripped (external) | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Tie breaker monitoring > Short circuit | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local power management > Alarms > Busbar blocked | Delay | FLOAT | 1 | s | 1 | 5 | 1
Local power management > Alarms > Busbar blocked | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section
Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains
Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0
Local power management > Mains configuration > Controls | MB failure start | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Controls | Exclude run all | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | MB close delay | FLOAT | 0.5 | s | 0 | 30 | 1
Local power management > Mains configuration > Mains breaker configuration | Back synchronising | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | Synchronisation to mains | INT32 | 1 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | Parallel | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Mains breaker configuration | No break transfer | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Tie breaker configuration | TB de-load before GB | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0
Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low voltage hysteresis | FLOAT | 0 | % | 0 | 70 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage hysteresis | FLOAT | 0 | % | 0 | 20 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Voltage OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low voltage | FLOAT | 90 | % | 30 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | High voltage | FLOAT | 110 | % | 100 | 130 | 0
Local power management > Mains configuration > Voltage and frequency OK | Voltage failure sequence | INT32 | Start engine and open MB |  |  |  |  | 0: Start engine and open MB, 1: Start engine
Local power management > Mains configuration > Voltage and frequency OK | Unbalance voltage | FLOAT | 100 | % | 2 | 100 | 0
Local power management > Mains configuration > Voltage and frequency OK | Frequency failure delay | FLOAT | 5 | s | 0.5 | 990 | 1
Local power management > Mains configuration > Voltage and frequency OK | Frequency OK delay | FLOAT | 60 | s | 2 | 9900 | 0
Local power management > Mains configuration > Voltage and frequency OK | Low frequency | FLOAT | 95 | % | 80 | 100 | 1
Local power management > Mains configuration > Voltage and frequency OK | High frequency | FLOAT | 105 | % | 100 | 120 | 1
Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1 |  | X
Power management rules > Plant/genset mode > Modes | Plant mode | INT32 | Auto mains failure |  |  |  |  | 0: Island operation, 1: Auto mains failure, 2: Peak shaving, 3: Fixed power, 4: Mains power export, 5: Load take over
Power management rules > Plant/genset mode > Modes | Mode shift | INT32 | Off |  |  |  |  | 0: Off, 1: On
Power management rules > Mains power > External set points | Fixed power | FLOAT | 750 | kW | -20000 | 20000 | 0
Power management rules > Mains power > External set points | Percent of nominal | FLOAT | 30 | % | -100 | 100 | 0
Power management rules > Mains power > External set points | Selection | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
Power management rules > Mains power > Mains test | Type | INT32 | Simple test |  |  |  |  | 0: Simple test, 1: Load test, 2: Full test
Power management rules > Mains power > Mains test | Base load | FLOAT | 500 | kW | 1 | 20000 | 0
Power management rules > Mains power > Mains test | Mode | INT32 | Auto |  |  |  |  | 0: Manual, 1: Auto, 2: No mode change
Power management rules > Mains power > Mains test | Test time | FLOAT | 300 | s | 0 | 59940 | 0
Power management rules > Mains power > Common power factor control | Set point | FLOAT | 0.9 |  | 0.7 | 1 | 3
Power management rules > Mains power > Common power factor control | Type | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Common power factor control | Usage | INT32 | Off |  |  |  |  | 0: Off, 1: Fixed for DG(s), 2: Fixed for import/export
Power management rules > Mains power > Active power | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Active power | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Power management rules > Mains power > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Mains power > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
Power management rules > Mains power > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
Power management rules > Short circuit > Short-circuit limitation | Section P> factor | FLOAT | 1 |  | 1 | 25.5 | 1
Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA | X
Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent | X
Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined] | X
System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
System power management > Store common settings > Settings | Store common settings | INT32 | 0 |  | 0 | 1 | 0
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Command mode | Selection | INT32 | Update all |  |  |  |  | 0: Local update, 1: Update all
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > Mode while controller missing | Mode | INT32 | Manual |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1
System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
System > Plant > Update | Application to broadcast | FLOAT | [User defined] |  |  |  |  | 1: [User defined]
System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 3: Trip mains breaker, 4: Trip tie breaker

## MAINS IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130018 | Mains > Command | Start | DI |  | BOOL_NUM | 0 | 1 | 0
90130019 | Mains > Command | Stop | DI |  | BOOL_NUM | 0 | 1 | 0
110100030 | Mains > External set points | Activate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100031 | Mains > External set points | Deactivate external power set point | DI |  | BOOL_NUM | 0 | 1 | 0
110100024 | Mains > Set point offsets > Active power | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100025 | Mains > Set point offsets > Active power | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100026 | Mains > Set point offsets > Active power | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
110100027 | Mains > Set point offsets > Cos phi | Active offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
110100028 | Mains > Set point offsets > Cos phi | Active offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
110100029 | Mains > Set point offsets > Cos phi | Active offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
20280028 | Breakers > Tie breaker > Command | TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280029 | Breakers > Tie breaker > Command | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280031 | Breakers > Tie breaker > Command | Block TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280000 | Breakers > Tie breaker > Feedback | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280001 | Breakers > Tie breaker > Feedback | TB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20280004 | Breakers > Tie breaker > Feedback | TB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20280012 | Breakers > Tie breaker > Feedback | TB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Mains breaker > Command | MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Mains breaker > Command | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Mains breaker > Command | Block MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Mains breaker > Feedback | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Mains breaker > Feedback | MB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Mains breaker > Feedback | MB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Mains breaker > Feedback | MB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
60000510 | Local > Mode | Block | DI |  | BOOL_NUM | 0 | 1 | 0
60000511 | Local > Mode | Test | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
90130017 | System power management > Automatic start | Auto start/stop | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Mains > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Mains > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Mains > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Mains > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Mains > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Mains > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Mains > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Mains > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90820001 | Mains > Supervision | Mains error | DO |  | BOOL_NUM | 0 | 1 | 0
90820002 | Mains > Supervision | Mains recovery fast | DO |  | BOOL_NUM | 0 | 1 | 0
90820003 | Mains > Supervision | Mains recovery slow | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20280002 | Breakers > Tie breaker > Controls | TB open | DO |  | BOOL_NUM | 0 | 1 | 0
20280003 | Breakers > Tie breaker > Controls | TB close | DO |  | BOOL_NUM | 0 | 1 | 0
20280014 | Breakers > Tie breaker > State | TB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20280015 | Breakers > Tie breaker > State | TB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20280024 | Breakers > Tie breaker > State | TB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20280025 | Breakers > Tie breaker > State | TB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20280026 | Breakers > Tie breaker > State | TB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Mains breaker > Controls | MB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Mains breaker > Controls | MB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Mains breaker > State | MB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Mains breaker > State | MB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Mains breaker > State | MB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Mains breaker > State | MB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Mains breaker > State | MB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035011 | Alarm system > State | Any TB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035019 | Alarm system > State | Any MB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
125019000 | Non-essential load trip | Non-essential load trip 1 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125029000 | Non-essential load trip | Non-essential load trip 2 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
125039000 | Non-essential load trip | Non-essential load trip 3 | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100035 | Mains > External set points | Power set point | AI | % | FLOAT | 0 | 100 | 0
40140000 | Busbar > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1
40140001 | Busbar > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1
40140002 | Busbar > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Mains > Voltage (V) | Mains ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Mains > Voltage (V) | Mains ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Mains > Voltage (V) | Mains ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Mains > Voltage (V) | Mains ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Mains > Voltage (V) | Mains ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Mains > Voltage (V) | Mains ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Mains > Voltage (V) | Mains ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Mains > Voltage (V) | Mains ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Mains > Voltage (V) | Mains ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Mains > Voltage (V) | Mains ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Mains > Voltage (V) | Mains ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Mains > Voltage (V) | Mains ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Mains > Voltage (V) | Mains ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Mains > Voltage (V) | Mains ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Mains > Voltage (V) | Mains ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Mains > Voltage (V) | Mains ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Mains > Frequency (f) (from voltage) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Mains > Frequency (f) (from voltage) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Mains > Frequency (f) (from voltage) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Mains > Frequency (f) (from voltage) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Mains > Frequency (f) (from voltage) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Mains > Frequency (f) (from voltage) | Mains ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Mains > Frequency (f) (from current) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Mains > Frequency (f) (from current) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Mains > Frequency (f) (from current) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Mains > Frequency (f) (from current) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Mains > Frequency (f) (from current) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Mains > Current (I) | Mains ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Mains > Current (I) | Mains ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Mains > Current (I) | Mains ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Mains > Current (I) | Mains ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Mains > Current (I) | Mains ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Mains > Current (I) | Mains ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Mains > Current (I) | Mains ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Mains > Current (I) | Mains ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Mains > Current (I) | Mains ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Mains > Current (I) | Mains ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Mains > Current (I) | Mains ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Mains > Power (P) | Mains ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Mains > Power (P) | Mains ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Mains > Power (P) | Mains ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Mains > Power (P) | Mains ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Mains > Power (P) | Mains ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Mains > Power (P) | Mains ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Mains > Power (P) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Mains > Power (P) | Mains ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Mains > Power (P) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Mains > Reactive power (Q) | Mains ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Mains > Reactive power (Q) | Mains ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Mains > Reactive power (Q) | Mains ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Mains > Reactive power (Q) | Mains ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Mains > Reactive power (Q) | Mains ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Mains > Reactive power (Q) | Mains ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Mains > Reactive power (Q) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Mains > Reactive power (Q) | Mains ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Mains > Reactive power (Q) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Mains > Apparent power (S) | Mains ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Mains > Apparent power (S) | Mains ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Mains > Apparent power (S) | Mains ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Mains > Apparent power (S) | Mains ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Mains > Apparent power (S) | Mains ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Mains > Apparent power (S) | Mains ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Mains > Apparent power (S) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Mains > Apparent power (S) | Mains ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Mains > Apparent power (S) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Mains > Power factor (PF) | Mains ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Mains > Power factor (PF) | Mains ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Mains > Phase angle | Mains ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Mains > Phase angle | Mains ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Mains > Phase angle | Mains ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Mains > Phase angle | Mains ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Mains > Phase angle | Mains ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Mains > Phase angle | Mains ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) (from voltage) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) (from voltage) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100024 | Busbar > Power (P) | Busbar ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100025 | Busbar > Power (P) | Busbar ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100026 | Busbar > Power (P) | Busbar ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100027 | Busbar > Reactive power (Q) | Busbar ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100028 | Busbar > Reactive power (Q) | Busbar ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100029 | Busbar > Reactive power (Q) | Busbar ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100030 | Busbar > Apparent power (S) | Busbar ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100031 | Busbar > Apparent power (S) | Busbar ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100032 | Busbar > Apparent power (S) | Busbar ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | System power management > Monitoring > Plant | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000000 | 2
110100101 | System power management > Monitoring > Plant | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000000 | 2
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## BUS TIE breaker parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 3: Single-phase L1
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 45 | 62 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 10 | 20000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 12.5 | 25000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.8 | 1 | 4
Busbar A > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Busbar A > Emergency stop > Emergency stop | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 5 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
Busbar A > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Busbar A > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Busbar A > Additional protections > V< and Q< 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
Busbar A > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Busbar A > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Busbar A > Additional protections > V< and Q< 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
Busbar A > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Busbar A > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar A > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Busbar A > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
Busbar A > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Busbar A > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar A > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Busbar A > Additional protections > Average over-voltage 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 100 | 25000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 100 | 25000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 4 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 3 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 4 | Inhibit |  | ACM wire break
Busbar B > Additional protections > Vector shift | AC setup | INT32 | Busbar B |  |  |  |  | 34: Busbar B, 35: Busbar A
Busbar B > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar B > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar B > Additional protections > Vector shift | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Additional protections > ROCOF | AC setup | INT32 | Busbar B |  |  |  |  | 32: Busbar B, 33: Busbar A
Busbar B > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar B > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar B > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar B > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar B > Additional protections > ROCOF | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar A side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Busbar B side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Relay, 1: Analogue / ECU | X
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 3 | s | 0 | 9900 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Pulse time | FLOAT | 5 | s | 0.1 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 100 | 0 |  | X
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Delay after Hz/V OK before close | FLOAT | 2 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Configuration | BTB supply | INT32 | DC voltage |  |  |  |  | 0: AC voltage, 1: DC voltage
Breakers > Bus tie breaker configuration > Configuration | Tie breaker normally open/closed | INT32 | Normally open |  |  |  |  | 0: Normally open, 1: Normally closed
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local power management > Alarms > Busbar blocked > Busbar A | Delay | FLOAT | 1 | s | 1 | 5 | 1
Local power management > Alarms > Busbar blocked > Busbar A | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local power management > Alarms > Busbar blocked > Busbar B | Delay | FLOAT | 1 | s | 1 | 5 | 1
Local power management > Alarms > Busbar blocked > Busbar B | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local power management > Mains configuration > Controls | Auto switch | INT32 | Off |  |  |  |  | 0: Off, 1: Static section, 2: Dynamic section, 3: All section | X
Local power management > Mains configuration > Controls | Run type | INT32 | Run one mains |  |  |  |  | 0: Run one mains, 1: Run all mains | X
Local power management > Mains configuration > Controls | ID to run | FLOAT | 32 |  | 1 | 32 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | TB open point | FLOAT | 50 | kW | 0 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity set point | FLOAT | 50 | kW | 1 | 20000 | 0 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule delay | FLOAT | 30 | s | 0 | 999.9 | 1 |  | X
Local power management > Mains configuration > Tie breaker configuration | Power capacity overrule enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 10 | 600 | 1 |  | X
Power management rules > Short circuit > Short-circuit limitation | Section P> | INT32 | 0 | kW | 0 | 30000000 | 0
Power management rules > Short circuit > Short-circuit limitation | Delay | FLOAT | 1 | s | 0 | 999 | 1
Power management rules > Short circuit > Short-circuit limitation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Set point | FLOAT | 80 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Configuration | Minimum load | FLOAT | 20 | kW | 0 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Configuration | Power selection | INT32 | kW |  |  |  |  | 0: kW, 1: kVA | X
Power management rules > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent | X
Power management rules > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 1 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Delay | FLOAT | 10 | s | 0 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 20000 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 990 | 1 |  | X
Power management rules > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Power management rules > Power reservation > Reserved power | Set point | FLOAT | 100 | kW | 0 | 30000 | 0 |  | X
Power management rules > Power reservation > N+X | N + X setup | INT32 | N + X OFF |  |  |  |  | 0: N + X OFF, 1: [User defined], 2: [User defined], 3: [User defined], 4: [User defined], 5: [User defined], 6: [User defined], 7: [User defined], 8: [User defined] | X
System power management > Priority > Running hours | Method | INT32 | Total |  |  |  |  | 0: Total, 1: Relative, 2: Load profiled | X
System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > CAN bus configuration > CAN bus configuration mode | CAN bus configuration mode | INT32 | Dual CAN (CAN A + B) |  |  |  |  | 0: Single CAN (CAN A only), 1: Dual CAN (CAN A + B) | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Remote control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Restore last |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Single-line hazard | Delay | FLOAT | 10 | s | 10 | 10 | 1 |  | X
System > Monitoring > Single-line hazard | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing any genset controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing any mains controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing any bustie controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing controllers | Missing controllers | FLOAT | 2 |  | 2 | 32 | 0
System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Mode while controller missing | Mode | INT32 | Manual |  |  |  |  | 0: No regulation, 1: Manual, 2: No mode change
System > Monitoring > BTB 33 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 33 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 34 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 34 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 35 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 35 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 36 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 36 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 37 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 37 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 38 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 38 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 39 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 39 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Monitoring > BTB 40 position failure | Delay | FLOAT | 2 | s | 1 | 5 | 1 |  | X
System > Monitoring > BTB 40 position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Plant > Update | Broadcast application | INT32 | Off |  |  |  |  | 0: Off, 1: On, 2: On + activate
System > Plant > Update | Application to broadcast | FLOAT | [User defined] |  |  |  |  | 1: [User defined]
System > Application selector | Application selector | INT32 | LC |  |  |  |  | 800000: LF, 800001: LC, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker

## BUS TIE breaker IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000500 | Local > Mode | MANUAL | DI |  | BOOL_NUM | 0 | 1 | 0
60000501 | Local > Mode | AUTO | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
60000510 | Local > Mode | Block | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000504 | Local > Mode | In MANUAL | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40140000 | Busbar B > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1 | X
40140001 | Busbar B > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1 | X
40140002 | Busbar B > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) (from voltage) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100100 | System power management > Monitoring > Plant | Section ¦ PMS P avail. | AO | kW | FLOAT | 0 | 10000000 | 2
110100101 | System power management > Monitoring > Plant | Section ¦ PMS P used | AO | kW | FLOAT | 0 | 10000000 | 2
100097000 | Hardware > Power supply > PCM2.1 | PCM2.1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1