## About
iE 250 Marine Power management Parameter lists
Software version
The information contained in these parameter lists (Revision A) are applicable to software version 2.0.17.x of the iE 250 Marine Power management.
Controller types
This document includes parameter lists for these controller types:
GENSET controller
HYBRID controller
EMERGENCY genset controller
SHAFT generator controller
SHORE connection controller
BUS TIE breaker controller
More information
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
See the iE 250 Marine Power management Designer's handbook for more information.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include I/O functions, and Fieldbus settings. These are not included in the parameter lists.

## GENSET
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40030110 | Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40175110 | Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40180110 | Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40185110 | Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
100010002 | Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11200030 | Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 3: Oil pressure, 1: Engine speed
11200040 | Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
11200010 | Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
11200000 | Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
11200100 | Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
11200070 | Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
11200020 | Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1
11200090 | Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0
11200052 | Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
11200053 | Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000182 | Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
11000183 | Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000184 | Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
11000000 | Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
11000050 | Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
11000030 | Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1
11000040 | Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on
11000010 | Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
11000020 | Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
11200060 | Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
11000230 | Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated
11000210 | Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
11000220 | Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
11000113 | Engine > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000120 | Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
11000122 | Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
11000123 | Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11000203 | Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
12000003 | Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11100000 | Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11120000 | Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
11100010 | Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
11100300 | Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100310 | Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
11100200 | Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100210 | Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
11100400 | Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100100 | Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100110 | Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
11000060 | Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
11000090 | Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
11000070 | Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0
11000080 | Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
11000102 | Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
11000103 | Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000193 | Engine > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11110000 | Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11110010 | Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
11110300 | Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110310 | Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
11110200 | Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110210 | Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
11110400 | Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110100 | Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110110 | Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
11000140 | Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
11000141 | Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000142 | Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000143 | Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000150 | Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
11000151 | Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000152 | Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000153 | Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000160 | Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
11000161 | Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000162 | Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000163 | Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000164 | Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
11000170 | Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
11000171 | Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000172 | Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000173 | Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000174 | Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
11001000 | Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1
11001001 | Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001002 | Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001003 | Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001004 | Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running
11001010 | Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1
11001011 | Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001012 | Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1
11001013 | Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001014 | Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running
11001020 | Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1
11001021 | Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001022 | Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001023 | Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001030 | Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1
11001031 | Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001032 | Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001033 | Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001040 | Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1
11001041 | Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001042 | Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001043 | Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001050 | Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1
11001051 | Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001052 | Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001053 | Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001060 | Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1
11001061 | Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001062 | Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001063 | Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001070 | Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1
11001071 | Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001072 | Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001073 | Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001080 | Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1
11001081 | Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001082 | Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001083 | Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001090 | Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1
11001091 | Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001092 | Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001093 | Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40600500 | Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11400000 | Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11400020 | Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
11400010 | Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
11300020 | Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300023 | Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11300050 | Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300053 | Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000070 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000240 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Use nominal RPM as reference | INT32 | 0 |  | 0 | 1 | 0
170000080 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000730 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Destination address | INT32 | 0 |  | 0 | 255 | 0
170000090 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000100 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Source address | INT32 | 234 |  | 0 | 255 | 0
170000120 | Engine > ECU > Controls > Cab message (CM1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000270 | Engine > ECU > Controls > CAN controls | Enable | INT32 | 1 |  | 0 | 1 | 0
170000410 | Engine > ECU > Controls > Droop | Droop settings | INT32 | None |  |  |  |  | 0: None, 2: Emulated droop
170000420 | Engine > ECU > Controls > Droop | Droop value | FLOAT | 4 | % | 0 | 25 | 1
170000610 | Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0
170000003 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000013 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000023 | Engine > ECU > Diagnostic alarms > ECU Protect lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000033 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000173 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp (ECU2) | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000183 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000193 | Engine > ECU > Diagnostic alarms > ECU Protect lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000203 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000320 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Inhibit Switch | INT32 | 0 |  | 0 | 1 | 0
170000330 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Force Switch | INT32 | Automatic |  |  |  |  | 0: Automatic, 1: Forced
11001500 | Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
11001510 | Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
11200080 | Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
11000280 | Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
11000290 | Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
11000300 | Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
11000310 | Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
11800000 | Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
11800010 | Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
11800020 | Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
11800030 | Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
40310000 | Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410130 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410140 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
40410150 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
40410160 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
40410102 | Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
40410070 | Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100082 | Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100092 | Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100102 | Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100042 | Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40030000 | Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
46010010 | Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010004 | Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker closed
46010110 | Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010104 | Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker closed
46010210 | Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010204 | Generator > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker closed
46000010 | Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000004 | Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
46000110 | Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000104 | Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
46000210 | Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000204 | Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
46020010 | Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46020004 | Generator > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46030204 | Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46030100 | Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46040000 | Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46040100 | Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46050000 | Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46050100 | Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46060000 | Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46060100 | Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46070000 | Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46070100 | Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
45300070 | Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46080000 | Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46080100 | Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090000 | Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090004 | Generator > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker closed
46090100 | Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090104 | Generator > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker closed
46100000 | Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46100004 | Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
46100100 | Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46100104 | Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, Generator breaker closed, Idle run active
46110000 | Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46110100 | Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46110200 | Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46120000 | Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
46120001 | Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120003 | Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46120100 | Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
46120101 | Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46120103 | Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46130000 | Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46130100 | Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46140000 | Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140001 | Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46140100 | Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
46140101 | Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40210010 | Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210020 | Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210010 | Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126210030 | Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210050 | Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210040 | Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126210060 | Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210080 | Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210070 | Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126210090 | Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210000 | Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126210100 | Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126210110 | Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
126220020 | Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220010 | Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126220030 | Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220050 | Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220040 | Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126220060 | Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220080 | Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220070 | Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126220090 | Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220000 | Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126220100 | Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126220110 | Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100052 | Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100062 | Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100072 | Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90100032 | Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46170004 | Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
70000780 | Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 1: Analogue / ECU, 2: Relay
70000560 | Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
80000040 | Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000022 | Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000023 | Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000800 | Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
70000820 | Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0
70000790 | Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70000810 | Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70001480 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
70001490 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
40030120 | Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175120 | Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180120 | Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185120 | Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000100 | Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000110 | Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000120 | Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000130 | Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000140 | Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000150 | Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000160 | Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000180 | Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000190 | Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000200 | Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000040 | Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000050 | Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000060 | Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000070 | Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000080 | Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000090 | Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000490 | Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1
70000000 | Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
70000010 | Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
70000950 | Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70001360 | Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
70001370 | Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
70001380 | Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70000230 | Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000240 | Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000270 | Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000280 | Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000290 | Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000300 | Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000250 | Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000260 | Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000210 | Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000220 | Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000520 | Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000522 | Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
70000523 | Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
70000590 | Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
70000592 | Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
70000593 | Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
70000770 | Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
70001010 | Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
80000050 | Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000032 | Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000033 | Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000840 | Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000860 | Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000880 | Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000830 | Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000850 | Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000870 | Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000990 | Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001420 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
70001430 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001440 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
70001450 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001460 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
70001470 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
70001040 | Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
40030130 | Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40175130 | Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40180130 | Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40185130 | Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
70000350 | Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000360 | Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000370 | Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000320 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000330 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000340 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000170 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000380 | Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000390 | Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000400 | Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000480 | Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
70000020 | Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
70000030 | Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
70000960 | Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70001390 | Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
70001400 | Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
70001410 | Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70000410 | Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000420 | Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000430 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000440 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
70000470 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000310 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000450 | Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000460 | Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000530 | Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
70000532 | Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
70000533 | Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000600 | Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
70000602 | Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
70000603 | Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
20100000 | Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000020 | Breakers > Generator breaker configuration > Configuration | Generator breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
3300070 | Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100092 | Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
3300090 | Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100052 | Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100042 | Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100062 | Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100072 | Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
20100123 | Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100133 | Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110700002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110700042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100002 | Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1 |  | X
90100003 | Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000300 | Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
90200022 | Local power management > Parallel timers > DG-SG max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
90200023 | Local power management > Parallel timers > DG-SG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90200032 | Local power management > Parallel timers > DG-SC max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
90200033 | Local power management > Parallel timers > DG-SC max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90200040 | Local power management > Non-connected genset > Stop timer | Delay | FLOAT | 60 | s | 0 | 3600 | 0
90200000 | Local power management > Asymmetric load sharing > P configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
90200050 | Local power management > Asymmetric load sharing > P configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
90200010 | Local power management > Asymmetric load sharing > P configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
90200070 | Local power management > Asymmetric load sharing > Q configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
90200060 | Local power management > Asymmetric load sharing > Q configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
90200080 | Local power management > Asymmetric load sharing > Q configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
90200100 | Local power management > Blackout > Blackout close | Allow blackout recovery | INT32 | 1 |  | 0 | 1 | 0
90100010 | Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
90100020 | Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
126000040 | Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
126000000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99 | % | 90 | 110 | 1
126002000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126002002 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002003 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
126000010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 101 | % | 90 | 110 | 1
126002010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126002012 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002013 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
126000020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99 | % | 90 | 110 | 1
126002020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126002022 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002023 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
126000030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 101 | % | 90 | 110 | 1
126002030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126002032 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002033 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90200090 | Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
11500050 | Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11500022 | Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11500023 | Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11500060 | Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11500000 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11500030 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11500010 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11500040 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600050 | Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11600022 | Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11600023 | Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11600060 | Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11600000 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11600030 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600010 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11600040 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700050 | Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11700022 | Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11700023 | Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11700060 | Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11700000 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11700030 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700010 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11700040 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
170000050 | Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON
170000060 | Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1
170000042 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1
170000043 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
190000320 | Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
191000022 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
191000023 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110000080 | System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
110002012 | System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
110002013 | System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine

## EMERGENCY genset
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40030110 | Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40175110 | Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40180110 | Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40185110 | Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
100010002 | Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11200030 | Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 3: Oil pressure, 1: Engine speed
11200040 | Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
11200010 | Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
11200000 | Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
11200100 | Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
11200070 | Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
11200020 | Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1
11200090 | Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0
11200052 | Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
11200053 | Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000182 | Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
11000183 | Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000184 | Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
11000000 | Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
11000050 | Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
11000030 | Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1
11000040 | Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on
11000010 | Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
11000020 | Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
11200060 | Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
11000230 | Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated
11000210 | Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
11000220 | Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
11000113 | Engine > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000120 | Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
11000122 | Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
11000123 | Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11000203 | Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
12000003 | Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11100000 | Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11120000 | Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
11100010 | Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
11100300 | Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100310 | Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
11100200 | Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100210 | Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
11100400 | Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100100 | Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11100110 | Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
11000060 | Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
11000090 | Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
11000070 | Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0
11000080 | Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
11000102 | Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
11000103 | Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000193 | Engine > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11110000 | Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11110010 | Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
11110300 | Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110310 | Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
11110200 | Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110210 | Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
11110400 | Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110100 | Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
11110110 | Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
11000140 | Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
11000141 | Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000142 | Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000143 | Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000150 | Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
11000151 | Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000152 | Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000153 | Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000160 | Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
11000161 | Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000162 | Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000163 | Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000164 | Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active
11000170 | Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
11000171 | Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000172 | Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000173 | Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11000174 | Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active
11001000 | Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1
11001001 | Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001002 | Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001003 | Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001004 | Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running
11001010 | Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1
11001011 | Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001012 | Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1
11001013 | Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001014 | Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running
11001020 | Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1
11001021 | Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001022 | Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001023 | Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001030 | Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1
11001031 | Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001032 | Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001033 | Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001040 | Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1
11001041 | Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001042 | Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001043 | Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001050 | Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1
11001051 | Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001052 | Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001053 | Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001060 | Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1
11001061 | Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001062 | Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001063 | Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001070 | Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1
11001071 | Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001072 | Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001073 | Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001080 | Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1
11001081 | Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001082 | Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001083 | Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11001090 | Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1
11001091 | Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001092 | Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001093 | Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40600500 | Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11400000 | Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
11400020 | Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
11400010 | Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
11300020 | Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300023 | Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
11300050 | Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300053 | Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000070 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000240 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Use nominal RPM as reference | INT32 | 0 |  | 0 | 1 | 0
170000080 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000730 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Destination address | INT32 | 0 |  | 0 | 255 | 0
170000090 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000100 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Source address | INT32 | 234 |  | 0 | 255 | 0
170000120 | Engine > ECU > Controls > Cab message (CM1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000270 | Engine > ECU > Controls > CAN controls | Enable | INT32 | 1 |  | 0 | 1 | 0
170000410 | Engine > ECU > Controls > Droop | Droop settings | INT32 | None |  |  |  |  | 0: None, 2: Emulated droop
170000420 | Engine > ECU > Controls > Droop | Droop value | FLOAT | 4 | % | 0 | 25 | 1
170000610 | Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0
170000003 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000013 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000023 | Engine > ECU > Diagnostic alarms > ECU Protect lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000033 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000173 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp (ECU2) | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000183 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000193 | Engine > ECU > Diagnostic alarms > ECU Protect lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000203 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
170000320 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Inhibit Switch | INT32 | 0 |  | 0 | 1 | 0
170000330 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Force Switch | INT32 | Automatic |  |  |  |  | 0: Automatic, 1: Forced
11001500 | Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
11001510 | Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
11200080 | Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
11000280 | Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
11000290 | Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
11000300 | Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
11000310 | Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
11800000 | Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
11800010 | Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
11800020 | Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
11800030 | Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
40310000 | Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410130 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410140 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
40410150 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
40410160 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
40410102 | Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
40410070 | Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
40030000 | Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
46010010 | Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010004 | Generator > Voltage protections > Over-voltage 1 | Inhibit |  | EDG in parallel
46010110 | Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010104 | Generator > Voltage protections > Over-voltage 2 | Inhibit |  | EDG in parallel
46010210 | Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46010204 | Generator > Voltage protections > Over-voltage 3 | Inhibit |  | EDG in parallel
46000010 | Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000004 | Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
46000110 | Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000104 | Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
46000210 | Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46000204 | Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
46020010 | Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46030200 | Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46030000 | Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46030100 | Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46040000 | Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46040100 | Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46050000 | Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46050100 | Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46060000 | Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46060100 | Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46070000 | Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46070100 | Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
45300070 | Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46080000 | Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46080100 | Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090000 | Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090004 | Generator > Frequency protections > Over-frequency 1 | Inhibit |  | EDG in parallel
46090100 | Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46090104 | Generator > Frequency protections > Over-frequency 2 | Inhibit |  | EDG in parallel
46100000 | Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46100004 | Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
46100100 | Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46100104 | Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, EDG in parallel, Idle run active
46110000 | Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46110100 | Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46110200 | Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46120000 | Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
46120001 | Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120003 | Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46120100 | Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
46120101 | Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46120103 | Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46130000 | Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46130100 | Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46140000 | Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140001 | Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46140100 | Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
46140101 | Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40210010 | Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Generator breaker open, Tie breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210020 | Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210010 | Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126210030 | Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210050 | Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210040 | Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126210060 | Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210080 | Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210070 | Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126210090 | Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210000 | Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126210100 | Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126210110 | Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
126220020 | Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220010 | Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126220030 | Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220050 | Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220040 | Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126220060 | Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220080 | Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220070 | Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126220090 | Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220000 | Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126220100 | Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126220110 | Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 15 | s | 0 | 3600 | 1
90600110 | Busbar > AC setup > Blackout detection | TB under-voltage timer | FLOAT | 15 | s | 0 | 3600 | 0
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 5 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open, Tie breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open, Tie breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open, Tie breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, Tie breaker open
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, Tie breaker open
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, Tie breaker open
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open, Tie breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open, Tie breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, Tie breaker open
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, Tie breaker open
70000780 | Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 1: Analogue / ECU, 2: Relay
70000560 | Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
80000040 | Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000022 | Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000023 | Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000800 | Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
70000820 | Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0
70000790 | Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70000810 | Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70001480 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
70001490 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
40030120 | Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
40175120 | Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
40180120 | Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
40185120 | Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
70000100 | Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000110 | Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000120 | Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000130 | Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000140 | Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000150 | Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000160 | Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000180 | Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000190 | Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000200 | Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000040 | Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000050 | Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000060 | Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000070 | Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
70000080 | Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
70000090 | Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
70000490 | Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1
70000000 | Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
70000010 | Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
70000950 | Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70001360 | Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
70001370 | Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
70001380 | Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70000230 | Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000240 | Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000270 | Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000280 | Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000290 | Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000300 | Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000250 | Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000260 | Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000210 | Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000220 | Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000520 | Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000522 | Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
70000523 | Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
70000590 | Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
70000592 | Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
70000593 | Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
70000770 | Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
70001010 | Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
80000050 | Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000032 | Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000033 | Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000840 | Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000860 | Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000880 | Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000830 | Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000850 | Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000870 | Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000990 | Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001420 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
70001430 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001440 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
70001450 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001460 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
70001470 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
70001040 | Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
40030130 | Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40175130 | Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40180130 | Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40185130 | Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
70000350 | Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000360 | Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000370 | Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000320 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000330 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000340 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000170 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000380 | Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000390 | Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000400 | Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000480 | Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
70000020 | Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
70000030 | Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
70000960 | Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70001390 | Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
70001400 | Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
70001410 | Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70000410 | Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000420 | Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000430 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000440 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
70000470 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000310 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000450 | Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000460 | Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000530 | Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
70000532 | Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
70000533 | Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
70000600 | Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
70000602 | Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
70000603 | Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
20100000 | Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000020 | Breakers > Generator breaker configuration > Configuration | Generator breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1
3300070 | Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100092 | Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
3300090 | Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100052 | Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100042 | Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100062 | Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100072 | Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
20100123 | Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20100133 | Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200000 | Breakers > Tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20200010 | Breakers > Tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20200020 | Breakers > Tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20200030 | Breakers > Tie breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20200110 | Breakers > Tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000000 | Breakers > Tie breaker configuration > Configuration | Tie breaker sync enabled | INT32 | 1 |  | 0 | 1 | 0
25000030 | Breakers > Tie breaker configuration > Configuration | Tie breaker transfer delay | FLOAT | 0.5 | s | 0 | 10 | 1
3310070 | Breakers > Tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3310080 | Breakers > Tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3310000 | Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.1 | Hz | -2 | 2 | 2
3310010 | Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3310020 | Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3310030 | Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3310040 | Breakers > Tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3310050 | Breakers > Tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3310060 | Breakers > Tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20200082 | Breakers > Tie breaker configuration > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20200083 | Breakers > Tie breaker configuration > Synchronisation failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200092 | Breakers > Tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20200093 | Breakers > Tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
3310090 | Breakers > Tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3310092 | Breakers > Tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3310093 | Breakers > Tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200052 | Breakers > Tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200053 | Breakers > Tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200042 | Breakers > Tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20200043 | Breakers > Tie breaker monitoring > Closing failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200062 | Breakers > Tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20200063 | Breakers > Tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200072 | Breakers > Tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20200073 | Breakers > Tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
20200123 | Breakers > Tie breaker monitoring > Tripped (external) | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
20200133 | Breakers > Tie breaker monitoring > Short circuit | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100002 | Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1
90100003 | Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000300 | Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
90600082 | Local power management > Parallel timers > EDG max. parallel time | Delay | FLOAT | 30 | s | 0.1 | 3600 | 1
90600083 | Local power management > Parallel timers > EDG max. parallel time | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
90100010 | Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
90100020 | Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
90600030 | Local power management > Return modes > After EDG test | Mode | INT32 | Auto |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
90600040 | Local power management > Emergency generator > Test delay | Test time | FLOAT | 30 | s | 10 | 3600 | 0
90600020 | Local power management > Emergency generator > Test base load | Base load | FLOAT | 50 | % | 10 | 100 | 1
90600010 | Local power management > Emergency generator > Test type | Type | INT32 | Engine test |  |  |  |  | 0: Engine test, 1: Parallel test, 2: Load take-over test
90600000 | Local power management > Emergency generator > Blackout handling | Blackout control | INT32 | Open TB and start engine |  |  |  |  | 0: Open TB and start engine, 1: Start engine and open TB
90600092 | Local power management > Emergency generator > EDG not ready for blackout | Delay | FLOAT | 7 | s | 1 | 180 | 1
90600093 | Local power management > Emergency generator > EDG not ready for blackout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
90600100 | Local power management > Emergency generator > Operator confirms harbour operation | Enable | INT32 | 1 |  | 0 | 1 | 0
90600120 | Local power management > Emergency generator > Solo supply harbour operation | Enable | INT32 | 0 |  | 0 | 1 | 0
90200090 | Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
11500050 | Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11500022 | Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11500023 | Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11500060 | Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11500000 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11500030 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11500010 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11500040 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600050 | Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11600022 | Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11600023 | Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11600060 | Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11600000 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11600030 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600010 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11600040 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700050 | Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11700022 | Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11700023 | Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
11700060 | Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11700000 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11700030 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700010 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11700040 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
170000050 | Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON
170000060 | Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1
170000042 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1
170000043 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
190000320 | Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
191000022 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
191000023 | Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110000080 | System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
110002012 | System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
110002013 | System > Monitoring > Blackout detection mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip generator breaker, 4: Trip tie breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine

## HYBRID
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
13000000 | Inverter > Start sequence > Restrictions | Allow start when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
11000010 | Inverter > Start sequence > Start | Start on | FLOAT | 5 | s | 1 | 180 | 1
11000113 | Inverter > Start sequence > Start failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
11000203 | Inverter > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
13000010 | Inverter > Stop sequence > Restrictions | Allow stop when | INT32 | Breaker is open |  |  |  |  | 0: Breaker is open, 1: Breaker is closed, 2: Breaker in any state
11000102 | Inverter > Stop sequence > Stop failure | Delay | FLOAT | 5 | s | 0 | 300 | 0
11000103 | Inverter > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
11000193 | Inverter > Stop sequence > Externally stopped | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40600500 | Inverter > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Inverter > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Inverter > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Inverter > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11300020 | Inverter > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300023 | Inverter > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
11300050 | Inverter > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300053 | Inverter > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40310000 | Inverter > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Inverter > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Inverter > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Inverter > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Inverter > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Inverter > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Inverter > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Inverter > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Inverter > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Inverter > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Inverter > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Inverter > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410130 | Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410140 | Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
40410150 | Inverter > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
40410160 | Inverter > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
40410102 | Inverter > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Inverter > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
40410070 | Inverter > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Inverter > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Inverter > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90100082 | Inverter > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Inverter > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100092 | Inverter > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Inverter > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100102 | Inverter > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Inverter > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100042 | Inverter > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Inverter > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40030000 | Inverter > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Inverter > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Inverter > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Inverter > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Inverter > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Inverter > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Inverter > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Inverter > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Inverter > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Inverter > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Inverter > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Inverter > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Inverter > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Inverter > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Inverter > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Inverter > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Inverter > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Inverter > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Inverter > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Inverter > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Inverter > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Inverter > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Inverter > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Inverter > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Inverter > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Inverter > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Inverter > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Inverter > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Inverter > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Inverter > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Inverter > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Inverter > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
100010002 | Inverter > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
100010003 | Inverter > Emergency stop > Emergency stop | Action | INT32 | Trip breaker and stop inverter |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46010010 | Inverter > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Inverter > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Inverter > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Inverter > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Inverter > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46010004 | Inverter > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker closed
46010110 | Inverter > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Inverter > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Inverter > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Inverter > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Inverter > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46010104 | Inverter > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker closed
46010210 | Inverter > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Inverter > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Inverter > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Inverter > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Inverter > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46010204 | Inverter > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker closed
46000010 | Inverter > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Inverter > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Inverter > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Inverter > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Inverter > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46000004 | Inverter > Voltage protections > Under-voltage 1 | Inhibit |  | Inverter not running, Breaker closed
46000110 | Inverter > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Inverter > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Inverter > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Inverter > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Inverter > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46000104 | Inverter > Voltage protections > Under-voltage 2 | Inhibit |  | Inverter not running, Breaker closed
46000210 | Inverter > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Inverter > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Inverter > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Inverter > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Inverter > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46000204 | Inverter > Voltage protections > Under-voltage 3 | Inhibit |  | Inverter not running, Breaker closed
46020010 | Inverter > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Inverter > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Inverter > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Inverter > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Inverter > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46020004 | Inverter > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Inverter > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Inverter > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Inverter > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Inverter > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46030204 | Inverter > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Inverter > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Inverter > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Inverter > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Inverter > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46030100 | Inverter > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Inverter > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Inverter > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Inverter > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46040000 | Inverter > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Inverter > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Inverter > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Inverter > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46040100 | Inverter > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Inverter > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Inverter > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Inverter > Current protections > Over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46050000 | Inverter > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Inverter > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Inverter > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Inverter > Current protections > Fast over-current 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46050100 | Inverter > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Inverter > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Inverter > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Inverter > Current protections > Fast over-current 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46060000 | Inverter > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Inverter > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Inverter > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Inverter > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46060100 | Inverter > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Inverter > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Inverter > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Inverter > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46070000 | Inverter > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Inverter > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Inverter > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Inverter > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46070100 | Inverter > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Inverter > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Inverter > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Inverter > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
45300070 | Inverter > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Inverter > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Inverter > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Inverter > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Inverter > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Inverter > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Inverter > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Inverter > Current protections > Inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46080000 | Inverter > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Inverter > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Inverter > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Inverter > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46080100 | Inverter > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Inverter > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Inverter > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Inverter > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46090000 | Inverter > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Inverter > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Inverter > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Inverter > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46090004 | Inverter > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker closed
46090100 | Inverter > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Inverter > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Inverter > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Inverter > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46090104 | Inverter > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker closed
46100000 | Inverter > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Inverter > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Inverter > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Inverter > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46100004 | Inverter > Frequency protections > Under-frequency 1 | Inhibit |  | Inverter not running, Breaker closed
46100100 | Inverter > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Inverter > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Inverter > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Inverter > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46100104 | Inverter > Frequency protections > Under-frequency 2 | Inhibit |  | Inverter not running, Breaker closed
46110000 | Inverter > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Inverter > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Inverter > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Inverter > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46110100 | Inverter > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Inverter > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Inverter > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Inverter > Power protections > Overload 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46110200 | Inverter > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Inverter > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Inverter > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Inverter > Power protections > Overload 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46120000 | Inverter > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
46120001 | Inverter > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Inverter > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120003 | Inverter > Power protections > Reverse power 1 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46120004 | Inverter > Power protections > Reverse power 1 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
46120100 | Inverter > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
46120101 | Inverter > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Inverter > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46120103 | Inverter > Power protections > Reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46120104 | Inverter > Power protections > Reverse power 2 | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
46120200 | Inverter > Power protections > Overload reverse power 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46120201 | Inverter > Power protections > Overload reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120202 | Inverter > Power protections > Overload reverse power 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120203 | Inverter > Power protections > Overload reverse power 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46120300 | Inverter > Power protections > Overload reverse power 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46120301 | Inverter > Power protections > Overload reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120302 | Inverter > Power protections > Overload reverse power 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120303 | Inverter > Power protections > Overload reverse power 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46130000 | Inverter > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Inverter > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Inverter > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Inverter > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46130100 | Inverter > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Inverter > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Inverter > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Inverter > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46140000 | Inverter > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140001 | Inverter > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Inverter > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Inverter > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46140100 | Inverter > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
46140101 | Inverter > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Inverter > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Inverter > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40210010 | Inverter > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Inverter > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Inverter > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Inverter > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Inverter > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Inverter > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Inverter > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Inverter > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210020 | Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210010 | Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126210030 | Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210050 | Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210040 | Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126210060 | Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210080 | Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210070 | Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126210090 | Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210000 | Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126210100 | Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126210110 | Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
126220020 | Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220010 | Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126220030 | Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220050 | Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220040 | Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126220060 | Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220080 | Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220070 | Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126220090 | Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220000 | Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126220100 | Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126220110 | Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90100052 | Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100062 | Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100072 | Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90100032 | Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Breaker open, ACM wire break
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Breaker open, ACM wire break
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Breaker open, ACM wire break
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46170004 | Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Breaker open, ACM wire break
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Breaker open, ACM wire break
39000030 | Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39000000 | Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000010 | Power transformer > Nominal settings 1 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39000020 | Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39001030 | Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39001000 | Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001010 | Power transformer > Nominal settings 2 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39001020 | Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39002030 | Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39002000 | Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002010 | Power transformer > Nominal settings 3 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39002020 | Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
39003030 | Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
39003000 | Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003010 | Power transformer > Nominal settings 4 | Inverter side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
39003020 | Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
70000780 | Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Relay |  |  |  |  | 0: Off, 2: Relay
70000560 | Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
80000040 | Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000022 | Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000023 | Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
70000800 | Regulators > GOV > General configuration > External offset | Frequency offset enable | INT32 | 0 |  | 0 | 1 | 0
70000820 | Regulators > GOV > General configuration > External offset | P set point enable | INT32 | 0 |  | 0 | 1 | 0
70000790 | Regulators > GOV > General configuration > External offset | Frequency offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70000810 | Regulators > GOV > General configuration > External offset | P set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off
70001480 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
70001490 | Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
40030120 | Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40175120 | Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40180120 | Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40185120 | Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
70000100 | Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000110 | Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000120 | Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000130 | Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000140 | Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000150 | Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000160 | Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000180 | Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000190 | Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000200 | Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000040 | Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000050 | Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000060 | Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000070 | Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000080 | Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000090 | Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000490 | Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
70000000 | Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0
70000010 | Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0
70000950 | Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70001360 | Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0
70001370 | Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0
70001380 | Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2
70000230 | Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000240 | Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000270 | Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000280 | Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1
70000290 | Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000300 | Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
70000250 | Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000260 | Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1
70000210 | Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000220 | Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1
70000520 | Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
70000522 | Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
70000523 | Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
70000590 | Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
70000592 | Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
70000593 | Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
70000770 | Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Off |  |  |  |  | 0: Off | X
70001010 | Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
80000050 | Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
80000032 | Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
80000033 | Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
70000840 | Regulators > AVR > General configuration > External offset | Q set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000860 | Regulators > AVR > General configuration > External offset | Voltage offset enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000880 | Regulators > AVR > General configuration > External offset | Cos phi set point enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
70000830 | Regulators > AVR > General configuration > External offset | Q set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000850 | Regulators > AVR > General configuration > External offset | Voltage offset source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000870 | Regulators > AVR > General configuration > External offset | Cos phi set point source | INT32 | External |  |  |  |  | 1: External, 2: External -> Off | X
70000990 | Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001420 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4 |  | X
70001430 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001440 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4 |  | X
70001450 | Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive | X
70001460 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2 |  | X
70001470 | Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2 |  | X
70001040 | Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0 |  | X
40030130 | Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40175130 | Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40180130 | Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
40185130 | Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1 |  | X
70000350 | Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000360 | Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000370 | Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000320 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000330 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000340 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000170 | Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000380 | Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2 |  | X
70000390 | Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2 |  | X
70000400 | Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2 |  | X
70000480 | Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1 |  | X
70000020 | Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
70000030 | Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
70000960 | Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70001390 | Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
70001400 | Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
70001410 | Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
70000410 | Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000420 | Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000430 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000440 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
70000470 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000310 | Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
70000450 | Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
70000460 | Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
70000530 | Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1 |  | X
70000532 | Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0 |  | X
70000533 | Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
70000600 | Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1 |  | X
70000602 | Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0 |  | X
70000603 | Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
20100000 | Breakers > Inverter breaker configuration > Configuration | Type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Inverter breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Inverter breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Inverter breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Inverter breaker configuration > Configuration | Breaker open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
13000020 | Breakers > Inverter breaker configuration > Configuration | Allow breaker close when | INT32 | Inverter is started |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
13000030 | Breakers > Inverter breaker configuration > Configuration | Allow breaker open when | INT32 | Inverter in any state |  |  |  |  | 0: Inverter is started, 1: Inverter is stopped, 2: Inverter in any state
3300070 | Breakers > Inverter breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Inverter breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Inverter breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Inverter breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Inverter breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Inverter breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Inverter breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Inverter breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Inverter breaker monitoring > Synchronisation failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100092 | Breakers > Inverter breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Inverter breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
3300090 | Breakers > Inverter breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Inverter breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Inverter breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100052 | Breakers > Inverter breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Inverter breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100042 | Breakers > Inverter breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Inverter breaker monitoring > Closing failure | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100062 | Breakers > Inverter breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Inverter breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100072 | Breakers > Inverter breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Inverter breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
20100123 | Breakers > Inverter breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
20100133 | Breakers > Inverter breaker monitoring > Short circuit | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110700002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110700042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90100002 | Local power management > Alarms > Forced to MANUAL mode | Delay | FLOAT | 0.2 | s | 0.2 | 0.2 | 1
90100003 | Local power management > Alarms > Forced to MANUAL mode | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000300 | Local power management > Mode > Update | Selection | INT32 | Local update |  |  |  |  | 0: Local update, 1: Update all
90900022 | Local power management > Parallel timers > Hybrid-SG max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
90900023 | Local power management > Parallel timers > Hybrid-SG max. parallel time | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90900024 | Local power management > Parallel timers > Hybrid-SG max. parallel time | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
90900032 | Local power management > Parallel timers > Hybrid-SC max. parallel time | Delay | FLOAT | 60 | s | 0.1 | 3600 | 1
90900033 | Local power management > Parallel timers > Hybrid-SC max. parallel time | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
90900034 | Local power management > Parallel timers > Hybrid-SC max. parallel time | Inhibit |  | Operating mode PTI (power take in), Operating mode standby
90200000 | Local power management > Asymmetric load sharing > P configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
90200050 | Local power management > Asymmetric load sharing > P configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
90200010 | Local power management > Asymmetric load sharing > P configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
90200070 | Local power management > Asymmetric load sharing > Q configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
90200060 | Local power management > Asymmetric load sharing > Q configuration | Source | INT32 | Parameter |  |  |  |  | 0: Parameter, 1: External, 2: External -> Off, 3: External -> Parameter
90200080 | Local power management > Asymmetric load sharing > Q configuration | Set point | FLOAT | 80 | % | 1 | 100 | 0
90200100 | Local power management > Blackout > Blackout close | Allow blackout recovery | INT32 | 1 |  | 0 | 1 | 0
90100010 | Local power management > Return modes > After SWBD control | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
90100020 | Local power management > Return modes > After blackout | Mode | INT32 | No mode change |  |  |  |  | 2: No mode change, 0: Manual, 1: Auto
126000040 | Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
126000000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99 | % | 90 | 110 | 1
126002000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126002002 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002003 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
126000010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 101 | % | 90 | 110 | 1
126002010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126002012 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002013 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
126000020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99 | % | 90 | 110 | 1
126002020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126002022 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002023 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
126000030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 101 | % | 90 | 110 | 1
126002030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126002032 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126002033 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90200090 | Local power management > Delays > P delay after connect | Delay | FLOAT | 0 | s | 0 | 30 | 1
90900120 | Local power management > Hybrid modes > Standby > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
90900102 | Local power management > Hybrid modes > Standby > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900103 | Local power management > Hybrid modes > Standby > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90900112 | Local power management > Hybrid modes > Standby > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900113 | Local power management > Hybrid modes > Standby > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90900180 | Local power management > Hybrid modes > PTO (power take off) > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
90900162 | Local power management > Hybrid modes > PTO (power take off) > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900163 | Local power management > Hybrid modes > PTO (power take off) > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90900172 | Local power management > Hybrid modes > PTO (power take off) > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900173 | Local power management > Hybrid modes > PTO (power take off) > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90900150 | Local power management > Hybrid modes > PTI (power take in) > Configuration | Acknowledge pulse length | FLOAT | 1 | s | 0 | 3600 | 1
90900190 | Local power management > Hybrid modes > PTI (power take in) > Configuration | Nominal load | FLOAT | 0 | kW | 0 | 1000000 | 0
90900132 | Local power management > Hybrid modes > PTI (power take in) > Request failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900133 | Local power management > Hybrid modes > PTI (power take in) > Request failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
90900142 | Local power management > Hybrid modes > PTI (power take in) > Acknowledge timeout | Delay | FLOAT | 30 | s | 0 | 3600 | 0
90900143 | Local power management > Hybrid modes > PTI (power take in) > Acknowledge timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110000080 | System > Monitoring > PMS mode while controller missing | Mode | INT32 | No mode change |  |  |  |  | 0: No mode change, 1: Manual, 2: Auto
110002012 | System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
110002013 | System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled stop, 3: Trip breaker, 6: Trip breaker and stop inverter, 12: Stop inverter

## SHAFT generator
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40030110 | Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40175110 | Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40180110 | Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
40185110 | Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
11200030 | Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency, 3: Oil pressure, 1: Engine speed
11200040 | Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
11200010 | Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
11200000 | Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1
11200100 | Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0
11200070 | Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0
11200020 | Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1
11200090 | Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0
11200052 | Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
11200053 | Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000182 | Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
11000183 | Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000184 | Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
11000140 | Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1
11000141 | Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000142 | Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000143 | Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000150 | Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1
11000151 | Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1
11000152 | Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000153 | Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000160 | Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1
11000161 | Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000162 | Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11000163 | Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000164 | Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running
11000170 | Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1
11000171 | Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11000172 | Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1
11000173 | Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11000174 | Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running
11001000 | Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1
11001001 | Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001002 | Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001003 | Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001004 | Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running
11001010 | Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1
11001011 | Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1
11001012 | Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1
11001013 | Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001014 | Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running
11001020 | Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1
11001021 | Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001022 | Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001023 | Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001030 | Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1
11001031 | Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001032 | Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001033 | Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001040 | Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1
11001041 | Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001042 | Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001043 | Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001050 | Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1
11001051 | Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001052 | Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001053 | Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001060 | Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1
11001061 | Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1
11001062 | Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001063 | Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001070 | Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1
11001071 | Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001072 | Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001073 | Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001080 | Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1
11001081 | Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001082 | Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001083 | Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11001090 | Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1
11001091 | Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1
11001092 | Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1
11001093 | Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
40600500 | Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40610500 | Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40620500 | Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
40640000 | Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
11300020 | Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300023 | Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
11300050 | Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
11300053 | Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000070 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000240 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Use nominal RPM as reference | INT32 | 0 |  | 0 | 1 | 0
170000080 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000730 | Engine > ECU > Controls > Speed control (TSC1 / Custom) | Destination address | INT32 | 0 |  | 0 | 255 | 0
170000090 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Enable | INT32 | 1 |  | 0 | 1 | 0
170000100 | Engine > ECU > Controls > Generator control (GC1 / Custom) | Source address | INT32 | 234 |  | 0 | 255 | 0
170000120 | Engine > ECU > Controls > Cab message (CM1 / Custom) | Source address | INT32 | 3 |  | 0 | 255 | 0
170000270 | Engine > ECU > Controls > CAN controls | Enable | INT32 | 1 |  | 0 | 1 | 0
170000410 | Engine > ECU > Controls > Droop | Droop settings | INT32 | None |  |  |  |  | 0: None, 2: Emulated droop
170000420 | Engine > ECU > Controls > Droop | Droop value | FLOAT | 4 | % | 0 | 25 | 1
170000003 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000013 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000023 | Engine > ECU > Diagnostic alarms > ECU Protect lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000033 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000173 | Engine > ECU > Diagnostic alarms > ECU Red stop lamp (ECU2) | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000183 | Engine > ECU > Diagnostic alarms > ECU Amber warning lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000193 | Engine > ECU > Diagnostic alarms > ECU Protect lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000203 | Engine > ECU > Diagnostic alarms > ECU Malfunction indicator lamp (ECU2) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
170000320 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Inhibit Switch | INT32 | 0 |  | 0 | 1 | 0
170000330 | Engine > ECU > DPF controls > Controls | Aftertreatment Regeneration Force Switch | INT32 | Automatic |  |  |  |  | 0: Automatic, 1: Forced
11800000 | Engine > Engine heater > Engine heater | Source selector | INT32 | 0 |  | 0 | 2147483647 | 0
11800010 | Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
11800020 | Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
11800030 | Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
40310000 | Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Generator > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410010 | Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
40410040 | Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
40410120 | Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
40410130 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410140 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
40410150 | Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 97 | % | 70 | 100 | 2
40410160 | Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
40410102 | Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
40410103 | Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
40410070 | Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100082 | Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100092 | Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100102 | Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100042 | Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
40030000 | Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
46010010 | Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46010004 | Generator > Voltage protections > Over-voltage 1 | Inhibit |  | Shaft breaker closed
46010110 | Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46010104 | Generator > Voltage protections > Over-voltage 2 | Inhibit |  | Shaft breaker closed
46010210 | Generator > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Generator > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Generator > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Generator > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Generator > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46010204 | Generator > Voltage protections > Over-voltage 3 | Inhibit |  | Shaft breaker closed
46000010 | Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46000004 | Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Shaft breaker closed
46000110 | Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46000104 | Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Shaft breaker closed
46000210 | Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46000204 | Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Shaft breaker closed
46020010 | Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Generator > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46020004 | Generator > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46030204 | Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46030100 | Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46040000 | Generator > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46040100 | Generator > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Generator > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46050000 | Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46050100 | Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46060000 | Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46060100 | Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46070000 | Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46070100 | Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
45300070 | Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46080000 | Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46080100 | Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46090000 | Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46090004 | Generator > Frequency protections > Over-frequency 1 | Inhibit |  | Shaft breaker closed
46090100 | Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46090104 | Generator > Frequency protections > Over-frequency 2 | Inhibit |  | Shaft breaker closed
46100000 | Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46100004 | Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, Shaft breaker closed
46100100 | Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46100104 | Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, Shaft breaker closed
46110000 | Generator > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46110100 | Generator > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Generator > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Generator > Power protections > Overload 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46110200 | Generator > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Generator > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Generator > Power protections > Overload 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46120000 | Generator > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
46120001 | Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Generator > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120003 | Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46120004 | Generator > Power protections > Reverse power 1 | Inhibit |  | Power take home active
46120100 | Generator > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
46120101 | Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Generator > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46120103 | Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46120104 | Generator > Power protections > Reverse power 2 | Inhibit |  | Power take home active
46130000 | Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46130100 | Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46140000 | Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140001 | Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46140004 | Generator > Reactive power protections > Reactive power import 1 | Inhibit |  | Power take home active
46140100 | Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
46140101 | Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46140104 | Generator > Reactive power protections > Reactive power import 2 | Inhibit |  | Power take home active
40210010 | Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Generator > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Generator > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Generator > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Generator > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Shaft breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Shaft breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Shaft breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Shaft breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210020 | Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210010 | Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126210030 | Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210050 | Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210040 | Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126210060 | Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210080 | Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210070 | Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126210090 | Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210000 | Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126210100 | Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126210110 | Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
126220020 | Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220010 | Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126220030 | Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220050 | Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220040 | Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126220060 | Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220080 | Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220070 | Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126220090 | Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220000 | Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126220100 | Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126220110 | Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100052 | Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100062 | Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100072 | Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
90100032 | Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Shaft breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Shaft breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Shaft breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Shaft breaker open, ACM wire break
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Shaft breaker open, ACM wire break
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Shaft breaker open, ACM wire break
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46170004 | Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Shaft breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Shaft breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Shaft breaker open, ACM wire break
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Shaft breaker open, ACM wire break
20100000 | Breakers > Shaft breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Shaft breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Shaft breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Shaft breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Shaft breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
3300070 | Breakers > Shaft breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Shaft breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Shaft breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Shaft breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Shaft breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Shaft breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Shaft breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Shaft breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Shaft breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
3310070 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3310080 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3310000 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
3310010 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
3310020 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3310030 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3310040 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3310050 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3310060 | Breakers > Shaft breaker configuration > Synchronisation setting (PTH) | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Shaft breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Shaft breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100092 | Breakers > Shaft breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Shaft breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
3300090 | Breakers > Shaft breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Shaft breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Shaft breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100052 | Breakers > Shaft breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Shaft breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100042 | Breakers > Shaft breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Shaft breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100062 | Breakers > Shaft breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Shaft breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100072 | Breakers > Shaft breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Shaft breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
20100123 | Breakers > Shaft breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
20100133 | Breakers > Shaft breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110700002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110700042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100362 | Local power management > Parallel timers > SG-DG max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
90100363 | Local power management > Parallel timers > SG-DG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100392 | Local power management > Parallel timers > SG-Hybrid max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
90100393 | Local power management > Parallel timers > SG-Hybrid max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100372 | Local power management > Parallel timers > SG-SG max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
90100373 | Local power management > Parallel timers > SG-SG max. parallel time | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
90100350 | Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
90100310 | Local power management > Shaft generator base load > Enable | Base load | INT32 | Off |  |  |  |  | 0: Off, 1: Active, 2: Active with priority
90100320 | Local power management > Shaft generator base load > Power set point | Set point | FLOAT | 90 | % | 10 | 120 | 0
90100330 | Local power management > Shaft generator base load > Min. set point | Minimum limit | FLOAT | 5 | % | 1 | 100 | 0
90100340 | Local power management > Shaft generator base load > Max. set point | Maximum limit | FLOAT | 95 | % | 1 | 120 | 0
90300070 | Local power management > Shaft generator PTH mode > Open point | Open point enabled | INT32 | 0 |  | 0 | 1 | 0
90300080 | Local power management > Shaft generator PTH mode > Open point | Open when power below | FLOAT | 5 | % | 2 | 100 | 0
90300090 | Local power management > Shaft generator PTH mode > Connect load | PTH connect load | FLOAT | 100 | kW | 1 | 900000 | 0
90300100 | Local power management > Shaft generator f [Hz] variation > Frequency [Hz] variation | Enable | INT32 | 1 |  | 0 | 1 | 0
90300110 | Local power management > Shaft generator f [Hz] variation > Engine start | Low frequency limit | FLOAT | 91 | % | 90 | 100 | 1
90300120 | Local power management > Shaft generator f [Hz] variation > Engine start | High frequency limit | FLOAT | 109 | % | 100 | 110 | 1
90300150 | Local power management > Shaft generator f [Hz] variation > Engine start | Delay | FLOAT | 0.5 | s | 0 | 10 | 1
90300130 | Local power management > Shaft generator f [Hz] variation > Connect gensets | Low frequency limit | FLOAT | 90 | % | 90 | 100 | 1
90300140 | Local power management > Shaft generator f [Hz] variation > Connect gensets | High frequency limit | FLOAT | 110 | % | 100 | 110 | 1
90300160 | Local power management > Shaft generator f [Hz] variation > Connect gensets | Delay | FLOAT | 0.5 | s | 0 | 10 | 1
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
11500050 | Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11500022 | Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11500023 | Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
11500060 | Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11500000 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11500030 | Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11500010 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11500040 | Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600050 | Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11600022 | Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11600023 | Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
11600060 | Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11600000 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11600030 | Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11600010 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11600040 | Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700050 | Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
11700022 | Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
11700023 | Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
11700060 | Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
11700000 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
11700030 | Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
11700010 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
11700040 | Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
170000050 | Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON
170000060 | Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1
170000042 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1
170000043 | Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110002012 | System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
110002013 | System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip generator breaker

## SHORE connection
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
125000000 | Non-essential load trip > Trip 1 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125000002 | Non-essential load trip > Trip 1 > Over-current | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000003 | Non-essential load trip > Trip 1 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125000004 | Non-essential load trip > Trip 1 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
125000010 | Non-essential load trip > Trip 1 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125000012 | Non-essential load trip > Trip 1 > Under-frequency | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000013 | Non-essential load trip > Trip 1 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125000020 | Non-essential load trip > Trip 1 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125000022 | Non-essential load trip > Trip 1 > Overload 1 | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000023 | Non-essential load trip > Trip 1 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125000024 | Non-essential load trip > Trip 1 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125000030 | Non-essential load trip > Trip 1 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000032 | Non-essential load trip > Trip 1 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125000033 | Non-essential load trip > Trip 1 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125000034 | Non-essential load trip > Trip 1 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125000040 | Non-essential load trip > Trip 1 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125000042 | Non-essential load trip > Trip 1 > Reactive overload | Delay | FLOAT | 5 | s | 0.1 | 3600 | 1 |  | X
125000043 | Non-essential load trip > Trip 1 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125000044 | Non-essential load trip > Trip 1 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
125000050 | Non-essential load trip > Trip 1 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125020000 | Non-essential load trip > Trip 2 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125020002 | Non-essential load trip > Trip 2 > Over-current | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020003 | Non-essential load trip > Trip 2 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125020004 | Non-essential load trip > Trip 2 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
125020010 | Non-essential load trip > Trip 2 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125020012 | Non-essential load trip > Trip 2 > Under-frequency | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020013 | Non-essential load trip > Trip 2 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125020020 | Non-essential load trip > Trip 2 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125020022 | Non-essential load trip > Trip 2 > Overload 1 | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020023 | Non-essential load trip > Trip 2 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125020024 | Non-essential load trip > Trip 2 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125020030 | Non-essential load trip > Trip 2 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020032 | Non-essential load trip > Trip 2 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125020033 | Non-essential load trip > Trip 2 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125020034 | Non-essential load trip > Trip 2 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125020040 | Non-essential load trip > Trip 2 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125020042 | Non-essential load trip > Trip 2 > Reactive overload | Delay | FLOAT | 8 | s | 0.1 | 3600 | 1 |  | X
125020043 | Non-essential load trip > Trip 2 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125020044 | Non-essential load trip > Trip 2 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
125020050 | Non-essential load trip > Trip 2 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
125030000 | Non-essential load trip > Trip 3 > Over-current | Set point | FLOAT | 100 | % | 50 | 200 | 0 |  | X
125030002 | Non-essential load trip > Trip 3 > Over-current | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030003 | Non-essential load trip > Trip 3 > Over-current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125030004 | Non-essential load trip > Trip 3 > Over-current | Inhibit |  | Shore connection breaker open | [5 empty] | X
125030010 | Non-essential load trip > Trip 3 > Under-frequency | Set point | FLOAT | 95 | % | 70 | 100 | 1 |  | X
125030012 | Non-essential load trip > Trip 3 > Under-frequency | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030013 | Non-essential load trip > Trip 3 > Under-frequency | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125030020 | Non-essential load trip > Trip 3 > Overload 1 | Set point | FLOAT | 100 | % | 10 | 200 | 0 |  | X
125030022 | Non-essential load trip > Trip 3 > Overload 1 | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030023 | Non-essential load trip > Trip 3 > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125030024 | Non-essential load trip > Trip 3 > Overload 1 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125030030 | Non-essential load trip > Trip 3 > Overload 2 | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030032 | Non-essential load trip > Trip 3 > Overload 2 | Delay | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
125030033 | Non-essential load trip > Trip 3 > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125030034 | Non-essential load trip > Trip 3 > Overload 2 | Inhibit |  | Shore connection breaker open | [5 empty] | X
125030040 | Non-essential load trip > Trip 3 > Reactive overload | Set point | FLOAT | 110 | % | 10 | 200 | 0 |  | X
125030042 | Non-essential load trip > Trip 3 > Reactive overload | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1 |  | X
125030043 | Non-essential load trip > Trip 3 > Reactive overload | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
125030044 | Non-essential load trip > Trip 3 > Reactive overload | Inhibit |  | Shore connection breaker open | [5 empty] | X
125030050 | Non-essential load trip > Trip 3 > Settings | Trip when breaker trips | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210020 | Load reduction > Reduction output 1 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210010 | Load reduction > Reduction output 1 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126210030 | Load reduction > Reduction output 1 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210050 | Load reduction > Reduction output 1 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210040 | Load reduction > Reduction output 1 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126210060 | Load reduction > Reduction output 1 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210080 | Load reduction > Reduction output 1 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126210070 | Load reduction > Reduction output 1 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126210090 | Load reduction > Reduction output 1 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126210000 | Load reduction > Reduction output 1 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126210100 | Load reduction > Reduction output 1 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126210110 | Load reduction > Reduction output 1 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
126220020 | Load reduction > Reduction output 2 > Low power available [kW] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220010 | Load reduction > Reduction output 2 > Low power available [kW] | Limit | FLOAT | 100 | kW | -1500000 | 1500000 | 1 |  | X
126220030 | Load reduction > Reduction output 2 > Low power available [kW] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220050 | Load reduction > Reduction output 2 > Low power available [%] | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220040 | Load reduction > Reduction output 2 > Low power available [%] | Limit | FLOAT | 0 | % | -50 | 100 | 1 |  | X
126220060 | Load reduction > Reduction output 2 > Low power available [%] | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220080 | Load reduction > Reduction output 2 > Under-frequency | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
126220070 | Load reduction > Reduction output 2 > Under-frequency | Limit | FLOAT | 98 | % | 80 | 100 | 1 |  | X
126220090 | Load reduction > Reduction output 2 > Under-frequency | Delay | FLOAT | 0 | s | 0 | 3600 | 2 |  | X
126220000 | Load reduction > Reduction output 2 > Settings | Power available method | INT32 | AUTO or MANUAL |  |  |  |  | 0: Connected, 1: AUTO or MANUAL, 2: AUTO | X
126220100 | Load reduction > Reduction output 2 > Settings | Period time | FLOAT | 2 | s | 0.04 | 3600 | 2 |  | X
126220110 | Load reduction > Reduction output 2 > Settings | Pulse time | FLOAT | 1 | s | 0.04 | 3600 | 2 |  | X
40310000 | Shore connection > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Shore connection > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Shore connection > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Shore connection > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Shore connection > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Shore connection > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410000 | Shore connection > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40410010 | Shore connection > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Shore connection > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Shore connection > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40410040 | Shore connection > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40410070 | Shore connection > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Shore connection > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Shore connection > AC setup > Phase sequence error | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100082 | Shore connection > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Shore connection > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100092 | Shore connection > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Shore connection > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100102 | Shore connection > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Shore connection > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100042 | Shore connection > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Shore connection > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
40030000 | Shore connection > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Shore connection > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Shore connection > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Shore connection > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Shore connection > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Shore connection > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Shore connection > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Shore connection > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Shore connection > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Shore connection > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Shore connection > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Shore connection > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Shore connection > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Shore connection > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Shore connection > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Shore connection > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Shore connection > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Shore connection > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Shore connection > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Shore connection > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Shore connection > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Shore connection > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Shore connection > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Shore connection > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Shore connection > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Shore connection > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Shore connection > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Shore connection > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Shore connection > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Shore connection > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Shore connection > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Shore connection > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
46010010 | Shore connection > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Shore connection > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Shore connection > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Shore connection > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Shore connection > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46010004 | Shore connection > Voltage protections > Over-voltage 1 | Inhibit |  | Shore connection breaker closed
46010110 | Shore connection > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Shore connection > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Shore connection > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Shore connection > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Shore connection > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46010104 | Shore connection > Voltage protections > Over-voltage 2 | Inhibit |  | Shore connection breaker closed
46010210 | Shore connection > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Shore connection > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Shore connection > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Shore connection > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Shore connection > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46010204 | Shore connection > Voltage protections > Over-voltage 3 | Inhibit |  | Shore connection breaker closed
46000010 | Shore connection > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Shore connection > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Shore connection > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Shore connection > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Shore connection > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46000004 | Shore connection > Voltage protections > Under-voltage 1 | Inhibit |  | Shore connection breaker closed, No shore voltage
46000110 | Shore connection > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Shore connection > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Shore connection > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Shore connection > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Shore connection > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46000104 | Shore connection > Voltage protections > Under-voltage 2 | Inhibit |  | Shore connection breaker closed, No shore voltage
46000210 | Shore connection > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Shore connection > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Shore connection > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Shore connection > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Shore connection > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46000204 | Shore connection > Voltage protections > Under-voltage 3 | Inhibit |  | Shore connection breaker closed, No shore voltage
46020010 | Shore connection > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Shore connection > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Shore connection > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Shore connection > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Shore connection > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46020004 | Shore connection > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Shore connection > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Shore connection > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Shore connection > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Shore connection > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46030204 | Shore connection > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Shore connection > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Shore connection > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Shore connection > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Shore connection > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46030100 | Shore connection > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Shore connection > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Shore connection > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Shore connection > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46040000 | Shore connection > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Shore connection > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Shore connection > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Shore connection > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46040100 | Shore connection > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Shore connection > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Shore connection > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Shore connection > Current protections > Over-current 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46050000 | Shore connection > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Shore connection > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Shore connection > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Shore connection > Current protections > Fast over-current 1 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46050100 | Shore connection > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Shore connection > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Shore connection > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Shore connection > Current protections > Fast over-current 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46060000 | Shore connection > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Shore connection > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Shore connection > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Shore connection > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46060100 | Shore connection > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Shore connection > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Shore connection > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Shore connection > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46070000 | Shore connection > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Shore connection > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Shore connection > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Shore connection > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46070100 | Shore connection > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Shore connection > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Shore connection > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Shore connection > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
45300070 | Shore connection > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Shore connection > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Shore connection > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Shore connection > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Shore connection > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Shore connection > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Shore connection > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Shore connection > Current protections > Inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46090000 | Shore connection > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Shore connection > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Shore connection > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Shore connection > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46090004 | Shore connection > Frequency protections > Over-frequency 1 | Inhibit |  | Shore connection breaker closed
46090100 | Shore connection > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Shore connection > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Shore connection > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Shore connection > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46090104 | Shore connection > Frequency protections > Over-frequency 2 | Inhibit |  | Shore connection breaker closed
46100000 | Shore connection > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Shore connection > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Shore connection > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Shore connection > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46100004 | Shore connection > Frequency protections > Under-frequency 1 | Inhibit |  | Shore connection breaker closed, No shore voltage
46100100 | Shore connection > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Shore connection > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Shore connection > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Shore connection > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46100104 | Shore connection > Frequency protections > Under-frequency 2 | Inhibit |  | Shore connection breaker closed, No shore voltage
46110000 | Shore connection > Power protections > Overload 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Shore connection > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Shore connection > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Shore connection > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46110100 | Shore connection > Power protections > Overload 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Shore connection > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Shore connection > Power protections > Overload 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Shore connection > Power protections > Overload 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46110200 | Shore connection > Power protections > Overload 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Shore connection > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Shore connection > Power protections > Overload 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Shore connection > Power protections > Overload 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46120000 | Shore connection > Power protections > Reverse power 1 | Set point | FLOAT | 8 | % | 0 | 200 | 1
46120001 | Shore connection > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Shore connection > Power protections > Reverse power 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46120003 | Shore connection > Power protections > Reverse power 1 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46120004 | Shore connection > Power protections > Reverse power 1 | Inhibit |  | Ship-to-ship active
46120100 | Shore connection > Power protections > Reverse power 2 | Set point | FLOAT | 15 | % | 0 | 200 | 1
46120101 | Shore connection > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Shore connection > Power protections > Reverse power 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
46120103 | Shore connection > Power protections > Reverse power 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46120104 | Shore connection > Power protections > Reverse power 2 | Inhibit |  | Ship-to-ship active
46130000 | Shore connection > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Shore connection > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Shore connection > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Shore connection > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46130100 | Shore connection > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Shore connection > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Shore connection > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Shore connection > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46140000 | Shore connection > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 300 | 1
46140001 | Shore connection > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Shore connection > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Shore connection > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46140004 | Shore connection > Reactive power protections > Reactive power import 1 | Inhibit |  | Ship-to-ship active
46140100 | Shore connection > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 300 | 1
46140101 | Shore connection > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Shore connection > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Shore connection > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46140104 | Shore connection > Reactive power protections > Reactive power import 2 | Inhibit |  | Ship-to-ship active
40210010 | Shore connection > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Shore connection > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Shore connection > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Shore connection > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Shore connection > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Shore connection > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Shore connection > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Shore connection > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40300000 | Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar > AC setup > Phase sequence error | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100052 | Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100062 | Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100072 | Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
90100032 | Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
40010000 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
40160000 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
40165000 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
40170000 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use shore busbar nominal voltage |  |  |  |  | 0: User defined, 1: Use shore busbar nominal voltage
46150010 | Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150003 | Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46150004 | Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Shore connection breaker open
46150110 | Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46150103 | Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46150104 | Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Shore connection breaker open
46150210 | Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46150204 | Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Shore connection breaker open
46160010 | Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46160004 | Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Shore connection breaker open, ACM wire break
46160110 | Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46160104 | Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Shore connection breaker open, ACM wire break
46160210 | Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46160204 | Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Shore connection breaker open, ACM wire break
46170010 | Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46170004 | Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46200204 | Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46200100 | Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46180000 | Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46180004 | Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Shore connection breaker open
46180100 | Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46180104 | Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Shore connection breaker open
46190000 | Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46190004 | Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Shore connection breaker open, ACM wire break
46190100 | Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
46190104 | Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Shore connection breaker open, ACM wire break
20100000 | Breakers > Shore breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Shore breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Shore breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Shore breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Shore breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
25000160 | Breakers > Shore breaker configuration > Configuration | Overlap | INT32 | 0 |  | 0 | 1 | 0
90400120 | Breakers > Shore breaker configuration > Configuration | Breaker action | INT32 | Open shore connection breaker |  |  |  |  | 0: Open shore connection breaker, 1: Open without de-loading, 2: Operator select
3300070 | Breakers > Shore breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Shore breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Shore breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Shore breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Shore breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Shore breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Shore breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Shore breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Shore breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Shore breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Shore breaker monitoring > Synchronisation failure | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100092 | Breakers > Shore breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Shore breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
3300090 | Breakers > Shore breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Shore breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Shore breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100052 | Breakers > Shore breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Shore breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100042 | Breakers > Shore breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Shore breaker monitoring > Closing failure | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100062 | Breakers > Shore breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Shore breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100072 | Breakers > Shore breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Shore breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
20100123 | Breakers > Shore breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
20100133 | Breakers > Shore breaker monitoring > Short circuit | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110700002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110700042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100362 | Local power management > Parallel timers > SC-DG max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
90100363 | Local power management > Parallel timers > SC-DG max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100392 | Local power management > Parallel timers > SC-Hybrid max. parallel time | Delay | FLOAT | 180 | s | 0.1 | 3600 | 1
90100393 | Local power management > Parallel timers > SC-Hybrid max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100372 | Local power management > Parallel timers > SC-SG max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
90100373 | Local power management > Parallel timers > SC-SG max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100382 | Local power management > Parallel timers > SC-SC max. parallel time | Delay | FLOAT | 0.1 | s | 0.1 | 0.1 | 1 |  | X
90100383 | Local power management > Parallel timers > SC-SC max. parallel time | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
90100350 | Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
90100310 | Local power management > Shore connection base load > Enable | Base load | INT32 | 0 |  | 0 | 1 | 0
90100320 | Local power management > Shore connection base load > Power set point | Set point | FLOAT | 90 | % | 10 | 120 | 0
90100330 | Local power management > Shore connection base load > Min. set point | Minimum limit | FLOAT | 5 | % | 1 | 100 | 0
90100340 | Local power management > Shore connection base load > Max. set point | Maximum limit | FLOAT | 95 | % | 1 | 120 | 0
90400090 | Local power management > Shore connection ship-to-ship > Open point | Open point enabled | INT32 | 0 |  | 0 | 1 | 0
90400100 | Local power management > Shore connection ship-to-ship > Open point | Open when power below | FLOAT | 5 | % | 2 | 100 | 0
90400110 | Local power management > Shore connection ship-to-ship > Connect load | Ship-to-ship connect load | FLOAT | 100 | kW | 1 | 900000 | 0
90400080 | Local power management > Shore connection close load > Shore connection breaker | Minimum load on ship busbar | FLOAT | 5 | % | 0 | 100 | 1
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip shore connection breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110002012 | System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
110002013 | System > Monitoring > Blackout detection mismatch | Action | INT32 | Block |  |  |  |  | 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip shore connection breaker

## BUS TIE breaker
ID | Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
40310000 | Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40310010 | Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40310020 | Busbar A > AC setup > Current transformer | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40310030 | Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
40500000 | Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
40500010 | Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
40410110 | Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40410000 | Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40410010 | Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40410020 | Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40410030 | Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40410040 | Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40410070 | Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40410082 | Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40410083 | Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
90100082 | Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100083 | Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100092 | Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100093 | Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100102 | Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100103 | Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100042 | Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100043 | Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
40030000 | Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
40030020 | Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 866 | A | 1 | 9000 | 1
40030010 | Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40030090 | Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40030100 | Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40030030 | Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 480 | kW | 1 | 900000 | 1
40030070 | Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 600 | kVA | 1 | 1000000 | 1
40030080 | Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40175000 | Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40175020 | Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40175010 | Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
40175090 | Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40175100 | Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40175030 | Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40175070 | Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40175080 | Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40180000 | Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40180020 | Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40180010 | Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40180090 | Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40180100 | Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40180030 | Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40180070 | Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40180080 | Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
40185000 | Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 480 | V | 10 | 1500000 | 1
40185020 | Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 346 | A | 1 | 9000 | 1
40185010 | Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 60 | Hz | 20 | 100 | 2
40185090 | Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
40185100 | Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
40185030 | Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 230 | kW | 1 | 900000 | 1
40185070 | Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 287.5 | kVA | 1 | 1000000 | 1
40185080 | Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
46010010 | Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010000 | Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
46010001 | Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010002 | Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46010003 | Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46010110 | Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010100 | Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010101 | Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010102 | Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46010103 | Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46010210 | Busbar A > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46010200 | Busbar A > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 80 | 120 | 1
46010201 | Busbar A > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46010202 | Busbar A > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46010203 | Busbar A > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46000010 | Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000000 | Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46000001 | Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000002 | Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46000003 | Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46000110 | Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000100 | Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46000101 | Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000102 | Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46000103 | Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46000210 | Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
46000200 | Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46000201 | Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46000202 | Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46000203 | Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46020010 | Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
46020000 | Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46020001 | Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46020002 | Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46020003 | Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46020004 | Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46030200 | Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46030201 | Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030202 | Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46030203 | Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46030204 | Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46030000 | Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46030001 | Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030002 | Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030003 | Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46030100 | Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46030101 | Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46030102 | Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46030103 | Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46040000 | Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 100 | % | 50 | 1212.47 | 1
46040001 | Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040002 | Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
46040003 | Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46040100 | Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 110 | % | 50 | 1212.47 | 1
46040101 | Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46040102 | Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 60 | s | 0 | 7200 | 2
46040103 | Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46050000 | Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 1212.47 | 1
46050001 | Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050002 | Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050003 | Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46050100 | Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 1212.47 | 1
46050101 | Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46050102 | Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0 | s | 0 | 7200 | 2
46050103 | Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46060000 | Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060001 | Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060002 | Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060003 | Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46060100 | Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
46060101 | Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46060102 | Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46060103 | Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46070000 | Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -1212.47 | 1212.47 | 1
46070001 | Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070002 | Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070003 | Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46070100 | Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -1212.47 | 1212.47 | 1
46070101 | Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070102 | Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070103 | Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46070200 | Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -1212.47 | 1212.47 | 1
46070201 | Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070202 | Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070203 | Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46070300 | Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -1212.47 | 1212.47 | 1
46070301 | Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46070302 | Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
46070303 | Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
45300070 | Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300080 | Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
45300090 | Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300130 | Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300140 | Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300150 | Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300430 | Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001033 | Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46080000 | Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
46080001 | Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080002 | Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080003 | Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46080100 | Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
46080101 | Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46080102 | Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46080103 | Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46090000 | Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 120 | 1
46090001 | Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090002 | Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46090003 | Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46090100 | Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 107 | % | 100 | 120 | 1
46090101 | Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46090102 | Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46090103 | Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46100000 | Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 95 | % | 80 | 100 | 1
46100001 | Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100002 | Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46100003 | Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46100100 | Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46100101 | Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46100102 | Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46100103 | Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46110000 | Busbar A > Power protections > Power export 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46110001 | Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110002 | Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110003 | Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46110100 | Busbar A > Power protections > Power export 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110101 | Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110102 | Busbar A > Power protections > Power export 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110103 | Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46110200 | Busbar A > Power protections > Power export 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46110201 | Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46110202 | Busbar A > Power protections > Power export 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46110203 | Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46120000 | Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
46120001 | Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120002 | Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120003 | Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46120100 | Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46120101 | Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120102 | Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120103 | Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46120200 | Busbar A > Power protections > Power import 3 | Set point | FLOAT | 110 | % | 0 | 200 | 1
46120201 | Busbar A > Power protections > Power import 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46120202 | Busbar A > Power protections > Power import 3 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
46120203 | Busbar A > Power protections > Power import 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46130000 | Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
46130001 | Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130002 | Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46130003 | Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46130100 | Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
46130101 | Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46130102 | Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46130103 | Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46140000 | Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
46140001 | Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140002 | Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46140003 | Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46140100 | Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
46140101 | Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46140102 | Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46140103 | Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
40210010 | Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210020 | Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210110 | Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210120 | Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210210 | Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210220 | Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210310 | Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210320 | Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210410 | Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
40210420 | Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40210510 | Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
40210520 | Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
40300000 | Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
40300010 | Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
40400090 | Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
40400000 | Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
40400010 | Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
40400020 | Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
40400030 | Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
40400040 | Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
40400070 | Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
40400082 | Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
40400083 | Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
90100052 | Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100053 | Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100062 | Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100063 | Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100072 | Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100073 | Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
90100032 | Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
90100033 | Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
40010000 | Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40010110 | Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40160000 | Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40160110 | Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40165000 | Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40165110 | Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
40170000 | Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
40170110 | Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
46150010 | Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150000 | Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
46150001 | Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150002 | Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46150003 | Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46150110 | Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150100 | Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150101 | Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150102 | Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46150103 | Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46150210 | Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46150200 | Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
46150201 | Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46150202 | Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
46150203 | Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46160010 | Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160000 | Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
46160001 | Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160002 | Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46160003 | Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46160004 | Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
46160110 | Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160100 | Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
46160101 | Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160102 | Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
46160103 | Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46160104 | Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
46160210 | Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
46160200 | Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 70 | % | 10 | 100 | 1
46160201 | Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46160202 | Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
46160203 | Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46160204 | Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
46170010 | Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
46170000 | Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
46170001 | Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46170002 | Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
46170003 | Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46170004 | Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
46200200 | Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
46200201 | Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200202 | Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
46200203 | Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46200204 | Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
46200000 | Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
46200001 | Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200002 | Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200003 | Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46200100 | Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
46200101 | Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46200102 | Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
46200103 | Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46180000 | Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
46180001 | Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180002 | Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46180003 | Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46180100 | Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
46180101 | Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46180102 | Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
46180103 | Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46190000 | Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
46190001 | Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190002 | Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
46190003 | Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46190004 | Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
46190100 | Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
46190101 | Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
46190102 | Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
46190103 | Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
46190104 | Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
20100000 | Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
20100010 | Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
20100020 | Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
20100030 | Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
20100110 | Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
3300070 | Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
3300080 | Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
3300000 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
3300010 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
3300020 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
3300030 | Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
3300040 | Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
3300050 | Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
3300060 | Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
20100082 | Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
20100083 | Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100092 | Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
20100093 | Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
3300090 | Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
3300092 | Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
3300093 | Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100052 | Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100053 | Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100042 | Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
20100043 | Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100062 | Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
20100063 | Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100072 | Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
20100073 | Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
20100123 | Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
20100133 | Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110700002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110700042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110700043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110710002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110710042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110710043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110720002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110720042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110720043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110730002 | Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730003 | Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110730042 | Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
110730043 | Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
90100220 | Local power management > Alarms > Configuration | Alarm reaction | INT32 | Section to SWBD control |  |  |  |  | 0: Section to SWBD control, 1: Controller to SWBD control
90000033 | Local power management > Alarms > Forced to switchboard control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
90100350 | Local power management > Blackout > Blackout close | Enable blackout close | INT32 | 0 |  | 0 | 1 | 0
90500000 | Local power management > Bus tie breaker > Supply mode after BTB close | Supply mode after connecting | INT32 | Stay on DG supply |  |  |  |  | 0: Stay on DG supply, 2: Stay on SG/SC supply
126001040 | Local power management > Advanced blackout prevention > Delay after load share changes | Delay | FLOAT | 12 | s | 0 | 3600 | 1
126001000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Low frequency limit | FLOAT | 99.5 | % | 90 | 110 | 1
126003000 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126003002 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
126003003 | Local power management > Advanced blackout prevention > P load sharing failure (low frequency) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126001010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | High frequency limit | FLOAT | 100.5 | % | 90 | 110 | 1
126003010 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126003012 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
126003013 | Local power management > Advanced blackout prevention > P load sharing failure (high frequency) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126001020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Low voltage limit | FLOAT | 99.5 | % | 90 | 110 | 1
126003020 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Set point | FLOAT | -20 | % | -100 | -0.1 | 1
126003022 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
126003023 | Local power management > Advanced blackout prevention > Q load sharing failure (low voltage) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126001030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | High voltage limit | FLOAT | 100.5 | % | 90 | 110 | 1
126003030 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Set point | FLOAT | 20 | % | 0.1 | 100 | 1
126003032 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Delay | FLOAT | 2 | s | 0 | 3600 | 1
126003033 | Local power management > Advanced blackout prevention > Q load sharing failure (high voltage) | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126003040 | Local power management > Advanced blackout prevention > Overload on a DG | Set point | FLOAT | 120 | % | 70 | 250 | 1
126003042 | Local power management > Advanced blackout prevention > Overload on a DG | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126003043 | Local power management > Advanced blackout prevention > Overload on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126003050 | Local power management > Advanced blackout prevention > Reverse power on a DG | Set point | FLOAT | -5 | % | -25 | -0.1 | 1
126003052 | Local power management > Advanced blackout prevention > Reverse power on a DG | Delay | FLOAT | 3 | s | 0 | 3600 | 1
126003053 | Local power management > Advanced blackout prevention > Reverse power on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126003060 | Local power management > Advanced blackout prevention > Reactive power export on a DG | Set point | FLOAT | 120 | % | 0.1 | 250 | 1
126003062 | Local power management > Advanced blackout prevention > Reactive power export on a DG | Delay | FLOAT | 10 | s | 0 | 3600 | 1
126003063 | Local power management > Advanced blackout prevention > Reactive power export on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126003070 | Local power management > Advanced blackout prevention > Reactive power import on a DG | Set point | FLOAT | -100 | % | -120 | -0.1 | 1
126003072 | Local power management > Advanced blackout prevention > Reactive power import on a DG | Delay | FLOAT | 10 | s | 0 | 3600 | 1
126003073 | Local power management > Advanced blackout prevention > Reactive power import on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
126003080 | Local power management > Advanced blackout prevention > Over-current on a DG | Set point | FLOAT | 200 | % | 70 | 250 | 1
126003082 | Local power management > Advanced blackout prevention > Over-current on a DG | Delay | FLOAT | 0.3 | s | 0 | 3600 | 1
126003083 | Local power management > Advanced blackout prevention > Over-current on a DG | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
150100340 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100350 | Power management rules > Configuration 1 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150100320 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150100330 | Power management rules > Configuration 1 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150100250 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100260 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100270 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100280 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100440 | Power management rules > Configuration 1 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100390 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150100400 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100410 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150100420 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150100450 | Power management rules > Configuration 1 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150100230 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150100220 | Power management rules > Configuration 1 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150100100 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150100110 | Power management rules > Configuration 1 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150100240 | Power management rules > Configuration 1 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150100040 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100000 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100010 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100020 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100030 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100090 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150100050 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100060 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100070 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100080 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100160 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100120 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150100130 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150100140 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150100150 | Power management rules > Configuration 1 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100210 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150100170 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150100180 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150100190 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150100200 | Power management rules > Configuration 1 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150100460 | Power management rules > Configuration 1 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150100370 | Power management rules > Configuration 1 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150100360 | Power management rules > Configuration 1 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150100290 | Power management rules > Configuration 1 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150100300 | Power management rules > Configuration 1 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150100310 | Power management rules > Configuration 1 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150100380 | Power management rules > Configuration 1 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150100430 | Power management rules > Configuration 1 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150200340 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200350 | Power management rules > Configuration 2 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150200320 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150200330 | Power management rules > Configuration 2 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150200250 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200260 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200270 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200280 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200440 | Power management rules > Configuration 2 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200390 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150200400 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200410 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150200420 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150200450 | Power management rules > Configuration 2 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150200230 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150200220 | Power management rules > Configuration 2 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150200100 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150200110 | Power management rules > Configuration 2 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150200240 | Power management rules > Configuration 2 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150200040 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200000 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200010 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200020 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200030 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200090 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150200050 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200060 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200070 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200080 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200160 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200120 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150200130 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150200140 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150200150 | Power management rules > Configuration 2 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200210 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150200170 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150200180 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150200190 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150200200 | Power management rules > Configuration 2 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150200460 | Power management rules > Configuration 2 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150200370 | Power management rules > Configuration 2 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150200360 | Power management rules > Configuration 2 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150200290 | Power management rules > Configuration 2 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150200300 | Power management rules > Configuration 2 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150200310 | Power management rules > Configuration 2 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150200380 | Power management rules > Configuration 2 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150200430 | Power management rules > Configuration 2 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150300340 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300350 | Power management rules > Configuration 3 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150300320 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150300330 | Power management rules > Configuration 3 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150300250 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300260 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300270 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300280 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300440 | Power management rules > Configuration 3 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300390 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150300400 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300410 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150300420 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150300450 | Power management rules > Configuration 3 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150300230 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150300220 | Power management rules > Configuration 3 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150300100 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150300110 | Power management rules > Configuration 3 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150300240 | Power management rules > Configuration 3 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150300040 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300000 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300010 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300020 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300030 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300090 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150300050 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300060 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300070 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300080 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300160 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300120 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150300130 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150300140 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150300150 | Power management rules > Configuration 3 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300210 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150300170 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150300180 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150300190 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150300200 | Power management rules > Configuration 3 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150300460 | Power management rules > Configuration 3 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150300370 | Power management rules > Configuration 3 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150300360 | Power management rules > Configuration 3 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150300290 | Power management rules > Configuration 3 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150300300 | Power management rules > Configuration 3 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150300310 | Power management rules > Configuration 3 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150300380 | Power management rules > Configuration 3 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150300430 | Power management rules > Configuration 3 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150400340 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400350 | Power management rules > Configuration 4 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150400320 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150400330 | Power management rules > Configuration 4 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150400250 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400260 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400270 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400280 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400440 | Power management rules > Configuration 4 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400390 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150400400 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400410 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150400420 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150400450 | Power management rules > Configuration 4 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150400230 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150400220 | Power management rules > Configuration 4 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150400100 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150400110 | Power management rules > Configuration 4 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150400240 | Power management rules > Configuration 4 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150400040 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400000 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400010 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400020 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400030 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400090 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150400050 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400060 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400070 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400080 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400160 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400120 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150400130 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150400140 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150400150 | Power management rules > Configuration 4 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400210 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150400170 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150400180 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150400190 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150400200 | Power management rules > Configuration 4 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150400460 | Power management rules > Configuration 4 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150400370 | Power management rules > Configuration 4 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150400360 | Power management rules > Configuration 4 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150400290 | Power management rules > Configuration 4 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150400300 | Power management rules > Configuration 4 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150400310 | Power management rules > Configuration 4 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150400380 | Power management rules > Configuration 4 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150400430 | Power management rules > Configuration 4 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150500340 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500350 | Power management rules > Configuration 5 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150500320 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150500330 | Power management rules > Configuration 5 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150500250 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500260 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500270 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500280 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500440 | Power management rules > Configuration 5 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500390 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150500400 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500410 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150500420 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150500450 | Power management rules > Configuration 5 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150500230 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150500220 | Power management rules > Configuration 5 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150500100 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150500110 | Power management rules > Configuration 5 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150500240 | Power management rules > Configuration 5 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150500040 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500000 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500010 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500020 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500030 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500090 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150500050 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500060 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500070 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500080 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500160 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500120 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150500130 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150500140 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150500150 | Power management rules > Configuration 5 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500210 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150500170 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150500180 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150500190 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150500200 | Power management rules > Configuration 5 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150500460 | Power management rules > Configuration 5 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150500370 | Power management rules > Configuration 5 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150500360 | Power management rules > Configuration 5 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150500290 | Power management rules > Configuration 5 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150500300 | Power management rules > Configuration 5 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150500310 | Power management rules > Configuration 5 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150500380 | Power management rules > Configuration 5 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150500430 | Power management rules > Configuration 5 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150600340 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600350 | Power management rules > Configuration 6 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150600320 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150600330 | Power management rules > Configuration 6 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150600250 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600260 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600270 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600280 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600440 | Power management rules > Configuration 6 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600390 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150600400 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600410 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150600420 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150600450 | Power management rules > Configuration 6 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150600230 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150600220 | Power management rules > Configuration 6 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150600100 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150600110 | Power management rules > Configuration 6 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150600240 | Power management rules > Configuration 6 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150600040 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600000 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600010 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600020 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600030 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600090 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150600050 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600060 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600070 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600080 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600160 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600120 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150600130 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150600140 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150600150 | Power management rules > Configuration 6 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600210 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150600170 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150600180 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150600190 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150600200 | Power management rules > Configuration 6 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150600460 | Power management rules > Configuration 6 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150600370 | Power management rules > Configuration 6 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150600360 | Power management rules > Configuration 6 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150600290 | Power management rules > Configuration 6 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150600300 | Power management rules > Configuration 6 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150600310 | Power management rules > Configuration 6 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150600380 | Power management rules > Configuration 6 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150600430 | Power management rules > Configuration 6 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150700340 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700350 | Power management rules > Configuration 7 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150700320 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150700330 | Power management rules > Configuration 7 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150700250 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700260 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700270 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700280 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700440 | Power management rules > Configuration 7 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700390 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150700400 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700410 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150700420 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150700450 | Power management rules > Configuration 7 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150700230 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150700220 | Power management rules > Configuration 7 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150700100 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150700110 | Power management rules > Configuration 7 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150700240 | Power management rules > Configuration 7 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150700040 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700000 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700010 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700020 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700030 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700090 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150700050 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700060 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700070 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700080 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700160 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700120 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150700130 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150700140 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150700150 | Power management rules > Configuration 7 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700210 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150700170 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150700180 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150700190 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150700200 | Power management rules > Configuration 7 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150700460 | Power management rules > Configuration 7 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150700370 | Power management rules > Configuration 7 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150700360 | Power management rules > Configuration 7 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150700290 | Power management rules > Configuration 7 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150700300 | Power management rules > Configuration 7 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150700310 | Power management rules > Configuration 7 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150700380 | Power management rules > Configuration 7 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150700430 | Power management rules > Configuration 7 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
150800340 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800350 | Power management rules > Configuration 8 > Number of gensets connected > Maximum | Set point | INT32 | 5 |  | 1 | 64 | 0
150800320 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Enable | INT32 | 0 |  | 0 | 1 | 0
150800330 | Power management rules > Configuration 8 > Number of gensets connected > Minimum | Set point | INT32 | 1 |  | 1 | 64 | 0
150800250 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800260 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800270 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800280 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800440 | Power management rules > Configuration 8 > Asymmetric load sharing > P configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800390 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum | FLOAT | 5 | % | 1 | 100 | 0
150800400 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Minimum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800410 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum | FLOAT | 95 | % | 1 | 100 | 0
150800420 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Maximum delay | FLOAT | 0.5 | s | 0 | 3600 | 1
150800450 | Power management rules > Configuration 8 > Asymmetric load sharing > Q configuration | Limit exceeded | INT32 | Switch to equal |  |  |  |  | 0: Switch to equal, 1: Adjust set point
150800230 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Enable | INT32 | 0 |  | 0 | 1 | 0
150800220 | Power management rules > Configuration 8 > Asymmetric load sharing > Start when an asymmetric set point is exceeded | Delay | FLOAT | 30 | s | 1 | 3600 | 0
150800100 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Power selection | INT32 | Calculation in P |  |  |  |  | 0: Calculation in P, 1: Calculation in S
150800110 | Power management rules > Configuration 8 > Load-dependent start/stop > Configuration | Method | INT32 | Power |  |  |  |  | 0: Power, 1: Percent
150800240 | Power management rules > Configuration 8 > Load-dependent start/stop > Heavy consumer | Block stop when active | INT32 | 0 |  | 0 | 1 | 0
150800040 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800000 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800010 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800020 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800030 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800090 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Enable | INT32 | 1 |  | 0 | 1 | 0
150800050 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800060 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800070 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800080 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 1 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800160 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800120 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | P available limit | FLOAT | 100 | kW | 1 | 9000000 | 0
150800130 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | S available limit | FLOAT | 100 | kVA | 1 | 9000000 | 0
150800140 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Load limit | FLOAT | 90 | % | 1 | 100 | 0
150800150 | Power management rules > Configuration 8 > Load-dependent start/stop > Start 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800210 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Enable | INT32 | 0 |  | 0 | 1 | 0
150800170 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | P available limit | FLOAT | 200 | kW | 1 | 9000000 | 0
150800180 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | S available limit | FLOAT | 200 | kVA | 1 | 9000000 | 0
150800190 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Load limit | FLOAT | 70 | % | 1 | 100 | 0
150800200 | Power management rules > Configuration 8 > Load-dependent start/stop > Stop 2 | Delay | FLOAT | 30 | s | 5 | 3600 | 0
150800460 | Power management rules > Configuration 8 > Load-dependent start/stop > Protective start | Protective start | INT32 | kW and kVA |  |  |  |  | 0: kW and kVA, 1: kW, 2: kVA
150800370 | Power management rules > Configuration 8 > Blackout > Blackout recovery | Number of gensets to start | INT32 | 1 |  | 1 | 64 | 0
150800360 | Power management rules > Configuration 8 > Blackout > Short circuit close attempts | Set point | INT32 | 0 |  | 0 | 1 | 0
150800290 | Power management rules > Configuration 8 > Power reservation > Secured mode | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
150800300 | Power management rules > Configuration 8 > Power reservation > Reserved power | Enable | INT32 | 0 |  | 0 | 1 | 0
150800310 | Power management rules > Configuration 8 > Power reservation > Reserved power | Set point | FLOAT | 480 |  | 1 | 9000000 | 0
150800380 | Power management rules > Configuration 8 > Shore connection > Parallel | Multiple shore connections | INT32 | Max. one SC may connect |  |  |  |  | 0: Max. one SC may connect, 1: One close command connects corresponding SC, 2: One close command connects all SCs | X
150800430 | Power management rules > Configuration 8 > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
110600010 | System power management > Priority > Selection | Method | INT32 | Manual |  |  |  |  | 0: Manual, 1: Delayed priority shift, 2: Dynamic, 3: Running hours
110600030 | System power management > Priority > Running hours | Method | INT32 | Total counter |  |  |  |  | 0: Total counter, 1: Trip counter
110600040 | System power management > Priority > Running hours | Swap timer | FLOAT | 175 | h | 1 | 20000 | 0
110002040 | System power management > Bus tie breaker > Closed ring | Ring close allowed | INT32 | 0 |  | 0 | 1 | 0
120000020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120000030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120000040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120000060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120000002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120000003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120000012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120000013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120000050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120000070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120100020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120100030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120100040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120100060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120100002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120100003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120100012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120100013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120100050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120100070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120200020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120200030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120200040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120200060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120200002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120200003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120200012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120200013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120200050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120200070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120300020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120300030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120300040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120300060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120300002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120300003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120300012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120300013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120300050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120300070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120400020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120400030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120400040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120400060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120400002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120400003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120400012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120400013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120400050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120400070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
120500020 | Heavy consumers > [User defined] > Nominal settings | Initial load | FLOAT | 125 | % | 100 | 500 | 0 |  | X
120500030 | Heavy consumers > [User defined] > Nominal settings | Nominal load | FLOAT | 100 | kVA | 0 | 1000000 | 0 |  | X
120500040 | Heavy consumers > [User defined] > Nominal settings | Power factor | FLOAT | 0.9 |  | 0.1 | 1 | 1 |  | X
120500060 | Heavy consumers > [User defined] > Request signal | Type | INT32 | Pulse |  |  |  |  | 0: Pulse, 1: Continuous | X
120500002 | Heavy consumers > [User defined] > Reservation not possible | Delay | FLOAT | 120 | s | 1 | 3600 | 0 |  | X
120500003 | Heavy consumers > [User defined] > Reservation not possible | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120500012 | Heavy consumers > [User defined] > Feedback timeout | Delay | FLOAT | 30 | s | 1 | 3600 | 0 |  | X
120500013 | Heavy consumers > [User defined] > Feedback timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
120500050 | Heavy consumers > [User defined] > Acknowledge | Pulse width | FLOAT | 1 | s | 1 | 10 | 1 |  | X
120500070 | Heavy consumers > [User defined] > Acknowledge | Delay | FLOAT | 0 | s | 0 | 30 | 1 |  | X
148000002 | Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
148000003 | Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110002003 | Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002363 | Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002343 | Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002072 | Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002073 | Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002092 | Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002093 | Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002122 | Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
110002123 | Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002082 | Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002083 | Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002102 | Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002103 | Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002112 | Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
110002113 | Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002133 | Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
110002143 | Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
181000003 | Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
181000013 | Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
60010010 | Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
60010020 | Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
60010030 | Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
60010000 | Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
60010110 | Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010120 | Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010130 | Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010100 | Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010210 | Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
60010220 | Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
60010230 | Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
60010200 | Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
40070000 | Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 867 | A | 1 | 9000 | 1
40190000 | Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40192500 | Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40195000 | Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 345 | A | 1 | 9000 | 1
40330000 | Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 1000 | A | 5 | 9000 | 0
40330010 | Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
45300170 | Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300180 | Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
45300190 | Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300230 | Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300240 | Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300250 | Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300440 | Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001043 | Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
45300270 | Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
45300280 | Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
45300290 | Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
45300330 | Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
45300340 | Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
45300350 | Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
45300450 | Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
45001053 | Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
60060000 | Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
60060013 | Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
60050003 | Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
40800000 | Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800010 | Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800020 | Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800030 | Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800040 | Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800050 | Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800060 | Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
40800070 | Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
60010320 | Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
60010330 | Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
60000100 | Local > Command sources > Active sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
60000120 | Local > Command sources > Active sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
60000130 | Local > Command sources > Active sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
60000140 | Local > Command sources > Active sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
60000150 | Local > Command sources > Active sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
60000160 | Local > Command sources > Active sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
40000000 | Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
40000100 | Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules
110000010 | System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
110000013 | System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000023 | System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000033 | System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000090 | System > Monitoring > Missing controllers | Set point | FLOAT | 2 |  | 1 | 5 | 0
110000093 | System > Monitoring > Missing controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000070 | System > Monitoring > Mode while controller missing | Mode | INT32 | Switchboard control |  |  |  |  | 0: Switchboard control, 1: No mode change
110000003 | System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000110 | System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
110000112 | System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000113 | System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000120 | System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
110000122 | System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000123 | System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
110000130 | System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
110000132 | System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
110000133 | System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
147000010 | System > Plant > Plant | Active application | INT32 | 1 |  | 1 | 4 | 0 | 1 | X
803000 | System > Application selector | Application selector | INT32 | MP |  |  |  |  | 800002: MP | X
140200000 | Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
140200010 | Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
140200020 | Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
130000000 | Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
100096020 | Hardware > PCM2.1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
100096010 | Hardware > PCM2.1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
100096012 | Hardware > PCM2.1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096013 | Hardware > PCM2.1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
100096000 | Hardware > PCM2.1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
100096002 | Hardware > PCM2.1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
100096003 | Hardware > PCM2.1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
100100002 | Hardware > MIO2.1 > Relay 9 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100003 | Hardware > MIO2.1 > Relay 9 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100102 | Hardware > MIO2.1 > Relay 10 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100103 | Hardware > MIO2.1 > Relay 10 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100202 | Hardware > MIO2.1 > Relay 11 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100203 | Hardware > MIO2.1 > Relay 11 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100302 | Hardware > MIO2.1 > Relay 12 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100303 | Hardware > MIO2.1 > Relay 12 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100402 | Hardware > MIO2.1 > Relay 13 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100403 | Hardware > MIO2.1 > Relay 13 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100502 | Hardware > MIO2.1 > Relay 14 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100503 | Hardware > MIO2.1 > Relay 14 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100602 | Hardware > MIO2.1 > Relay 15 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100603 | Hardware > MIO2.1 > Relay 15 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
100100702 | Hardware > MIO2.1 > Relay 16 supervision | Delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
100100703 | Hardware > MIO2.1 > Relay 16 supervision | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker | X
160000030 | CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
160000010 | CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
160000022 | CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
160000023 | CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker
160000003 | CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block, 2: PMS-controlled open breaker, 3: Trip bus tie breaker