## About
iE 350 Core Parameter lists
Software version
The information contained in these parameter lists (Revision B) are applicable to software version 2.0.18.x of the iE 350 Core.
Controller types
This document includes the parameter and I/O function lists for these controller types:
SINGLE genset controller (with GB and MB)
GENSET controller
MAINS controller (with MB and TB)
BUS TIE breaker controller
See the iE 350 Core Designer's handbook for more information.
Parameters
The parameter lists are based on the parameters shown in the display or in PICUS, under Configure > Parameters.
If you cannot find a parameter in the display or PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Parameter path = The location of the parameter.
Parameter name = The name of the parameter.
Data type = The data type for the parameter value.*
Default = The default value or selection for the parameter.
Unit = The unit of measurement for the parameter value.*
Minimum = The minimum value of the parameter range.*
Maximum = The maximum value of the parameter range.*
Decimals = The number of decimal places for the value.*
Selections = The drop-down choices for the parameter.*
Hidden = To see this parameter, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
Inhibits are only included in the parameter list when they are selected in the default controller configuration.
Some advanced parameters (for example, Auto acknowledge and Latch) are not included in the parameter list.
[User defined] is used where part of the parameter path is configurable.
Custom parameters and Custom alarm are not included in the parameter list.
In addition to the parameters, the controllers also have a variety of other configurable settings. Examples include Fieldbus and Communication settings. These are not included in the parameter lists.
Input/output functions
The input/output function lists are based on the functions that can be selected in PICUS, under Configure > Input/ouput.
If you cannot find an input/output function in PICUS, it is probably Hidden. To see Hidden parameters you need to configure the application, configure an I/O function, and/or change a specific parameter selection. By only showing relevant parameters, the Hidden function ensures that the configuration is consistent.
Column names
Path = The location of the input/output function.
Name = The name of the input/output function.
IO type = The type of the input/output function.
DI = Digital input function DO = Digital output function AI = Analogue input function AO = Analogue output function
Unit = The default unit of measurement for the input/output function.*
Data type = The data type for the input/output function.
Minimum = The default minimum value of the input/output function.*
Maximum = The default maximum value of the input/output function.*
Decimals = The number of decimal places for the value.*
Hidden = To see this input/output function, you need to configure the application, an I/O function, and/or change a related parameter selection.*
Notes
* Only included where relevant.
[User defined] is used where part of the path is configurable.

## SINGLE genset parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1 |  | X
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0 |  | X
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on | X
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated | X
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0 |  | X
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Stop sequence > Externally stopped | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active | [5 empty] | X
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Generator type | Generator type | INT32 | Synchronous |  |  |  |  | 0: Synchronous, 1: Asynchronous
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Voltage protections > Asynchronous over-voltage | Set point | FLOAT | 30 | % | 1 | 80 | 0 |  | X
Generator > Voltage protections > Asynchronous over-voltage | Delay | FLOAT | 2 | s | 0 | 60 | 1 |  | X
Generator > Voltage protections > Asynchronous over-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Generator > Voltage protections > Asynchronous over-voltage | Inhibit |  | Generator breaker closed | [5 empty] | X
Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase mains, 2: Phase-neutral mains, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase mains, 49: Phase-neutral mains, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Mains > AC setup > Mains power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Mains > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Mains > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel
Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Additional protections > Vector shift | AC setup | INT32 | Mains |  |  |  |  | 34: Mains, 35: Generator
Mains > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Mains > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Mains > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
Mains > Additional protections > ROCOF | AC setup | INT32 | Mains |  |  |  |  | 32: Mains, 33: Generator
Mains > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Mains > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Mains > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Mains > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Mains > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Mains > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator mode | Selection | INT32 | Automatic |  |  |  |  | 0: Manual, 1: Automatic
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Off, 1: Analogue / ECU
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -0.5 | % | -10 | -0.1 | 2
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 0.5 | % | 0.1 | 10 | 2
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Frequency | Hysteresis low limit | FLOAT | -0.25 | Hz | -100 | -0.05 | 2 |  | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Frequency | Hysteresis high limit | FLOAT | 0.25 | Hz | 0.05 | 100 | 2 |  | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Offset calculated from | INT32 | Active power snapshot |  |  |  |  | 0: Active power snapshot, 1: Nominal power
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Ramp selection | INT32 | Ramp 2 |  |  |  |  | 0: Ramp 1, 1: Ramp 2
Regulators > GOV > Regulation set points > Fixed power | Set point of nominal | FLOAT | 30 | % | 0 | 100 | 0
Regulators > GOV > Regulation set points > Fixed power | Set point | FLOAT | 100 | kW | 0 | 100000 | 0 |  | X
Regulators > GOV > Regulation set points > Fixed power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked
Regulators > GOV > Regulation set points > Fixed power | Set point unit | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
Regulators > GOV > Regulation set points > Fixed power offset | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > RPM regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > RPM regulation | Deadband | FLOAT | 0.5 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > RPM synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Regulators > GOV > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Regulators > AVR > General configuration > Regulator mode | Selection | INT32 | Automatic |  |  |  |  | 0: Manual, 1: Automatic
Regulators > AVR > General configuration > Regulator mode | Mains parallel | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 1: Fixed reactive power
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Off, 1: Analogue / Digital AVR
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -1 | % | -10 | -0.1 | 2
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 1 | % | 0.1 | 10 | 2
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -4 | V | -1500000 | -1 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 4 | V | 1 | 1500000 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -1 | % | -10 | -0.1 | 2
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 1 | % | 0.1 | 10 | 2
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -4 | V | -1500000 | -1 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 4 | V | 1 | 1500000 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Offset calculated from | INT32 | Reactive power snapshot |  |  |  |  | 0: Reactive power snapshot, 1: Nominal reactive power
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Fixed cos phi | Set point | FLOAT | 0.9 |  | 0.6 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Capacitive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power | Set point | FLOAT | 0 | % | 0 | 100 | 0
Regulators > AVR > Regulation set points > Fixed reactive power | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Reactive power ramp up | Ramping method | INT32 | Fixed cos phi |  |  |  |  | 0: Reactive power curve, 1: Fixed cos phi
Regulators > AVR > Regulation set points > Reactive power ramp down | Ramping method | INT32 | Fixed cos phi |  |  |  |  | 0: Reactive power curve, 1: Fixed cos phi
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0
Regulators > AVR > Regulation set points > Power-dependent cos phi droop | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Power-dependent reactive power droop | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Regulators > AVR > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > AVR > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Blackout close | Blackout close | INT32 | Generator OK, busbar is dead |  |  |  |  | 0: Blackout close is OFF, 2: Generator OK, busbar is dead
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > De-load last breaker | Load share | INT32 | 0 |  | 0 | 1 | 0
Breakers > Generator breaker configuration > De-load last breaker | Fixed frequency | INT32 | 0 |  | 0 | 1 | 0
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Generator breaker monitoring > No synchronisation signal | Delay | FLOAT | 10 | s | 0.1 | 300 | 1 |  | X
Breakers > Generator breaker monitoring > No synchronisation signal | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Breakers > Generator breaker monitoring > No synchronisation signal | Inhibit |  | Engine not running, Generator breaker closed | [5 empty] | X
Breakers > Mains breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | LF |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 4: Trip mains breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine, 14: Block mains breaker, 15: Trip generator and main breakers

## SINGLE genset IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Engine > Command | Block engine start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
11280003 | Engine > Function | Remove start (release crank relay) | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Function | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180002 | Engine > Idle run | End idle start | DI |  | BOOL_NUM | 0 | 1 | 0
11180003 | Engine > Idle run | End idle stop | DI |  | BOOL_NUM | 0 | 1 | 0
11080100 | Engine > Safety shutdown | Manual reset | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
70100053 | Regulators > GOV > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100055 | Regulators > GOV > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100065 | Regulators > GOV > Modes | Override GOV automatic regulator mode | DI |  | BOOL_NUM | 0 | 1 | 0
70100200 | Regulators > GOV > Modes | Activate fixed frequency | DI |  | BOOL_NUM | 0 | 1 | 0
70100201 | Regulators > GOV > Modes | Activate fixed power | DI |  | BOOL_NUM | 0 | 1 | 0
70100202 | Regulators > GOV > Modes | Activate frequency droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100203 | Regulators > GOV > Modes | Activate power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100207 | Regulators > GOV > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100208 | Regulators > GOV > Modes | Activate fixed RPM | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100206 | Regulators > GOV > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100216 | Regulators > GOV > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100057 | Regulators > GOV > Active power offset | Active power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100058 | Regulators > GOV > Active power offset | Active power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100059 | Regulators > GOV > Active power offset | Active power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100054 | Regulators > AVR > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100056 | Regulators > AVR > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100066 | Regulators > AVR > Modes | Override AVR automatic regulator mode | DI |  | BOOL_NUM | 0 | 1 | 0
70100500 | Regulators > AVR > Modes | Activate fixed voltage | DI |  | BOOL_NUM | 0 | 1 | 0
70100501 | Regulators > AVR > Modes | Activate fixed reactive power | DI |  | BOOL_NUM | 0 | 1 | 0
70100502 | Regulators > AVR > Modes | Activate fixed cos phi | DI |  | BOOL_NUM | 0 | 1 | 0
70100503 | Regulators > AVR > Modes | Activate voltage droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100504 | Regulators > AVR > Modes | Activate reactive power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100508 | Regulators > AVR > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100507 | Regulators > AVR > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100517 | Regulators > AVR > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100060 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100061 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100062 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Generator breaker > Command | GB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Generator breaker > Command | GB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Generator breaker > Command | GB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
3316001 | Breakers > Mains breaker > Command | MB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3316002 | Breakers > Mains breaker > Command | MB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20280028 | Breakers > Mains breaker > Command | MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280029 | Breakers > Mains breaker > Command | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280030 | Breakers > Mains breaker > Command | Open MB without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20280031 | Breakers > Mains breaker > Command | Block MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280000 | Breakers > Mains breaker > Feedback | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280001 | Breakers > Mains breaker > Feedback | MB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20280004 | Breakers > Mains breaker > Feedback | MB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20280012 | Breakers > Mains breaker > Feedback | MB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
11480000 | Engine > Controls | Priming | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080021 | Engine > State | Not ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Engine > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Engine > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080024 | Engine > State | Cooldown | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Engine > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11080028 | Engine > State | Extended stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080101 | Engine > Safety shutdown | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Mains > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Mains > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90820001 | Mains > Supervision | Mains error | DO |  | BOOL_NUM | 0 | 1 | 0
90820002 | Mains > Supervision | Mains recovery fast | DO |  | BOOL_NUM | 0 | 1 | 0
90820003 | Mains > Supervision | Mains recovery slow | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100220 | Regulators > GOV > State | Fixed frequency regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100221 | Regulators > GOV > State | Fixed power regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100222 | Regulators > GOV > State | Frequency droop regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100223 | Regulators > GOV > State | Power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100224 | Regulators > GOV > State | Manual GOV regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100227 | Regulators > GOV > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100228 | Regulators > GOV > State | Fixed RPM is active | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100520 | Regulators > AVR > State | Fixed voltage is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100521 | Regulators > AVR > State | Fixed reactive power is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100522 | Regulators > AVR > State | Fixed cos phi is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100523 | Regulators > AVR > State | Reactive power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100524 | Regulators > AVR > State | Voltage droop is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100525 | Regulators > AVR > State | Manual AVR regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100528 | Regulators > AVR > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Generator breaker > Controls | GB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
20280002 | Breakers > Mains breaker > Controls | MB open | DO |  | BOOL_NUM | 0 | 1 | 0
20280003 | Breakers > Mains breaker > Controls | MB close | DO |  | BOOL_NUM | 0 | 1 | 0
20280027 | Breakers > Mains breaker > Controls | MB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20280014 | Breakers > Mains breaker > State | MB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20280015 | Breakers > Mains breaker > State | MB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20280024 | Breakers > Mains breaker > State | MB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20280025 | Breakers > Mains breaker > State | MB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20280026 | Breakers > Mains breaker > State | MB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035019 | Alarm system > State | Any MB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035021 | Alarm system > State | Any MB block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035022 | Alarm system > State | Any GB and MB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any GB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any GB + AVR + stop engine alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
40140000 | Mains > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1
40140001 | Mains > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1
40140002 | Mains > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | 0 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | 0 | 100 | 0
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 4
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380013 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380014 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380015 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380016 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380017 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380018 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380019 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380020 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380021 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Mains > Voltage (V) | Mains ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Mains > Voltage (V) | Mains ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Mains > Voltage (V) | Mains ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Mains > Voltage (V) | Mains ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Mains > Voltage (V) | Mains ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Mains > Voltage (V) | Mains ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Mains > Voltage (V) | Mains ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Mains > Voltage (V) | Mains ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Mains > Voltage (V) | Mains ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Mains > Voltage (V) | Mains ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Mains > Voltage (V) | Mains ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Mains > Voltage (V) | Mains ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Mains > Voltage (V) | Mains ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Mains > Voltage (V) | Mains ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Mains > Voltage (V) | Mains ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Mains > Voltage (V) | Mains ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Mains > Frequency (f) (from voltage) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Mains > Frequency (f) (from voltage) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Mains > Frequency (f) (from voltage) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Mains > Frequency (f) (from voltage) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Mains > Frequency (f) (from voltage) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Mains > Frequency (f) (from voltage) | Mains ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100024 | Mains > Power (P) | Mains ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100025 | Mains > Power (P) | Mains ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100026 | Mains > Power (P) | Mains ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100027 | Mains > Reactive power (Q) | Mains ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100028 | Mains > Reactive power (Q) | Mains ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100029 | Mains > Reactive power (Q) | Mains ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100030 | Mains > Apparent power (S) | Mains ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100031 | Mains > Apparent power (S) | Mains ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100032 | Mains > Apparent power (S) | Mains ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100018 | Mains > Phase angle | Mains ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Mains > Phase angle | Mains ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Mains > Phase angle | Mains ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## GENSET parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Engine > Nominal settings > Nominal settings 1 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 2 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 3 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Nominal settings > Nominal settings 4 > Nominal RPM | Nominal | FLOAT | 1500 | RPM | 100 | 50000 | 0
Engine > Emergency stop > Emergency stop | Delay | FLOAT | 0 | s | 0 | 60 | 1
Engine > Emergency stop > Emergency stop | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Feedback type | Primary running feedback | INT32 | Frequency |  |  |  |  | 2: Frequency
Engine > Running detection > Engine ready | Delay | FLOAT | 2 | s | 1 | 300 | 1
Engine > Running detection > Frequency running detection | Frequency | FLOAT | 32 | Hz | 10 | 100 | 1
Engine > Running detection > RPM running detection | RPM | FLOAT | 1000 | RPM | 0 | 50000 | 1 |  | X
Engine > Running detection > RPM running detection | Use engine speed | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > MPU setup | Number of MPU teeth | FLOAT | 1 |  | 1 | 10000 | 0 |  | X
Engine > Running detection > Oil pressure running detection | Oil pressure | FLOAT | 3 | bar | 0 | 10 | 1 |  | X
Engine > Running detection > Oil pressure running detection | Use oil pressure | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Running detection > Primary running feedback failure | Delay | FLOAT | 2 | s | 0 | 180 | 1
Engine > Running detection > Primary running feedback failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Magnetic pickup wire break | Delay | FLOAT | 10 | s | 1 | 3600 | 0
Engine > Running detection > Magnetic pickup wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Running detection > Magnetic pickup wire break | Inhibit |  | Engine not running
Engine > Start sequence > Start prepare | Start prepare | FLOAT | 5 | s | 0 | 600 | 1 |  | X
Engine > Start sequence > Start prepare | Extended start prepare | FLOAT | 0 | s | 0 | 20 | 1 |  | X
Engine > Start sequence > Run coil | Run coil before crank | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Engine > Start sequence > Run coil | During start attempts | INT32 | Follow crank |  |  |  |  | 0: Follow crank, 1: Always on | X
Engine > Start sequence > Crank | Crank on | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Crank off | FLOAT | 5 | s | 1 | 180 | 1
Engine > Start sequence > Crank | Disengage crank | FLOAT | 400 | RPM | 1 | 2000 | 0
Engine > Start sequence > Stop coil | During crank off | INT32 | Activated |  |  |  |  | 0: Activated, 1: Not activated | X
Engine > Start sequence > Start attempts | Normal | INT32 | 3 |  | 1 | 10 | 0
Engine > Start sequence > Start attempts | Suppress alarm action | INT32 | 5 |  | 1 | 10 | 0
Engine > Start sequence > Start failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Start sequence > Crank failure | Set point | FLOAT | 50 | RPM | 1 | 400 | 1 |  | X
Engine > Start sequence > Crank failure | Delay | FLOAT | 20 | s | 0 | 180 | 1 |  | X
Engine > Start sequence > Crank failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Start sequence > Externally started | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Start sequence > Start enable removed during start | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Idle run start > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Idle run | Extended inhibit | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Engine > Idle run start > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run start > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Coolant temperature | Set point | FLOAT | 50 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Oil temperature | Set point | FLOAT | 40 | °C | -50 | 200 | 0 |  | X
Engine > Idle run start > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run start > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Stop sequence > Cooldown | Cooldown time | FLOAT | 240 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Suppress alarm action | FLOAT | 480 | s | 1 | 10800 | 0
Engine > Stop sequence > Cooldown | Temperature threshold | FLOAT | 0 | °C | 0 | 150 | 0 |  | X
Engine > Stop sequence > Extended stop | Extended stop | FLOAT | 5 | s | 1 | 180 | 1
Engine > Stop sequence > Stop failure | Delay | FLOAT | 30 | s | 0 | 300 | 0
Engine > Stop sequence > Stop failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Stop sequence > Externally stopped | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Idle run stop > Idle run | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Minimum | Delay | FLOAT | 5 | s | 0 | 7200 | 1 |  | X
Engine > Idle run stop > Coolant temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Coolant temperature | Set point | FLOAT | 90 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > Oil temperature | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Oil temperature | Set point | FLOAT | 60 | °C | -50 | 200 | 0 |  | X
Engine > Idle run stop > External condition | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Use | INT32 | 1 |  | 0 | 1 | 0 |  | X
Engine > Idle run stop > Maximum | Delay | FLOAT | 60 | s | 1 | 7200 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Set point | FLOAT | 110 | % | 10 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Overspeed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Speed > Overspeed 2 | Set point | FLOAT | 120 | % | 10 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 150 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Overspeed 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Speed > Under-speed 1 | Set point | FLOAT | 90 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Under-speed 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Speed > Under-speed 1 | Inhibit |  | Engine not running, Idle run active | [5 empty] | X
Engine > Protections > Speed > Under-speed 2 | Set point | FLOAT | 80 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Delay | FLOAT | 1 | s | 0 | 180 | 1 |  | X
Engine > Protections > Speed > Under-speed 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Speed > Under-speed 2 | Inhibit |  | Engine not running, Idle run active | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 1 | Set point | FLOAT | 2 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Pressure > Oil pressure 1 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Pressure > Oil pressure 2 | Set point | FLOAT | 1 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Reset hysteresis | FLOAT | 0 | bar | 0 | 10 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Delay | FLOAT | 0.8 | s | 0 | 180 | 1 |  | X
Engine > Protections > Pressure > Oil pressure 2 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Pressure > Oil pressure 2 | Inhibit |  | Engine not running | [5 empty] | X
Engine > Protections > Temperature > Oil temperature 1 | Set point | FLOAT | 120 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Oil temperature 2 | Set point | FLOAT | 140 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Oil temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 1 | Set point | FLOAT | 100 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 2 | Set point | FLOAT | 110 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Temperature > Coolant temperature 3 | Set point | FLOAT | 115 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Reset hysteresis | FLOAT | 0 | °C | 0 | 200 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Temperature > Coolant temperature 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 1 | Set point | FLOAT | 20 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 2 | Set point | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Protections > Level > Coolant level 3 | Set point | FLOAT | 5 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 100 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Delay | FLOAT | 5 | s | 0 | 180 | 1 |  | X
Engine > Protections > Level > Coolant level 3 | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Engine > Power derate > Temperature > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 2 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Temperature > Derate 3 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Power derate > Percentage > Derate 1 > Enable | Enable derate | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | Enable | INT32 | 0 |  | 0 | 1 | 0 |  | X
Engine > Maintenance > Priming | ON timer | FLOAT | 5 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Priming | OFF timer | FLOAT | 30 | s | 0 | 3600 | 1 |  | X
Engine > Maintenance > Running hours total | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > Running hours total | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > Maintenance > [User defined] | Set point | FLOAT | 500 | h | 0 | 1000000 | 0
Engine > Maintenance > [User defined] | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Engine > ECU > Controls > Reset | Power off timer | FLOAT | 5 | s | 1 | 300 | 0 |  | X
Engine > Safety shutdown > Safety shutdown | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Keep stop coil active | INT32 | 0 |  | 0 | 1 | 0
Engine > Safety shutdown > Safety shutdown | Use magnetic pickup | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Enable | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Use timer | INT32 | 0 |  | 0 | 1 | 0
Engine > ECU diagnostic > ECU diagnostic | Time to enable function | FLOAT | 30 | s | 1 | 600 | 0
Engine > ECU diagnostic > ECU diagnostic | Mode | INT32 | Disable at start |  |  |  |  | 0: Disable at start, 1: Always on
Engine > Engine heater > Engine heater | Source selector | INT32 | Custom analogue input |  |  |  |  | 0: Custom analogue input, 1: Oil temperature, 2: Coolant temperature
Engine > Engine heater > Engine heater | Set point | FLOAT | 30 |  | 0 | 100 | 1
Engine > Engine heater > Engine heater | Hysteresis | FLOAT | 5 |  | 0 | 50 | 1
Engine > Engine heater > Engine heater | Enable | INT32 | 0 |  | 0 | 1 | 0
Generator > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Generator > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Generator > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Generator > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Generator > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Generator > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Generator > AC setup > Generator type | Generator type | INT32 | Synchronous |  |  |  |  | 0: Synchronous, 1: Asynchronous
Generator > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Generator > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 99 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 101 | % | 100 | 110 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Voltage and frequency OK | FLOAT | 2 | s | 0 | 3600 | 1
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK voltage | FLOAT | 105 | % | 100 | 110 | 0
Generator > AC setup > Voltage and frequency OK (blackout) | Minimum OK frequency | FLOAT | 94 | % | 70 | 100 | 2
Generator > AC setup > Voltage and frequency OK (blackout) | Maximum OK frequency | FLOAT | 106 | % | 100 | 110 | 2
Generator > AC setup > Voltage or frequency not OK | Delay | FLOAT | 30 | s | 1 | 3600 | 0
Generator > AC setup > Voltage or frequency not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Generator > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Generator > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Generator > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Generator > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Generator > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Generator > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Generator > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Generator > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Generator > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Generator > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Generator > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Generator > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Generator > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Generator > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Generator > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 1 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 2 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 2 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Generator > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Generator > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Generator > Voltage protections > Under-voltage 3 | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Under-voltage 3 | Inhibit |  | Engine not running, Idle run active
Generator > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Generator > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Generator > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Voltage unbalance | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Voltage unbalance | Inhibit |  | No generator voltage, ACM wire break
Generator > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Generator > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Generator > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
Generator > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Generator > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Generator > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Voltage protections > Asynchronous over-voltage | Set point | FLOAT | 30 | % | 1 | 80 | 0 |  | X
Generator > Voltage protections > Asynchronous over-voltage | Delay | FLOAT | 2 | s | 0 | 60 | 1 |  | X
Generator > Voltage protections > Asynchronous over-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Generator > Voltage protections > Asynchronous over-voltage | Inhibit |  | Generator breaker closed | [5 empty] | X
Generator > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Generator > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Current protections > Over-current 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Generator > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Generator > Current protections > Fast over-current 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Generator > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Generator > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Generator > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Generator > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Generator > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Generator > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Generator > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Generator > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Generator > Current protections > Inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Generator > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Generator > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Generator > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Generator > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 1 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 2 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Generator > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker and stop engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Frequency protections > Under-frequency 3 | Inhibit |  | Engine not running, No generator voltage, Idle run active
Generator > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Generator > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Generator > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Generator > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Overload 5 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Generator > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Power protections > Reverse power 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Generator > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Generator > Reactive power protections > Reactive power import 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 1 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase generator, 10: Phase-neutral generator
Generator > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Generator > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Generator > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Generator > Additional protections > V< and Q< 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase generator |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase generator, 51: Phase-neutral generator
Generator > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Generator > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Generator > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Generator > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Generator > Additional protections > Average over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Generator > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Generator > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Generator > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Generator > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Busbar > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use generator nominal voltage |  |  |  |  | 0: User defined, 1: Use generator nominal voltage
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 1 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 2 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Over-voltage 3 | Inhibit |  | Generator breaker open
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Under-voltage 4 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Voltage unbalance | Inhibit |  | ACM wire break
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Mains not in parallel, ACM wire break
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 1 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 2 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Over-frequency 3 | Inhibit |  | Generator breaker open
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 1 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 2 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 3 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Frequency protections > Under-frequency 4 | Inhibit |  | Generator breaker open, ACM wire break
Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Generator
Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar > Additional protections > Vector shift | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Additional protections > Vector shift | Inhibit |  | Mains not in parallel
Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Generator
Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar > Additional protections > ROCOF | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Busbar > Additional protections > ROCOF | Inhibit |  | Mains not in parallel
Power transformer > Nominal settings 1 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 1 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 1 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 2 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 2 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 2 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 3 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 3 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 3 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Power transformer > Nominal settings 4 | Winding nominal voltage source | INT32 | Use nominal voltages |  |  |  |  | 0: Use nominal voltages, 1: User defined
Power transformer > Nominal settings 4 | Busbar side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Generator side winding nominal voltage | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Power transformer > Nominal settings 4 | Phase shift | FLOAT | 0 | ° | -180 | 180 | 1
Regulators > GOV > General configuration > Regulator mode | Selection | INT32 | Automatic |  |  |  |  | 0: Manual, 1: Automatic
Regulators > GOV > General configuration > Regulator output | Output type | INT32 | Analogue / ECU |  |  |  |  | 0: Off, 1: Analogue / ECU
Regulators > GOV > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > GOV > General configuration > Stand-alone configuration | GOV stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > GOV > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > GOV > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -0.5 | % | -10 | -0.1 | 2
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 0.5 | % | 0.1 | 10 | 2
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Frequency | Hysteresis low limit | FLOAT | -0.25 | Hz | -100 | -0.05 | 2 |  | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Hysteresis > Frequency | Hysteresis high limit | FLOAT | 0.25 | Hz | 0.05 | 100 | 2 |  | X
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Offset calculated from | INT32 | Active power snapshot |  |  |  |  | 0: Active power snapshot, 1: Nominal power
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > GOV > Regulation set points > Frequency-dependent power droop > Configuration | Ramp selection | INT32 | Ramp 2 |  |  |  |  | 0: Ramp 1, 1: Ramp 2
Regulators > GOV > Regulation set points > Fixed power | Set point of nominal | FLOAT | 30 | % | 0 | 100 | 0
Regulators > GOV > Regulation set points > Fixed power | Set point | FLOAT | 100 | kW | 0 | 100000 | 0 |  | X
Regulators > GOV > Regulation set points > Fixed power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked
Regulators > GOV > Regulation set points > Fixed power | Set point unit | INT32 | In percent |  |  |  |  | 0: In percent, 1: In kW
Regulators > GOV > Regulation set points > Fixed power offset | Offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power offset | Offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Regulation set points > Fixed power limit | Limit 1 | FLOAT | 2 | % | -300 | 300 | 2
Regulators > GOV > Regulation set points > Fixed power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > GOV > Analogue > Offset | GOV output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Offset | GOV output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > GOV > Analogue > Frequency regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > GOV > Analogue > Power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > RPM synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Phase synchronisation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > GOV > Analogue > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > GOV > Analogue > Manual slope | Manual GOV slope | FLOAT | 10 | %/s | 0 | 200 | 1
Regulators > GOV > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > GOV > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency regulation | Deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | f deadband | FLOAT | 1 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Power load sharing regulation | P weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Power regulation | Deadband | FLOAT | 2 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > RPM regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > RPM regulation | Deadband | FLOAT | 0.5 | % | 0.2 | 10 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > RPM synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Phase synchronisation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > GOV > Relay configuration > Frequency droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > GOV > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > GOV > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > GOV > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > GOV > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > GOV > Monitoring > P load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > GOV > Monitoring > P load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > GOV > Monitoring > P load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > AVR > General configuration > Regulator mode | Selection | INT32 | Automatic |  |  |  |  | 0: Manual, 1: Automatic
Regulators > AVR > General configuration > Regulator mode | Mains parallel | INT32 | Fixed cos phi |  |  |  |  | 0: Fixed cos phi, 1: Fixed reactive power
Regulators > AVR > General configuration > Regulator output | Output type | INT32 | Analogue / Digital AVR |  |  |  |  | 0: Off, 1: Analogue / Digital AVR
Regulators > AVR > General configuration > Regulation delay | Regulator delay | FLOAT | 2 | s | 0 | 3600 | 1
Regulators > AVR > General configuration > Stand-alone configuration | AVR stand-alone activation | INT32 | High |  |  |  |  | 0: Low, 1: High | X
Regulators > AVR > General configuration > Stand-alone configuration error | Delay | FLOAT | 60 | s | 0 | 3600 | 0 |  | X
Regulators > AVR > General configuration > Stand-alone configuration error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -1 | % | -10 | -0.1 | 2
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 1 | % | 0.1 | 10 | 2
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -4 | V | -1500000 | -1 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 4 | V | 1 | 1500000 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent cos phi droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis low limit | FLOAT | -1 | % | -10 | -0.1 | 2
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Percentage | Hysteresis high limit | FLOAT | 1 | % | 0.1 | 10 | 2
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis low limit | FLOAT | -4 | V | -1500000 | -1 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Hysteresis > Voltage | Hysteresis high limit | FLOAT | 4 | V | 1 | 1500000 | 1 |  | X
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Offset calculated from | INT32 | Reactive power snapshot |  |  |  |  | 0: Reactive power snapshot, 1: Nominal reactive power
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Calculation method | INT32 | Percentage |  |  |  |  | 0: Percentage, 1: Absolute
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Hysteresis low enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Voltage-dependent reactive power droop > Configuration | Hysteresis high enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Fixed cos phi | Set point | FLOAT | 0.9 |  | 0.6 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 | FLOAT | 0 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 | FLOAT | 0.97 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 1 direction | INT32 | Capacitive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 | FLOAT | 0.8 |  | 0 | 1 | 4
Regulators > AVR > Regulation set points > Fixed cos phi limit | Limit 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power | Set point | FLOAT | 0 | % | 0 | 100 | 0
Regulators > AVR > Regulation set points > Fixed reactive power | Set point direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power | Set point adjustment | INT32 | Preferred |  |  |  |  | 0: Preferred, 1: Locked
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 1 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 2 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 | FLOAT | 0 | % | 0 | 100 | 1
Regulators > AVR > Regulation set points > Fixed reactive power offset | Offset 3 direction | INT32 | Inductive |  |  |  |  | 0: Inductive, 1: Capacitive
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 1 | FLOAT | -10 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Fixed reactive power limit | Limit 2 | FLOAT | 100 | % | -300 | 300 | 2
Regulators > AVR > Regulation set points > Reactive power ramp up | Ramping method | INT32 | Fixed cos phi |  |  |  |  | 0: Reactive power curve, 1: Fixed cos phi
Regulators > AVR > Regulation set points > Reactive power ramp down | Ramping method | INT32 | Fixed cos phi |  |  |  |  | 0: Reactive power curve, 1: Fixed cos phi
Regulators > AVR > Regulation set points > Reactive power ramp down | Cos phi reset point | FLOAT | 5 | % | 0 | 100 | 0
Regulators > AVR > Regulation set points > Power-dependent cos phi droop | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Regulation set points > Power-dependent reactive power droop | Droop enable | INT32 | 0 |  | 0 | 1 | 0
Regulators > AVR > Analogue > Offset | AVR output offset 1 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 2 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 3 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Offset | AVR output offset 4 | FLOAT | 0 | % | -100 | 100 | 1
Regulators > AVR > Analogue > Voltage regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1
Regulators > AVR > Analogue > Reactive power regulation | Kp | FLOAT | 2.5 |  | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power regulation | Ti | FLOAT | 1.5 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Reactive power regulation | Td | FLOAT | 0 | s | 0 | 1000 | 2
Regulators > AVR > Analogue > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1
Regulators > AVR > Analogue > Manual slope | Manual AVR slope | FLOAT | 10 | %/s | 0 | 200 | 1
Regulators > AVR > Relay configuration > Automatic configuration | Period time | INT32 | 2000 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Minimum ON time | INT32 | 200 | ms | 20 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Automatic configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Period time | INT32 | 2000 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Minimum ON time | INT32 | 200 | ms | 40 | 3600000 | 0 |  | X
Regulators > AVR > Relay configuration > Manual configuration | Maximum ON time | FLOAT | 100 | % | 0 | 100 | 2 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | V deadband | FLOAT | 1 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power load sharing regulation | Q weight | FLOAT | 10 | % | 0 | 100 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Kp | FLOAT | 10 |  | 0 | 1000 | 1 |  | X
Regulators > AVR > Relay configuration > Reactive power regulation | Deadband | FLOAT | 2 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Relay configuration > Voltage droop | Droop | FLOAT | 4 | % | 0 | 10 | 1 |  | X
Regulators > AVR > Monitoring > Regulation error | Set point | FLOAT | 30 | % | 1 | 100 | 1
Regulators > AVR > Monitoring > Regulation error | Delay | FLOAT | 60 | s | 10 | 3600 | 0
Regulators > AVR > Monitoring > Regulation error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > AVR > Monitoring > Regulation mode not selected | Delay | FLOAT | 2 | s | 0 | 3600 | 0
Regulators > AVR > Monitoring > Regulation mode not selected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Regulators > AVR > Monitoring > Q load sharing failure | Set point | FLOAT | 15 | % | 0 | 50 | 1
Regulators > AVR > Monitoring > Q load sharing failure | Delay | FLOAT | 30 | s | 0 | 3600 | 0
Regulators > AVR > Monitoring > Q load sharing failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Generator breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Generator breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Generator breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Generator breaker configuration > Blackout close | Blackout close | INT32 | Generator OK, busbar is dead |  |  |  |  | 0: Blackout close is OFF, 2: Generator OK, busbar is dead
Breakers > Generator breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Generator breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Generator breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Generator breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed min. | FLOAT | 0 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > Synchronisation setting | Delta speed max. | FLOAT | 1 | % | -10 | 10 | 1 |  | X
Breakers > Generator breaker configuration > De-load last breaker | Load share | INT32 | 0 |  | 0 | 1 | 0
Breakers > Generator breaker configuration > De-load last breaker | Fixed frequency | INT32 | 0 |  | 0 | 1 | 0
Breakers > Generator breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Generator breaker monitoring > Synchronisation failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > De-load failure | Delay | FLOAT | 10 | s | 0 | 3600 | 1
Breakers > Generator breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Generator breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Generator breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Opening failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Generator breaker monitoring > Closing failure | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Generator breaker monitoring > Position failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Generator breaker monitoring > Configuration failure | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > Generator breaker monitoring > Tripped (external) | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > Short circuit | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Breakers > Generator breaker monitoring > No synchronisation signal | Delay | FLOAT | 10 | s | 0.1 | 300 | 1 |  | X
Breakers > Generator breaker monitoring > No synchronisation signal | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > Generator breaker monitoring > No synchronisation signal | Inhibit |  | Engine not running, Generator breaker closed | [5 empty] | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 1 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 1 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 1 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 1 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 1 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 2 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 2 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 2 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 2 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Source selection | Pump source select | INT32 | Fuel level |  |  |  |  | 0: Fuel level, 1: Coolant level, 2: Oil level, 3: Custom analogue input, 4: DEF level | X
Auxiliary > Pump logic 3 > Fill alarm | Delay | FLOAT | 60 | s | 1 | 300 | 0 |  | X
Auxiliary > Pump logic 3 > Fill alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Auxiliary > Pump logic 3 > Fill check slope | Fill check slope | FLOAT | 2 | % | 1 | 100 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON set point | FLOAT | 20 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump ON delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF set point | FLOAT | 80 | % | 0 | 100 | 0 |  | X
Auxiliary > Pump logic 3 > Pump logic settings | Pump OFF delay | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > ECU > ECU Power configuration | ECU Power configuration | INT32 | Auto |  |  |  |  | 0: Auto, 1: Always ON | X
Communication > Fieldbus > CAN bus > ECU > ECU powerup time | ECU powerup time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Delay | FLOAT | 1 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > ECU > ECU Communication failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > CAN bus > Digital AVR > Power-up time | Power-up time | FLOAT | 2 | s | 0 | 3600 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Delay | FLOAT | 0 | s | 0 | 120 | 1 |  | X
Communication > Fieldbus > CAN bus > Digital AVR > Communication error | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Missing controllers | Range | INT32 | Section |  |  |  |  | 0: Section, 1: Plant
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block generator breaker |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Any mains breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Group alarm | Delay | FLOAT | 0 | s | 0 | 3600 | 1
System > Monitoring > Group alarm | Action | INT32 | Trip generator breaker and shutdown engine |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | LF |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block generator breaker, 3: Trip generator breaker, 6: Trip generator breaker and stop engine, 7: Trip generator breaker and shutdown engine

## GENSET IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
90130000 | Engine > Command | Start engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130001 | Engine > Command | Stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
90130002 | Engine > Command | Block engine start | DI |  | BOOL_NUM | 0 | 1 | 0
90230002 | Engine > Command | Start engine and close generator breaker | DI |  | BOOL_NUM | 0 | 1 | 0
90230003 | Engine > Command | Open generator breaker and stop engine | DI |  | BOOL_NUM | 0 | 1 | 0
11280002 | Engine > Feedback | Digital running detection | DI |  | BOOL_NUM | 0 | 1 | 0
11280003 | Engine > Function | Remove start (release crank relay) | DI |  | BOOL_NUM | 0 | 1 | 0
12080001 | Engine > Function | Start enable | DI |  | BOOL_NUM | 0 | 1 | 0
170000900 | Engine > ECU | Measurement list filter - available | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000901 | Engine > ECU | Measurement list filter - clear | DI |  | BOOL_NUM | 0 | 1 | 0 | X
170000930 | Engine > ECU | ECU reset input | DI |  | BOOL_NUM | 0 | 1 | 0
11180002 | Engine > Idle run | End idle start | DI |  | BOOL_NUM | 0 | 1 | 0
11180003 | Engine > Idle run | End idle stop | DI |  | BOOL_NUM | 0 | 1 | 0
11080100 | Engine > Safety shutdown | Manual reset | DI |  | BOOL_NUM | 0 | 1 | 0
11080054 | Engine > ECU diagnostic | ECU diagnostic on | DI |  | BOOL_NUM | 0 | 1 | 0
11080055 | Engine > ECU diagnostic | ECU diagnostic off | DI |  | BOOL_NUM | 0 | 1 | 0
70100053 | Regulators > GOV > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
70100063 | Regulators > GOV > Command | Activate ramp 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100064 | Regulators > GOV > Command | Activate ramp 2 | DI |  | BOOL_NUM | 0 | 1 | 0
90230011 | Regulators > GOV > Command | Reset GOV to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100055 | Regulators > GOV > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100065 | Regulators > GOV > Modes | Override GOV automatic regulator mode | DI |  | BOOL_NUM | 0 | 1 | 0
70100200 | Regulators > GOV > Modes | Activate fixed frequency | DI |  | BOOL_NUM | 0 | 1 | 0
70100201 | Regulators > GOV > Modes | Activate fixed power | DI |  | BOOL_NUM | 0 | 1 | 0
70100202 | Regulators > GOV > Modes | Activate frequency droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100203 | Regulators > GOV > Modes | Activate power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100207 | Regulators > GOV > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100208 | Regulators > GOV > Modes | Activate fixed RPM | DI |  | BOOL_NUM | 0 | 1 | 0
80100000 | Regulators > GOV > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230006 | Regulators > GOV > Manual | Manual GOV increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230007 | Regulators > GOV > Manual | Manual GOV decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100206 | Regulators > GOV > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100216 | Regulators > GOV > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100057 | Regulators > GOV > Active power offset | Active power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100058 | Regulators > GOV > Active power offset | Active power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100059 | Regulators > GOV > Active power offset | Active power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100054 | Regulators > AVR > Command | Pause ramping | DI |  | BOOL_NUM | 0 | 1 | 0
90230010 | Regulators > AVR > Command | Reset AVR to offset | DI |  | BOOL_NUM | 0 | 1 | 0
70100056 | Regulators > AVR > Modes | Deactivate regulation | DI |  | BOOL_NUM | 0 | 1 | 0
70100066 | Regulators > AVR > Modes | Override AVR automatic regulator mode | DI |  | BOOL_NUM | 0 | 1 | 0
70100500 | Regulators > AVR > Modes | Activate fixed voltage | DI |  | BOOL_NUM | 0 | 1 | 0
70100501 | Regulators > AVR > Modes | Activate fixed reactive power | DI |  | BOOL_NUM | 0 | 1 | 0
70100502 | Regulators > AVR > Modes | Activate fixed cos phi | DI |  | BOOL_NUM | 0 | 1 | 0
70100503 | Regulators > AVR > Modes | Activate voltage droop | DI |  | BOOL_NUM | 0 | 1 | 0
70100504 | Regulators > AVR > Modes | Activate reactive power load sharing | DI |  | BOOL_NUM | 0 | 1 | 0
70100508 | Regulators > AVR > Modes | Activate manual regulation | DI |  | BOOL_NUM | 0 | 1 | 0
80100001 | Regulators > AVR > Modes | Stand-alone mode | DI |  | BOOL_NUM | 0 | 1 | 0 | X
90230008 | Regulators > AVR > Manual | Manual AVR increase | DI |  | BOOL_NUM | 0 | 1 | 0
90230009 | Regulators > AVR > Manual | Manual AVR decrease | DI |  | BOOL_NUM | 0 | 1 | 0
70100507 | Regulators > AVR > External set points | Activate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100517 | Regulators > AVR > External set points | Deactivate external set point | DI |  | BOOL_NUM | 0 | 1 | 0
70100060 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 1 | DI |  | BOOL_NUM | 0 | 1 | 0
70100061 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 2 | DI |  | BOOL_NUM | 0 | 1 | 0
70100062 | Regulators > AVR > Cos phi/reactive power offset | Cos phi/Reactive power offset 3 | DI |  | BOOL_NUM | 0 | 1 | 0
70100052 | Regulators > Common | Freeze regulator | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Generator breaker > Command | GB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Generator breaker > Command | GB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Generator breaker > Command | GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Generator breaker > Command | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Generator breaker > Command | GB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Generator breaker > Command | Block GB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Generator breaker > Feedback | GB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Generator breaker > Feedback | GB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Generator breaker > Feedback | GB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Generator breaker > Feedback | GB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
11580002 | Auxiliary > Pump logic | Activate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11580003 | Auxiliary > Pump logic | Deactivate pump logic 1 | DI |  | BOOL_NUM | 0 | 1 | 0
11680002 | Auxiliary > Pump logic | Activate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11680003 | Auxiliary > Pump logic | Deactivate pump logic 2 | DI |  | BOOL_NUM | 0 | 1 | 0
11780002 | Auxiliary > Pump logic | Activate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
11780003 | Auxiliary > Pump logic | Deactivate pump logic 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
100001100 | Alarm system > Additional functions | Emergency stop | DI |  | BOOL_NUM | 0 | 1 | 0
110100012 | Alarm system > Additional functions | Group alarm | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
11080000 | Engine > Controls | Run coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080001 | Engine > Controls | Stop coil | DO |  | BOOL_NUM | 0 | 1 | 0
11080002 | Engine > Controls | Start prepare | DO |  | BOOL_NUM | 0 | 1 | 0
11080003 | Engine > Controls | Crank | DO |  | BOOL_NUM | 0 | 1 | 0
11480000 | Engine > Controls | Priming | DO |  | BOOL_NUM | 0 | 1 | 0
170000902 | Engine > Controls | ECU power | DO |  | BOOL_NUM | 0 | 1 | 0
11180001 | Engine > Controls | Idle run | DO |  | BOOL_NUM | 0 | 1 | 0
11080021 | Engine > State | Not ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080022 | Engine > State | Ready to start | DO |  | BOOL_NUM | 0 | 1 | 0
11080023 | Engine > State | Starting | DO |  | BOOL_NUM | 0 | 1 | 0
11080024 | Engine > State | Cooldown | DO |  | BOOL_NUM | 0 | 1 | 0
11080027 | Engine > State | Stopping | DO |  | BOOL_NUM | 0 | 1 | 0
11080028 | Engine > State | Extended stop | DO |  | BOOL_NUM | 0 | 1 | 0
11080041 | Engine > State | Start prepare completed | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11280005 | Engine > State | Running | DO |  | BOOL_NUM | 0 | 1 | 0
11280006 | Engine > State | Not running | DO |  | BOOL_NUM | 0 | 1 | 0
11880000 | Engine > State | Engine heater | DO |  | BOOL_NUM | 0 | 1 | 0
11180000 | Engine > State | Idling | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11080101 | Engine > Safety shutdown | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
40219000 | Generator > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Generator > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40418002 | Generator > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Generator > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90120018 | Generator > AVR | Trip AVR | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
70100004 | Regulators > GOV > Controls | GOV increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100005 | Regulators > GOV > Controls | GOV decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100220 | Regulators > GOV > State | Fixed frequency regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100221 | Regulators > GOV > State | Fixed power regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100222 | Regulators > GOV > State | Frequency droop regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100223 | Regulators > GOV > State | Power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100224 | Regulators > GOV > State | Manual GOV regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100227 | Regulators > GOV > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100228 | Regulators > GOV > State | Fixed RPM is active | DO |  | BOOL_NUM | 0 | 1 | 0
80100002 | Regulators > GOV > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
70100002 | Regulators > AVR > Controls | AVR increase | DO |  | BOOL_NUM | 0 | 1 | 0
70100003 | Regulators > AVR > Controls | AVR decrease | DO |  | BOOL_NUM | 0 | 1 | 0
70100520 | Regulators > AVR > State | Fixed voltage is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100521 | Regulators > AVR > State | Fixed reactive power is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100522 | Regulators > AVR > State | Fixed cos phi is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100523 | Regulators > AVR > State | Reactive power load sharing is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100524 | Regulators > AVR > State | Voltage droop is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100525 | Regulators > AVR > State | Manual AVR regulation is active | DO |  | BOOL_NUM | 0 | 1 | 0
70100528 | Regulators > AVR > State | External set point is active | DO |  | BOOL_NUM | 0 | 1 | 0
80100003 | Regulators > AVR > State | Stand-alone is active | DO |  | BOOL_NUM | 0 | 1 | 0 | X
20180002 | Breakers > Generator breaker > Controls | GB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Generator breaker > Controls | GB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Generator breaker > Controls | GB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Generator breaker > State | GB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Generator breaker > State | GB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Generator breaker > State | GB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Generator breaker > State | GB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Generator breaker > State | GB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
11580000 | Auxiliary > Pump logic | Activate pump 1 | DO |  | BOOL_NUM | 0 | 1 | 0
11680000 | Auxiliary > Pump logic | Activate pump 2 | DO |  | BOOL_NUM | 0 | 1 | 0
11780000 | Auxiliary > Pump logic | Activate pump 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035008 | Alarm system > State | Any GB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035009 | Alarm system > State | Any GB trip and stop alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035010 | Alarm system > State | Any GB trip and shutdown alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035023 | Alarm system > State | Any AVR trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035024 | Alarm system > State | Any GB + AVR alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035025 | Alarm system > State | Any GB + AVR + stop engine alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
90120012 | Local > System OK | GAM3.2 1 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120013 | Local > System OK | GAM3.2 2 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
90120014 | Local > System OK | GAM3.2 3 status OK | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
11080004 | Engine > Measurements > Coolant | Engine coolant water | AI | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant | Engine coolant level | AI | % | FLOAT | 0 | 100 | 1
11080031 | Engine > Measurements > Lube oil | Engine oil temperature | AI | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil | Engine oil level | AI | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil | Engine oil pressure | AI | bar | FLOAT | 0 | 10 | 1
11080052 | Engine > Measurements > Fuel | Engine fuel level | AI | % | FLOAT | 0 | 100 | 1
11880001 | Engine > Engine heater | Custom analogue engine heater input | AI | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AI | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AI | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AI | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AI | % | FLOAT | 0 | 100 | 0
40140000 | Busbar > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1 | X
40140001 | Busbar > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1 | X
40140002 | Busbar > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1 | X
70100034 | Regulators > GOV | Frequency offset | AI | % | FLOAT | -10 | 10 | 1
70100035 | Regulators > GOV | Power set point | AI | % | FLOAT | 0 | 100 | 0
70100036 | Regulators > AVR | Voltage offset | AI | % | FLOAT | -10 | 10 | 1
70100037 | Regulators > AVR | Reactive power set point | AI | % | FLOAT | 0 | 100 | 0
70100038 | Regulators > AVR | Cos phi set point | AI |  | FLOAT | 0.6 | 1 | 4
11580004 | Auxiliary > Pump logic | Custom analogue input 1 | AI | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic | Custom analogue input 2 | AI | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic | Custom analogue input 3 | AI | % | FLOAT | 0 | 100 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
11080044 | Engine > Measurements > Coolant | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080045 | Engine > Measurements > Coolant | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080004 | Engine > Measurements > Coolant > Analogue input | Engine coolant water | AO | °C | FLOAT | -50 | 200 | 0
11080040 | Engine > Measurements > Coolant > Analogue input | Engine coolant level | AO | % | FLOAT | 0 | 100 | 1
11080042 | Engine > Measurements > Lube oil | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080043 | Engine > Measurements > Lube oil | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080058 | Engine > Measurements > Lube oil | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11080031 | Engine > Measurements > Lube oil > Analogue input | Engine oil temperature | AO | °C | FLOAT | -50 | 200 | 0
11080057 | Engine > Measurements > Lube oil > Analogue input | Engine oil level | AO | % | FLOAT | 0 | 100 | 0
11280000 | Engine > Measurements > Lube oil > Analogue input | Engine oil pressure | AO | bar | FLOAT | 0 | 10 | 1
11080046 | Engine > Measurements > Speed | Engine speed | AO | RPM | FLOAT | 0 | 2000 | 0
11280001 | Engine > Measurements > Speed > Analogue input | Engine MPU | AO | RPM | FLOAT | 0 | 2000 | 0
11080053 | Engine > Measurements > Fuel | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
11080052 | Engine > Measurements > Fuel > Analogue input | Engine fuel level | AO | % | FLOAT | 0 | 100 | 1
40600510 | Engine > Power derate > Temperature | Derate 1 temperature | AO | °C | FLOAT | -50 | 200 | 1
40610510 | Engine > Power derate > Temperature | Derate 2 temperature | AO | °C | FLOAT | -50 | 200 | 1
40620510 | Engine > Power derate > Temperature | Derate 3 temperature | AO | °C | FLOAT | -50 | 200 | 1
40640010 | Engine > Power derate > Percentage | Derate percentage | AO | % | FLOAT | 0 | 100 | 0
11380002 | Engine > Service timers | Hours until total running hours notification | AO | h | FLOAT | -1000000 | 1000000 | 0
11380003 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380013 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380014 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380015 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380016 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380017 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380018 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380019 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380020 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
11380021 | Engine > Service timers | [User defined] | AO | h | FLOAT | -1000000 | 1000000 | 0
40110000 | Generator > Voltage (V) | Generator ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Generator > Voltage (V) | Generator ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Generator > Voltage (V) | Generator ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Generator > Voltage (V) | Generator ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Generator > Voltage (V) | Generator ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Generator > Voltage (V) | Generator ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Generator > Voltage (V) | Generator ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Generator > Voltage (V) | Generator ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Generator > Voltage (V) | Generator ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Generator > Voltage (V) | Generator ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Generator > Voltage (V) | Generator ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Generator > Voltage (V) | Generator ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Generator > Voltage (V) | Generator ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Generator > Voltage (V) | Generator ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Generator > Voltage (V) | Generator ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Generator > Voltage (V) | Generator ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Generator > Frequency (f) (from voltage) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Generator > Frequency (f) (from voltage) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Generator > Frequency (f) (from voltage) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Generator > Frequency (f) (from voltage) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Generator > Frequency (f) (from voltage) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Generator > Frequency (f) (from voltage) | Generator ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Generator > Frequency (f) (from current) | Generator ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Generator > Frequency (f) (from current) | Generator ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Generator > Frequency (f) (from current) | Generator ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Generator > Frequency (f) (from current) | Generator ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Generator > Frequency (f) (from current) | Generator ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Generator > Current (I) | Generator ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Generator > Current (I) | Generator ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Generator > Current (I) | Generator ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Generator > Current (I) | Generator ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Generator > Current (I) | Generator ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Generator > Current (I) | Generator ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Generator > Current (I) | Generator ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Generator > Current (I) | Generator ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Generator > Current (I) | Generator ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Generator > Current (I) | Generator ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Generator > Current (I) | Generator ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Generator > Power (P) | Generator ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Generator > Power (P) | Generator ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Generator > Power (P) | Generator ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Generator > Power (P) | Generator ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Generator > Power (P) | Generator ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Generator > Power (P) | Generator ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Generator > Power (P) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Generator > Power (P) | Generator ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Generator > Power (P) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Generator > Reactive power (Q) | Generator ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Generator > Reactive power (Q) | Generator ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Generator > Reactive power (Q) | Generator ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Generator > Reactive power (Q) | Generator ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Generator > Reactive power (Q) | Generator ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Generator > Reactive power (Q) | Generator ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Generator > Reactive power (Q) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Generator > Reactive power (Q) | Generator ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Generator > Reactive power (Q) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Generator > Apparent power (S) | Generator ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Generator > Apparent power (S) | Generator ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Generator > Apparent power (S) | Generator ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Generator > Apparent power (S) | Generator ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Generator > Apparent power (S) | Generator ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Generator > Apparent power (S) | Generator ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Generator > Apparent power (S) | Generator ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Generator > Apparent power (S) | Generator ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Generator > Apparent power (S) | Generator ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Generator > Power factor (PF) | Generator ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Generator > Power factor (PF) | Generator ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Generator > Phase angle | Generator ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Generator > Phase angle | Generator ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Generator > Phase angle | Generator ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Generator > Phase angle | Generator ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Generator > Phase angle | Generator ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Generator > Phase angle | Generator ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
70100001 | Regulators > GOV | GOV output | AO | % | FLOAT | -100 | 100 | 0
70100000 | Regulators > AVR | AVR output | AO | % | FLOAT | -100 | 100 | 0
11580004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 1 | AO | % | FLOAT | 0 | 100 | 1
11680004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 2 | AO | % | FLOAT | 0 | 100 | 1
11780004 | Auxiliary > Pump logic > Analogue input | Custom analogue input 3 | AO | % | FLOAT | 0 | 100 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100210 | System power management > Monitoring > Plant | Plant ¦ P produced | AO | kW | FLOAT | 0 | 1000 | 0
110100211 | System power management > Monitoring > Plant | Plant ¦ Q produced | AO | kvar | FLOAT | 0 | 750 | 0
110100212 | System power management > Monitoring > Plant | Plant ¦ S produced | AO | kVA | FLOAT | 0 | 1250 | 0
110100213 | System power management > Monitoring > Plant | Plant ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
110100200 | System power management > Monitoring > Section | Section ¦ P produced | AO | kW | FLOAT | 0 | 1000 | 0
110100201 | System power management > Monitoring > Section | Section ¦ Q produced | AO | kvar | FLOAT | 0 | 750 | 0
110100202 | System power management > Monitoring > Section | Section ¦ S produced | AO | kVA | FLOAT | 0 | 1250 | 0
110100203 | System power management > Monitoring > Section | Section ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
110100204 | System power management > Monitoring > Section | Section ¦ P used | AO | % | FLOAT | -100 | 100 | 0
110100205 | System power management > Monitoring > Section | Section ¦ Q used | AO | % | FLOAT | -100 | 100 | 0
110100206 | System power management > Monitoring > Section | Section ¦ S used | AO | % | FLOAT | -100 | 100 | 0
110100300 | System power management > Monitoring > Section | Section ¦ P nominal | AO | kW | FLOAT | 0 | 1000 | 0
110100301 | System power management > Monitoring > Section | Section ¦ Q nominal | AO | kvar | FLOAT | 0 | 750 | 0
110100302 | System power management > Monitoring > Section | Section ¦ S nominal | AO | kVA | FLOAT | 0 | 1250 | 0
110100400 | System power management > Monitoring > Section | Section ¦ P available | AO | kW | FLOAT | 0 | 1000 | 0
110100401 | System power management > Monitoring > Section | Section ¦ Q available | AO | kvar | FLOAT | 0 | 750 | 0
110100402 | System power management > Monitoring > Section | Section ¦ S available | AO | kVA | FLOAT | 0 | 1250 | 0
110100410 | System power management > Monitoring > Section | Section ¦ P available | AO | % | FLOAT | -100 | 100 | 0
110100411 | System power management > Monitoring > Section | Section ¦ Q available | AO | % | FLOAT | -100 | 100 | 0
110100412 | System power management > Monitoring > Section | Section ¦ S available | AO | % | FLOAT | -100 | 100 | 0
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## MAINS parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Mains > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Mains > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Mains > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Mains > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Mains > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Mains > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Mains > AC setup > Supervision selector | Enable supervision | INT32 | 0 |  | 0 | 1 | 0
Mains > AC setup > Supervision selector | Recovery selector time | FLOAT | 3 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time fast | FLOAT | 5 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Recovery time slow | FLOAT | 60 | s | 0.1 | 3600 | 1
Mains > AC setup > Supervision selector | Voltage low | FLOAT | 85 | % | 80 | 100 | 1
Mains > AC setup > Supervision selector | Voltage high | FLOAT | 110 | % | 100 | 120 | 1
Mains > AC setup > Supervision selector | Frequency low | FLOAT | 95 | % | 90 | 100 | 1
Mains > AC setup > Supervision selector | Frequency high | FLOAT | 101 | % | 100 | 110 | 1
Mains > AC setup > Supervision alarm | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Mains > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Mains > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Mains > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Mains > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Mains > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Mains > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Mains > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Mains > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Mains > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Mains > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Mains > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Mains > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Mains > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Mains > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Mains > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Mains > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Mains > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Mains > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Mains > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Mains > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Mains > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Mains > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Mains > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Mains > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Mains > Voltage protections > Over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Mains > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Mains > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Mains > Voltage protections > Under-voltage 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Mains > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Mains > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Voltage unbalance | Inhibit |  | No mains voltage
Mains > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Mains > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Mains > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Positive sequence under-voltage | Inhibit |  | Genset not in parallel
Mains > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Mains > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Mains > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Mains > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Current protections > Over-current 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Mains > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Mains > Current protections > Fast over-current 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Mains > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Mains > Current protections > Fast over-current 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Mains > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Mains > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Mains > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Mains > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Mains > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Mains > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Mains > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Mains > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Mains > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Mains > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Mains > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Mains > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Mains > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Mains > Current protections > Inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Mains > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Mains > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Mains > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Mains > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Over-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Mains > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Frequency protections > Under-frequency 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Overload 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Mains > Power protections > Overload 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Mains > Power protections > Overload 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Overload 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Overload 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 3 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Overload 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 4 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Overload 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Mains > Power protections > Overload 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Overload 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Overload 5 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Reverse power 1 | Set point | FLOAT | 5 | % | 0 | 200 | 1
Mains > Power protections > Reverse power 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Reverse power 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Power protections > Reverse power 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Power protections > Reverse power 2 | Set point | FLOAT | 10 | % | 0 | 200 | 1
Mains > Power protections > Reverse power 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Power protections > Reverse power 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Power protections > Reverse power 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 40 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 50 | % | 0 | 300 | 1
Mains > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Mains > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
Mains > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Mains > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Mains > Additional protections > V< and Q< 1 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 1: Phase-phase busbar, 2: Phase-neutral busbar, 9: Phase-phase mains, 10: Phase-neutral mains
Mains > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Mains > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Mains > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Mains > Additional protections > V< and Q< 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
Mains > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Mains > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Mains > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Mains > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase mains |  |  |  |  | 48: Phase-phase busbar, 49: Phase-neutral busbar, 50: Phase-phase mains, 51: Phase-neutral mains
Mains > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Mains > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Mains > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Mains > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Mains > Additional protections > Average over-voltage 2 | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Mains > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Mains > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Mains > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Mains > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input
Busbar > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar > AC setup > Phase sequence error | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use mains nominal voltage |  |  |  |  | 0: User defined, 1: Use mains nominal voltage
Busbar > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 2 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Over-voltage 3 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 2 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 3 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar > Voltage protections > Under-voltage 4 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Positive sequence under-voltage | Inhibit |  | Genset not in parallel
Busbar > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 2 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar > Frequency protections > Over-frequency 3 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 2 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 3 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar > Frequency protections > Under-frequency 4 | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Additional protections > Vector shift | AC setup | INT32 | Busbar |  |  |  |  | 34: Busbar, 35: Mains
Busbar > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar > Additional protections > Vector shift | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Additional protections > Vector shift | Inhibit |  | Genset not in parallel
Busbar > Additional protections > ROCOF | AC setup | INT32 | Busbar |  |  |  |  | 32: Busbar, 33: Mains
Busbar > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar > Additional protections > ROCOF | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Busbar > Additional protections > ROCOF | Inhibit |  | Genset not in parallel
Breakers > Tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Tie breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Load point is dead, busbar OK, 2: Load point OK, busbar is dead, 3: One busbar is alive, 4: On
Breakers > Tie breaker configuration > Synchronisation setting | Sync type | INT32 | Dynamic |  |  |  |  | 0: Static, 1: Dynamic
Breakers > Tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | -0.3 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1 |  | X
Breakers > Tie breaker configuration > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Tie breaker configuration > Synchronisation failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Opening failure | Action | INT32 | Block tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Tie breaker monitoring > Closing failure | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Tie breaker monitoring > Position failure | Action | INT32 | Block tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Tie breaker monitoring > Configuration failure | Action | INT32 | Block tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > Tie breaker monitoring > Tripped (external) | Action | INT32 | Block tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Tie breaker monitoring > Short circuit | Action | INT32 | Trip tie breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Mains breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Mains breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Spring-load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Mains breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Mains breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Mains is dead, busbar OK, 2: Mains OK, busbar is dead, 3: One busbar is alive, 4: On
Breakers > Mains breaker configuration > Synchronisation setting | Sync type | INT32 | Automatic |  |  |  |  | 0: Static, 1: Dynamic, 3: Automatic
Breakers > Mains breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Mains breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1
Breakers > Mains breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1
Breakers > Mains breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Mains breaker monitoring > Synchronisation failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Mains breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Mains breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Mains breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Opening failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Mains breaker monitoring > Closing failure | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Mains breaker monitoring > Position failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Mains breaker monitoring > Configuration failure | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > Mains breaker monitoring > Tripped (external) | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > Mains breaker monitoring > Short circuit | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Missing controllers | Range | INT32 | Section |  |  |  |  | 0: Section, 1: Plant
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block mains breaker |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Any mains breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Group alarm | Delay | FLOAT | 0 | s | 0 | 3600 | 1
System > Monitoring > Group alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | LF |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block mains breaker, 3: Trip mains breaker, 4: Trip tie breaker, 14: Block tie breaker, 15: Trip mains and tie breaker

## MAINS IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
3316001 | Breakers > Tie breaker > Command | TB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3316002 | Breakers > Tie breaker > Command | TB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20280028 | Breakers > Tie breaker > Command | TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280029 | Breakers > Tie breaker > Command | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280030 | Breakers > Tie breaker > Command | Open TB without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20280031 | Breakers > Tie breaker > Command | Block TB close | DI |  | BOOL_NUM | 0 | 1 | 0
20280000 | Breakers > Tie breaker > Feedback | TB open | DI |  | BOOL_NUM | 0 | 1 | 0
20280001 | Breakers > Tie breaker > Feedback | TB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20280004 | Breakers > Tie breaker > Feedback | TB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20280012 | Breakers > Tie breaker > Feedback | TB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
3306001 | Breakers > Mains breaker > Command | MB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Mains breaker > Command | MB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Mains breaker > Command | MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Mains breaker > Command | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Mains breaker > Command | Open MB without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Mains breaker > Command | Block MB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Mains breaker > Feedback | MB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Mains breaker > Feedback | MB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Mains breaker > Feedback | MB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Mains breaker > Feedback | MB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
110100012 | Alarm system > Additional functions | Group alarm | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Mains > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Mains > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Mains > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Mains > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Mains > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Mains > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Mains > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Mains > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
90820001 | Mains > Supervision | Mains error | DO |  | BOOL_NUM | 0 | 1 | 0
90820002 | Mains > Supervision | Mains recovery fast | DO |  | BOOL_NUM | 0 | 1 | 0
90820003 | Mains > Supervision | Mains recovery slow | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20280002 | Breakers > Tie breaker > Controls | TB open | DO |  | BOOL_NUM | 0 | 1 | 0
20280003 | Breakers > Tie breaker > Controls | TB close | DO |  | BOOL_NUM | 0 | 1 | 0
20280027 | Breakers > Tie breaker > Controls | TB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20280014 | Breakers > Tie breaker > State | TB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20280015 | Breakers > Tie breaker > State | TB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20280024 | Breakers > Tie breaker > State | TB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20280025 | Breakers > Tie breaker > State | TB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20280026 | Breakers > Tie breaker > State | TB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Mains breaker > Controls | MB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Mains breaker > Controls | MB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Mains breaker > Controls | MB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Mains breaker > State | MB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Mains breaker > State | MB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Mains breaker > State | MB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Mains breaker > State | MB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Mains breaker > State | MB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035011 | Alarm system > State | Any TB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035019 | Alarm system > State | Any MB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035028 | Alarm system > State | Any TB block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035029 | Alarm system > State | Any MB and TB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40140000 | Busbar > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1
40140001 | Busbar > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1
40140002 | Busbar > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Mains > Voltage (V) | Mains ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Mains > Voltage (V) | Mains ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Mains > Voltage (V) | Mains ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Mains > Voltage (V) | Mains ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Mains > Voltage (V) | Mains ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Mains > Voltage (V) | Mains ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Mains > Voltage (V) | Mains ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Mains > Voltage (V) | Mains ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Mains > Voltage (V) | Mains ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Mains > Voltage (V) | Mains ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Mains > Voltage (V) | Mains ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Mains > Voltage (V) | Mains ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Mains > Voltage (V) | Mains ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Mains > Voltage (V) | Mains ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Mains > Voltage (V) | Mains ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Mains > Voltage (V) | Mains ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Mains > Frequency (f) (from voltage) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Mains > Frequency (f) (from voltage) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Mains > Frequency (f) (from voltage) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Mains > Frequency (f) (from voltage) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Mains > Frequency (f) (from voltage) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Mains > Frequency (f) (from voltage) | Mains ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Mains > Frequency (f) (from current) | Mains ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Mains > Frequency (f) (from current) | Mains ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Mains > Frequency (f) (from current) | Mains ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Mains > Frequency (f) (from current) | Mains ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Mains > Frequency (f) (from current) | Mains ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Mains > Current (I) | Mains ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Mains > Current (I) | Mains ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Mains > Current (I) | Mains ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Mains > Current (I) | Mains ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Mains > Current (I) | Mains ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Mains > Current (I) | Mains ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Mains > Current (I) | Mains ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Mains > Current (I) | Mains ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Mains > Current (I) | Mains ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Mains > Current (I) | Mains ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Mains > Current (I) | Mains ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Mains > Power (P) | Mains ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Mains > Power (P) | Mains ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Mains > Power (P) | Mains ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Mains > Power (P) | Mains ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Mains > Power (P) | Mains ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Mains > Power (P) | Mains ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Mains > Power (P) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Mains > Power (P) | Mains ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Mains > Power (P) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Mains > Reactive power (Q) | Mains ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Mains > Reactive power (Q) | Mains ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Mains > Reactive power (Q) | Mains ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Mains > Reactive power (Q) | Mains ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Mains > Reactive power (Q) | Mains ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Mains > Reactive power (Q) | Mains ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Mains > Reactive power (Q) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Mains > Reactive power (Q) | Mains ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Mains > Reactive power (Q) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Mains > Apparent power (S) | Mains ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Mains > Apparent power (S) | Mains ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Mains > Apparent power (S) | Mains ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Mains > Apparent power (S) | Mains ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Mains > Apparent power (S) | Mains ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Mains > Apparent power (S) | Mains ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Mains > Apparent power (S) | Mains ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Mains > Apparent power (S) | Mains ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Mains > Apparent power (S) | Mains ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Mains > Power factor (PF) | Mains ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Mains > Power factor (PF) | Mains ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Mains > Phase angle | Mains ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Mains > Phase angle | Mains ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Mains > Phase angle | Mains ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Mains > Phase angle | Mains ¦ A-B phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Mains > Phase angle | Mains ¦ A-B phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Mains > Phase angle | Mains ¦ A-B phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar > Voltage (V) | Busbar ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar > Voltage (V) | Busbar ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar > Voltage (V) | Busbar ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar > Voltage (V) | Busbar ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar > Voltage (V) | Busbar ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar > Voltage (V) | Busbar ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar > Voltage (V) | Busbar ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar > Voltage (V) | Busbar ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar > Voltage (V) | Busbar ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar > Voltage (V) | Busbar ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar > Voltage (V) | Busbar ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar > Voltage (V) | Busbar ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar > Voltage (V) | Busbar ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar > Voltage (V) | Busbar ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar > Voltage (V) | Busbar ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar > Voltage (V) | Busbar ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar > Frequency (f) | Busbar ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar > Frequency (f) | Busbar ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar > Frequency (f) | Busbar ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar > Frequency (f) | Busbar ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar > Frequency (f) | Busbar ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar > Frequency (f) | Busbar ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100024 | Busbar > Power (P) | Busbar ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100025 | Busbar > Power (P) | Busbar ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100026 | Busbar > Power (P) | Busbar ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40100027 | Busbar > Reactive power (Q) | Busbar ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100028 | Busbar > Reactive power (Q) | Busbar ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100029 | Busbar > Reactive power (Q) | Busbar ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40100030 | Busbar > Apparent power (S) | Busbar ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100031 | Busbar > Apparent power (S) | Busbar ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100032 | Busbar > Apparent power (S) | Busbar ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40100018 | Busbar > Phase angle | Busbar ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar > Phase angle | Busbar ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar > Phase angle | Busbar ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100210 | System power management > Monitoring > Plant | Plant ¦ P produced | AO | kW | FLOAT | 0 | 0 | 0
110100211 | System power management > Monitoring > Plant | Plant ¦ Q produced | AO | kvar | FLOAT | 0 | 0 | 0
110100212 | System power management > Monitoring > Plant | Plant ¦ S produced | AO | kVA | FLOAT | 0 | 0 | 0
110100213 | System power management > Monitoring > Plant | Plant ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
110100200 | System power management > Monitoring > Section | Section ¦ P produced | AO | kW | FLOAT | 0 | 0 | 0
110100201 | System power management > Monitoring > Section | Section ¦ Q produced | AO | kvar | FLOAT | 0 | 0 | 0
110100202 | System power management > Monitoring > Section | Section ¦ S produced | AO | kVA | FLOAT | 0 | 0 | 0
110100203 | System power management > Monitoring > Section | Section ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
110100204 | System power management > Monitoring > Section | Section ¦ P used | AO | % | FLOAT | -100 | 100 | 0
110100205 | System power management > Monitoring > Section | Section ¦ Q used | AO | % | FLOAT | -100 | 100 | 0
110100206 | System power management > Monitoring > Section | Section ¦ S used | AO | % | FLOAT | -100 | 100 | 0
110100300 | System power management > Monitoring > Section | Section ¦ P nominal | AO | kW | FLOAT | 0 | 0 | 0
110100301 | System power management > Monitoring > Section | Section ¦ Q nominal | AO | kvar | FLOAT | 0 | 0 | 0
110100302 | System power management > Monitoring > Section | Section ¦ S nominal | AO | kVA | FLOAT | 0 | 0 | 0
110100400 | System power management > Monitoring > Section | Section ¦ P available | AO | kW | FLOAT | 0 | 0 | 0
110100401 | System power management > Monitoring > Section | Section ¦ Q available | AO | kvar | FLOAT | 0 | 0 | 0
110100402 | System power management > Monitoring > Section | Section ¦ S available | AO | kVA | FLOAT | 0 | 0 | 0
110100410 | System power management > Monitoring > Section | Section ¦ P available | AO | % | FLOAT | -100 | 100 | 0
110100411 | System power management > Monitoring > Section | Section ¦ Q available | AO | % | FLOAT | -100 | 100 | 0
110100412 | System power management > Monitoring > Section | Section ¦ S available | AO | % | FLOAT | -100 | 100 | 0
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1

## BTB parameters
Parameter path | Parameter name | Data type | Default | Unit | Minimum | Maximum | Decimals | Selections | Hidden
Busbar A > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar A > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar A > AC setup > Current transformer | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Busbar A > AC setup > Current transformer | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Busbar A > AC setup > Phase configuration | AC configuration | INT32 | Three-phase |  |  |  |  | 0: Three-phase, 8: Three-phase (2 CT, L1-L3), 9: Three-phase (L1-L2, CT L1), 1: Split-phase L1-L3, 2: Split-phase L1-L2, 4: Split-phase L2-L3, 3: Single-phase L1, 5: Single-phase L2, 6: Single-phase L3
Busbar A > AC setup > Phase direction | AC setup | INT32 | L1-L2-L3 |  |  |  |  | 0: L1-L2-L3, 1: L1-L3-L2
Busbar A > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar A > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar A > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar A > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar A > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar A > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar A > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar A > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Busbar A > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar A > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 1 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 1 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 1 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 2 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 2 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 2 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 3 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 3 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 3 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Current (I) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Frequency (f) | Nominal | FLOAT | 50 | Hz | 20 | 100 | 2
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | Reactive power (Q) nominal | INT32 | Q nominal calculated |  |  |  |  | 0: Q nominal calculated, 1: Q nominal = P nominal, 2: Q nominal = S nominal
Busbar A > Nominal settings > Nominal settings 4 > Calculation method | P or S nominal | INT32 | No calculation |  |  |  |  | 0: No calculation, 1: P nominal calculated, 2: S nominal calculated
Busbar A > Nominal settings > Nominal settings 4 > Power (P) | Nominal | FLOAT | 1000 | kW | 1 | 900000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Apparent power (S) | Nominal | FLOAT | 1250 | kVA | 1 | 1000000 | 1
Busbar A > Nominal settings > Nominal settings 4 > Power factor (PF) | Nominal | FLOAT | 0.8 |  | 0.6 | 1 | 4
Busbar A > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Over-voltage 2 | Set point | FLOAT | 110 | % | 80 | 120 | 1
Busbar A > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Over-voltage 2 | Delay | FLOAT | 1 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 9: Phase-phase, 10: Phase-neutral
Busbar A > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar A > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar A > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 12: Phase-phase, 11: Phase-neutral
Busbar A > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar A > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Voltage unbalance | Inhibit |  | No busbar A voltage, ACM wire break
Busbar A > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar A > Voltage protections > Positive sequence under-voltage | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar A > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar A > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar A > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 1 | Set point | FLOAT | 105 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 1 | Delay | FLOAT | 20 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 2 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 3 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Over-current 4 | Set point | FLOAT | 120 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Over-current 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Current protections > Over-current 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 1 | Set point | FLOAT | 200 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Fast over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 1 | Delay | FLOAT | 0.5 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Fast over-current 2 | Set point | FLOAT | 300 | % | 50 | 5121.95 | 1
Busbar A > Current protections > Fast over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Fast over-current 2 | Delay | FLOAT | 0.2 | s | 0 | 7200 | 2
Busbar A > Current protections > Fast over-current 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (average calc.) | Set point | FLOAT | 30 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (average calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (average calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Current unbalance (nominal calc.) | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Current unbalance (nominal calc.) | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Current unbalance (nominal calc.) | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 1 | Set point | FLOAT | 110 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 1 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 2 | Set point | FLOAT | 130 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 2 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 3 | Set point | FLOAT | -110 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 3 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 3 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Directional over-current 4 | Set point | FLOAT | -130 | % | -5121.95 | 5121.95 | 1
Busbar A > Current protections > Directional over-current 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Directional over-current 4 | Delay | FLOAT | 0.1 | s | 0 | 7200 | 2
Busbar A > Current protections > Directional over-current 4 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Busbar A > Current protections > Inverse time over-current | Limit | FLOAT | 110 | % | 2 | 200 | 1
Busbar A > Current protections > Inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Busbar A > Current protections > Inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Busbar A > Current protections > Inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Busbar A > Current protections > Inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Negative sequence current | Set point | FLOAT | 20 | % | 1 | 100 | 1
Busbar A > Current protections > Negative sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Negative sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Negative sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Current protections > Zero sequence current | Set point | FLOAT | 20 | % | 0 | 100 | 1
Busbar A > Current protections > Zero sequence current | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Current protections > Zero sequence current | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar A > Current protections > Zero sequence current | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 1 | Set point | FLOAT | 103 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 2 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Over-frequency 3 | Set point | FLOAT | 105 | % | 100 | 120 | 1
Busbar A > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Over-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 1 | Set point | FLOAT | 97 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 2 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 2 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Frequency protections > Under-frequency 3 | Set point | FLOAT | 95 | % | 80 | 100 | 1
Busbar A > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Frequency protections > Under-frequency 3 | Delay | FLOAT | 2 | s | 0 | 7200 | 2
Busbar A > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 1 | Set point | FLOAT | 105 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 2 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 2 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 3 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 3 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 3 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 4 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 4 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 4 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power export 5 | Set point | FLOAT | 115 | % | 0 | 200 | 1
Busbar A > Power protections > Power export 5 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power export 5 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Power protections > Power export 5 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 1 | Set point | FLOAT | 95 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 1 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Power protections > Power import 2 | Set point | FLOAT | 110 | % | 0 | 200 | 1
Busbar A > Power protections > Power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Power protections > Power import 2 | Delay | FLOAT | 30 | s | 0 | 7200 | 2
Busbar A > Power protections > Power import 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 1 | Set point | FLOAT | 60 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power export 2 | Set point | FLOAT | 75 | % | 0 | 300 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power export 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power export 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 1 | Set point | FLOAT | 50 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Reactive power protections > Reactive power import 2 | Set point | FLOAT | 70 | % | 0 | 150 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Reactive power protections > Reactive power import 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar A > Reactive power protections > Reactive power import 2 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > V< and Q< 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
Busbar A > Additional protections > V< and Q< 1 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 1 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Busbar A > Additional protections > V< and Q< 1 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > V< and Q< 1 | Delay | FLOAT | 0.5 | s | 0 | 120.1 | 2
Busbar A > Additional protections > V< and Q< 1 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > V< and Q< 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 1: Phase-phase busbar B, 2: Phase-neutral busbar B, 9: Phase-phase busbar A, 10: Phase-neutral busbar A
Busbar A > Additional protections > V< and Q< 2 | I min. | FLOAT | 10 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 2 | Angle min. | FLOAT | 3 | ° | 0 | 10 | 2
Busbar A > Additional protections > V< and Q< 2 | Set point | FLOAT | 85 | % | 0 | 100 | 1
Busbar A > Additional protections > V< and Q< 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > V< and Q< 2 | Delay | FLOAT | 1.5 | s | 0 | 120.1 | 2
Busbar A > Additional protections > V< and Q< 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > Average over-voltage 1 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
Busbar A > Additional protections > Average over-voltage 1 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Busbar A > Additional protections > Average over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar A > Additional protections > Average over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > Average over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Busbar A > Additional protections > Average over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Additional protections > Average over-voltage 2 | AC setup | INT32 | Phase-phase busbar A |  |  |  |  | 48: Phase-phase busbar B, 49: Phase-neutral busbar B, 50: Phase-phase busbar A, 51: Phase-neutral busbar A
Busbar A > Additional protections > Average over-voltage 2 | V> aggregate time | FLOAT | 30 | s | 30 | 900 | 0
Busbar A > Additional protections > Average over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar A > Additional protections > Average over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar A > Additional protections > Average over-voltage 2 | Delay | FLOAT | 5 | s | 0 | 3600 | 2
Busbar A > Additional protections > Average over-voltage 2 | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar A > Production counters > Active energy export | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy export | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy export | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy import | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy import | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy import | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Active energy difference | Pulse every | INT32 | 10 | kWh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Active energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse every | INT32 | 10 | kvarh | 1 | 10000 | 0 |  | X
Busbar A > Production counters > Reactive energy difference | Pulse length | FLOAT | 1 | s | 0.1 | 3600 | 1 |  | X
Busbar B > AC setup > Voltage transformer | Primary | FLOAT | 400 | V | 10 | 1500000 | 0
Busbar B > AC setup > Voltage transformer | Secondary | FLOAT | 400 | V | 17 | 690 | 0
Busbar B > AC setup > Power measurement | Source | INT32 | None |  |  |  |  | 0: None, 1: I4, 2: Analogue input | X
Busbar B > AC setup > Blackout detection | Blackout delay | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Voltage and frequency OK | FLOAT | 0 | s | 0 | 3600 | 1
Busbar B > AC setup > Voltage and frequency OK | Minimum OK voltage | FLOAT | 95 | % | 70 | 100 | 0
Busbar B > AC setup > Voltage and frequency OK | Maximum OK voltage | FLOAT | 105 | % | 100 | 120 | 0
Busbar B > AC setup > Voltage and frequency OK | Minimum OK frequency | FLOAT | 98 | % | 70 | 100 | 2
Busbar B > AC setup > Voltage and frequency OK | Maximum OK frequency | FLOAT | 102 | % | 100 | 110 | 2
Busbar B > AC setup > Phase sequence error | Detection voltage | FLOAT | 70 | % | 30 | 90 | 0
Busbar B > AC setup > Phase sequence error | Delay | FLOAT | 1 | s | 1 | 10 | 0
Busbar B > AC setup > Phase sequence error | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Busbar B > AC setup > L1 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L1 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L2 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L2 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > L3 wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > L3 wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > AC setup > Multiple phase wire break | Delay | FLOAT | 0.5 | s | 0.5 | 0.5 | 1 |  | X
Busbar B > AC setup > Multiple phase wire break | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 1 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 2 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 3 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal | FLOAT | 400 | V | 10 | 1500000 | 1 |  | X
Busbar B > Nominal settings > Nominal settings 4 > Voltage (V) | Nominal value source | INT32 | Use busbar A nominal voltage |  |  |  |  | 0: User defined, 1: Use busbar A nominal voltage
Busbar B > Voltage protections > Over-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 1 | Set point | FLOAT | 105 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 2 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Over-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Over-voltage 3 | Set point | FLOAT | 115 | % | 90 | 120 | 1
Busbar B > Voltage protections > Over-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Over-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Over-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 1 | Set point | FLOAT | 95 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 1 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 2 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 2 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 2 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 2 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 3 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 3 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 3 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 3 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Under-voltage 4 | AC setup | INT32 | Phase-phase |  |  |  |  | 1: Phase-phase, 2: Phase-neutral
Busbar B > Voltage protections > Under-voltage 4 | Set point | FLOAT | 80 | % | 10 | 100 | 1
Busbar B > Voltage protections > Under-voltage 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Under-voltage 4 | Delay | FLOAT | 3 | s | 0 | 7200 | 2
Busbar B > Voltage protections > Under-voltage 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Under-voltage 4 | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Voltage unbalance | AC setup | INT32 | Phase-phase |  |  |  |  | 4: Phase-phase, 3: Phase-neutral
Busbar B > Voltage protections > Voltage unbalance | Set point | FLOAT | 10 | % | 0 | 50 | 1
Busbar B > Voltage protections > Voltage unbalance | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Voltage unbalance | Delay | FLOAT | 10 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Voltage unbalance | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Voltage unbalance | Inhibit |  | No busbar B voltage, ACM wire break
Busbar B > Voltage protections > Positive sequence under-voltage | Set point | FLOAT | 70 | % | 10 | 110 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Positive sequence under-voltage | Delay | FLOAT | 0.04 | s | 0.02 | 7200 | 2
Busbar B > Voltage protections > Positive sequence under-voltage | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Positive sequence under-voltage | Inhibit |  | ACM wire break
Busbar B > Voltage protections > Negative sequence voltage | Set point | FLOAT | 5 | % | 1 | 100 | 1
Busbar B > Voltage protections > Negative sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Negative sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Negative sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Voltage protections > Zero sequence voltage | Set point | FLOAT | 5 | % | 0 | 100 | 1
Busbar B > Voltage protections > Zero sequence voltage | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Voltage protections > Zero sequence voltage | Delay | FLOAT | 0.5 | s | 0.1 | 7200 | 2
Busbar B > Voltage protections > Zero sequence voltage | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 1 | Set point | FLOAT | 105 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 1 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 2 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 2 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Over-frequency 3 | Set point | FLOAT | 110 | % | 100 | 130 | 1
Busbar B > Frequency protections > Over-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Over-frequency 3 | Delay | FLOAT | 8 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Over-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Set point | FLOAT | 96 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 1 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 1 | Delay | FLOAT | 10 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 1 | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 1 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 2 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 2 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 2 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 2 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 2 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 3 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 3 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 3 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 3 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 3 | Inhibit |  | ACM wire break
Busbar B > Frequency protections > Under-frequency 4 | Set point | FLOAT | 93 | % | 80 | 100 | 1
Busbar B > Frequency protections > Under-frequency 4 | Reset hysteresis | FLOAT | 0 | % | 0 | 20 | 1
Busbar B > Frequency protections > Under-frequency 4 | Delay | FLOAT | 5 | s | 0 | 7200 | 2
Busbar B > Frequency protections > Under-frequency 4 | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Frequency protections > Under-frequency 4 | Inhibit |  | ACM wire break
Busbar B > Additional protections > Vector shift | AC setup | INT32 | Busbar B |  |  |  |  | 34: Busbar B, 35: Busbar A
Busbar B > Additional protections > Vector shift | Vector shift select | INT32 | Individual phases |  |  |  |  | 0: Individual phases, 1: All phases
Busbar B > Additional protections > Vector shift | Set point | FLOAT | 10 | ° | 1 | 90 | 0
Busbar B > Additional protections > Vector shift | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Busbar B > Additional protections > ROCOF | AC setup | INT32 | Busbar B |  |  |  |  | 32: Busbar B, 33: Busbar A
Busbar B > Additional protections > ROCOF | ROCOF measurement half period | FLOAT | 8 |  | 8 | 20 | 0
Busbar B > Additional protections > ROCOF | ROCOF positive set point | FLOAT | 5 | Hz/s | 0.2 | 10 | 3
Busbar B > Additional protections > ROCOF | ROCOF negative set point | FLOAT | -5 | Hz/s | -10 | -0.2 | 3
Busbar B > Additional protections > ROCOF | Delay | FLOAT | 0 | s | 0 | 0.5 | 1
Busbar B > Additional protections > ROCOF | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker configuration > Configuration | Breaker type | INT32 | Pulse breaker |  |  |  |  | 0: Continuous breaker, 1: Pulse breaker, 2: Compact breaker
Breakers > Bus tie breaker configuration > Configuration | Pulse time ON | FLOAT | 1 | s | 0 | 60 | 1
Breakers > Bus tie breaker configuration > Configuration | Pulse time OFF | FLOAT | 0.5 | s | 0 | 10 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Spring load time | FLOAT | 1 | s | 0 | 30 | 1 |  | X
Breakers > Bus tie breaker configuration > Configuration | Open point (de-loading) | FLOAT | 5 | % | 1 | 20 | 1
Breakers > Bus tie breaker configuration > Blackout close | Blackout close | INT32 | Blackout close is OFF |  |  |  |  | 0: Blackout close is OFF, 1: Busbar A is dead, busbar B OK, 2: Busbar A OK, busbar B is dead, 3: One busbar is alive, 4: On
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync type | INT32 | Automatic |  |  |  |  | 0: Static, 1: Dynamic, 3: Automatic
Breakers > Bus tie breaker configuration > Synchronisation setting | Sync behavior | INT32 | Synchronise and close breaker |  |  |  |  | 0: Synchronise and close breaker, 1: Sync check (signal when in sync.) | X
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency min. | FLOAT | 0 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta frequency max. | FLOAT | 0.3 | Hz | -2 | 2 | 2
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage min. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Delta voltage max. | FLOAT | 5 | % | 2 | 10 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Breaker close time | FLOAT | 0.05 | s | 0.04 | 0.3 | 3
Breakers > Bus tie breaker configuration > Synchronisation setting | Phase window | FLOAT | 5 | ° | 0 | 45 | 1
Breakers > Bus tie breaker configuration > Synchronisation setting | Minimum time in phase window | FLOAT | 1 | s | 0.1 | 900 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Delay | FLOAT | 60 | s | 30 | 300 | 1
Breakers > Bus tie breaker monitoring > Synchronisation failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > De-load failure | Delay | FLOAT | 30 | s | 0 | 3600 | 1
Breakers > Bus tie breaker monitoring > De-load failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Vector mismatch | Set point | FLOAT | 20 | ° | 1 | 20 | 0
Breakers > Bus tie breaker monitoring > Vector mismatch | Delay | FLOAT | 10 | s | 5 | 60 | 1
Breakers > Bus tie breaker monitoring > Vector mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Opening failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Opening failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Closing failure | Delay | FLOAT | 2 | s | 0.1 | 60 | 1
Breakers > Bus tie breaker monitoring > Closing failure | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1
Breakers > Bus tie breaker monitoring > Position failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Configuration failure | Delay | FLOAT | 1 | s | 1 | 1 | 1 |  | X
Breakers > Bus tie breaker monitoring > Configuration failure | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > Bus tie breaker monitoring > Tripped (external) | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > Bus tie breaker monitoring > Short circuit | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Position failure | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Breakers > [User defined] > Feedback mismatch | Delay | FLOAT | 1 | s | 0.1 | 5 | 1 |  | X
Breakers > [User defined] > Feedback mismatch | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Modbus > Modbus communication timeout | Delay | FLOAT | 10 | s | 0.1 | 3600 | 1
Communication > Modbus > Modbus communication timeout | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Communication > DEIF network > DEIF network redundancy broken | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network has only one connection | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > DEIF network > DEIF network fork detected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 1 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > NTP server 2 not connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server(s) connected | Delay | FLOAT | 240 | s | 120 | 3600 | 1
Communication > NTP > No NTP server(s) connected | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 1 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 1 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > NTP server 2 not responding | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > NTP server 2 not responding | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > NTP > No NTP server time synchronisation | Delay | FLOAT | 60 | s | 10 | 3600 | 1
Communication > NTP > No NTP server time synchronisation | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-A bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > CAN bus > Bus off > CAN-B bus off | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus conflict | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Communication > Fieldbus > Fieldbus connection missing | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker | X
Local > Alarm horn > Horn 1 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 1 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1
Local > Alarm horn > Horn 1 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0
Local > Alarm horn > Horn 2 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 2 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 2 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Reset when new alarm | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > Alarm horn > Horn 3 | Minimum down time | FLOAT | 1 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | Minimum up time | FLOAT | 10 | s | 0 | 3600 | 1 |  | X
Local > Alarm horn > Horn 3 | De-energise when all alarms are acknowledged | INT32 | 0 |  | 0 | 1 | 0 |  | X
Local > 4th current input > Nominal settings > Nominal settings 1 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 2 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 3 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Nominal settings > Nominal settings 4 > Current (I4) | Nominal | FLOAT | 1804 | A | 1 | 9000 | 1
Local > 4th current input > Current transformer (I4) | Primary | FLOAT | 8800 | A | 5 | 9000 | 0
Local > 4th current input > Current transformer (I4) | Secondary | INT32 | 1 | A |  |  |  | 1: 1, 5: 5
Local > 4th current input > Earth inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Earth inverse time over-current | Limit | FLOAT | 10 | % | 2 | 200 | 1
Local > 4th current input > Earth inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Earth inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Earth inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Earth inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > 4th current input > Neutral inverse time over-current | Curve | INT32 | IEC inverse |  |  |  |  | 0: IEC inverse, 1: IEC very inverse, 2: IEC extremely inverse, 3: IEEE moderately inverse, 4: IEEE very inverse, 5: IEEE extremely inverse, 6: Custom characteristic
Local > 4th current input > Neutral inverse time over-current | Limit | FLOAT | 30 | % | 2 | 200 | 1
Local > 4th current input > Neutral inverse time over-current | Time multiplier setting | FLOAT | 1 |  | 0.01 | 100 | 2
Local > 4th current input > Neutral inverse time over-current | k | FLOAT | 0.14 | s | 0.001 | 120 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | c | FLOAT | 0 | s | 0 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | alpha | FLOAT | 0.02 | s | 0.001 | 60 | 3 |  | X
Local > 4th current input > Neutral inverse time over-current | Threshold | FLOAT | 1.1 |  | 1 | 1.3 | 3
Local > 4th current input > Neutral inverse time over-current | Action | INT32 | Trip bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > CustomLogic > Configuration | Enable | INT32 | 0 |  | 0 | 1 | 0
Local > CustomLogic > Configuration invalid | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > Monitoring > System not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > AC measurement filters > Primary AC measurements | Voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Active power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Reactive power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Apparent power | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Power factor and cos phi | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from voltage | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > AC measurement filters > Primary AC measurements | Frequency from current | INT32 | No filter |  |  |  |  | 0: No filter, 1: Averaged (200 ms), 2: Averaged (800 ms)
Local > Alive > Alive configuration | Duty cycle | FLOAT | 50 | % | 0 | 100 | 1
Local > Alive > Alive configuration | Period | FLOAT | 2 | s | 0.1 | 60 | 2
Local > Mode > Command mode | Selected mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control
Local > Mode > Command mode | Boot mode | INT32 | Local control |  |  |  |  | 0: Local control, 1: Remote control, 9999: Restore last
Local > Mode > Not under remote control | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Local > Mode > Not under remote control | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Local > Command sources > Active local sources | PICUS commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Modbus commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | I/O commands | INT32 | 0 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active local sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Command sources > Active remote sources | PICUS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Modbus commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | I/O commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CustomLogic commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | CODESYS commands | INT32 | 1 |  | 0 | 1 | 0
Local > Command sources > Active remote sources | Display commands | INT32 | 0 |  | -2147483648 | 2147483647 | 0
Local > Nominal settings > Controller nominal setting | Selection | INT32 | Nominal settings 1 |  |  |  |  | 0: Nominal settings 1, 1: Nominal settings 2, 2: Nominal settings 3, 3: Nominal settings 4
Local > Nominal settings > Controller nominal setting | Source | INT32 | Local |  |  |  |  | 0: Local, 1: Power management rules | X
System > Monitoring > Duplicate controller ID | Set point | FLOAT | 0 |  | 0 | 0 | 0 |  | X
System > Monitoring > Duplicate controller ID | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing all controllers | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing any controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Missing controllers | Range | INT32 | Section |  |  |  |  | 0: Section, 1: Plant
System > Monitoring > Blackout detection mismatch | Delay | FLOAT | 1 | s | 0 | 3600 | 1
System > Monitoring > Blackout detection mismatch | Action | INT32 | Block bus tie breaker |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Any mains breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Any bus tie breaker position failure | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Group alarm | Delay | FLOAT | 0 | s | 0 | 3600 | 1
System > Monitoring > Group alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Data loss from a controller | Set point | FLOAT | 5 | % | 0 | 100 | 1
System > Monitoring > Data loss from a controller | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss from a controller | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > Data loss on DEIF network | Set point | FLOAT | 2.5 | % | 0 | 100 | 1
System > Monitoring > Data loss on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > Data loss on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Monitoring > High traffic on DEIF network | Set point | FLOAT | 200 | % | 100 | 500 | 1
System > Monitoring > High traffic on DEIF network | Delay | FLOAT | 60 | s | 0 | 3600 | 1
System > Monitoring > High traffic on DEIF network | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
System > Plant > Plant | Active application | INT32 | [User defined] |  |  |  |  | 1: [User defined] | X
System > Application selector | Application selector | INT32 | LF |  |  |  |  | 800000: LF, 800002: MP, 800003: MS
Test functions > Lamp test > Lamp test | Activate | INT32 | 0 |  | 0 | 1 | 0
Test functions > Lamp test > Lamp test | Duration | FLOAT | 18 | s | 1 | 3600 | 0
Test functions > Lamp test > Lamp test | Colour cycle time | FLOAT | 3 | s | 1 | 3600 | 0
Test functions > Emulation > Emulation | Emulation active | INT32 | 0 |  | 0 | 1 | 0
Hardware > PSM3.1 1 > Diode compensation | Diode offset | FLOAT | 0 | V | 0 | 1 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Set point | FLOAT | 18 | V | 8 | 32 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > Low voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
Hardware > PSM3.1 1 > High voltage alarm | Set point | FLOAT | 30 | V | 12 | 36 | 1
Hardware > PSM3.1 1 > High voltage alarm | Delay | FLOAT | 1 | s | 0 | 3600 | 1
Hardware > PSM3.1 1 > High voltage alarm | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
CODESYS > Configuration > CODESYS | Enable | INT32 | 1 |  | 0 | 1 | 0
CODESYS > Monitoring > Application not OK | Startup time | FLOAT | 60 | s | 0 | 600 | 0
CODESYS > Monitoring > Application not OK | Delay | FLOAT | 1 | s | 0 | 300 | 2
CODESYS > Monitoring > Application not OK | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker
CODESYS > Monitoring > I/O config conflict | Action | INT32 | Warning |  |  |  |  | 0: Warning, 1: Block bus tie breaker, 3: Trip bus tie breaker

## BTB IO
ID | Path | Name | IO Type | Unit | Type | Minimum | Maximum | Decimals | Hidden
3306001 | Breakers > Bus tie breaker > Command | BTB static synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
3306002 | Breakers > Bus tie breaker > Command | BTB dynamic synchronisation | DI |  | BOOL_NUM | 0 | 1 | 0
20180028 | Breakers > Bus tie breaker > Command | BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180029 | Breakers > Bus tie breaker > Command | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180030 | Breakers > Bus tie breaker > Command | BTB open without de-loading | DI |  | BOOL_NUM | 0 | 1 | 0
20180031 | Breakers > Bus tie breaker > Command | Block BTB close | DI |  | BOOL_NUM | 0 | 1 | 0
20180000 | Breakers > Bus tie breaker > Feedback | BTB open | DI |  | BOOL_NUM | 0 | 1 | 0
20180001 | Breakers > Bus tie breaker > Feedback | BTB closed | DI |  | BOOL_NUM | 0 | 1 | 0
20180004 | Breakers > Bus tie breaker > Feedback | BTB is spring loaded | DI |  | BOOL_NUM | 0 | 1 | 0 | X
20180012 | Breakers > Bus tie breaker > Feedback | BTB short circuit | DI |  | BOOL_NUM | 0 | 1 | 0
110705000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110705001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110715001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110725001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110735001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110741001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110743001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110745001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110747001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110749001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110751001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110753001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110755001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110757001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110759001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110761001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110763001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110765001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110767001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110769001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771000 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
110771001 | Breakers > [User defined] > Feedback | [User defined] | DI |  | BOOL_NUM | 0 | 1 | 0 | X
60035000 | Alarm system > Command | Acknowledge all alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035001 | Alarm system > Command | Reset all latched alarms | DI |  | BOOL_NUM | 0 | 1 | 0
60035033 | Alarm system > Command | Reset horn | DI |  | BOOL_NUM | 0 | 1 | 0
60025000 | Alarm system > Inhibits | Activate inhibit 1 | DI |  | BOOL_NUM | 0 | 1 | 0
60025001 | Alarm system > Inhibits | Activate inhibit 2 | DI |  | BOOL_NUM | 0 | 1 | 0
60025002 | Alarm system > Inhibits | Activate inhibit 3 | DI |  | BOOL_NUM | 0 | 1 | 0
60035030 | Alarm system > Additional functions | Suppress alarm action | DI |  | BOOL_NUM | 0 | 1 | 0
110100012 | Alarm system > Additional functions | Group alarm | DI |  | BOOL_NUM | 0 | 1 | 0
60000505 | Local > Mode | Local control | DI |  | BOOL_NUM | 0 | 1 | 0
60000506 | Local > Mode | Remote control | DI |  | BOOL_NUM | 0 | 1 | 0
203000000 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000001 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000002 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000003 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000004 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000005 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000006 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000007 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000008 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000009 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000010 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000011 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000012 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000013 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000014 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000015 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000016 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000017 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000018 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000019 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000020 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000021 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000022 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000023 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000024 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000025 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000026 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000027 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000028 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000029 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000030 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000031 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000032 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000033 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000034 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000035 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000036 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000037 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000038 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000039 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000040 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000041 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000042 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000043 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000044 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000045 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000046 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000047 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000048 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000049 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000050 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000051 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000052 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000053 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000054 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000055 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000056 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000057 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000058 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000059 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000060 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000061 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000062 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000063 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000064 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000065 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000066 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000067 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000068 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000069 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000070 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000071 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000072 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000073 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000074 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000075 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000076 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000077 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000078 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203000079 | Local > CustomLogic > Inputs | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100000 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100001 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100002 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100003 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100004 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100005 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100006 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100007 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100008 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100009 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100010 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100011 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100012 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100013 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100014 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100015 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100016 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100017 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100018 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100019 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100020 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100021 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100022 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100023 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100024 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100025 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100026 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100027 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100028 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100029 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100030 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100031 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100032 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100033 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100034 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100035 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100036 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100037 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100038 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100039 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100040 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100041 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100042 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100043 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100044 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100045 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100046 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100047 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100048 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100049 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100050 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100051 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100052 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100053 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100054 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100055 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100056 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100057 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100058 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100059 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100060 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100061 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100062 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100063 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100064 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100065 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100066 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100067 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100068 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100069 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100070 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100071 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100072 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100073 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100074 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100075 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100076 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100077 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100078 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100079 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100080 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100081 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100082 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100083 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100084 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100085 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100086 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100087 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100088 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100089 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100090 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100091 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100092 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100093 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100094 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100095 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100096 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100097 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100098 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
203100099 | Local > CODESYS | Custom digital input | DI |  | BOOL_NUM | 0 | 1 | 0
40002000 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 | DI |  | BOOL_NUM | 0 | 1 | 0
40002001 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 | DI |  | BOOL_NUM | 0 | 1 | 0
40002002 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 | DI |  | BOOL_NUM | 0 | 1 | 0
40002003 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 | DI |  | BOOL_NUM | 0 | 1 | 0
140210000 | Test functions > Lamp test | Start lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
140210001 | Test functions > Lamp test | Stop lamp test | DI |  | BOOL_NUM | 0 | 1 | 0
40219000 | Busbar A > Production counters | Active energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219010 | Busbar A > Production counters | Reactive energy export pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219020 | Busbar A > Production counters | Active energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219030 | Busbar A > Production counters | Reactive energy import pulse | DO |  | BOOL_NUM | 0 | 1 | 0
40219040 | Busbar A > Production counters | Active energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40219050 | Busbar A > Production counters | Reactive energy difference pulse | DO |  | BOOL_NUM | 0 | 1 | 0 | X
40418002 | Busbar A > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40418003 | Busbar A > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
40408002 | Busbar B > State | Voltage and frequency OK | DO |  | BOOL_NUM | 0 | 1 | 0
40408003 | Busbar B > State | No voltage and frequency | DO |  | BOOL_NUM | 0 | 1 | 0
20180002 | Breakers > Bus tie breaker > Controls | BTB open | DO |  | BOOL_NUM | 0 | 1 | 0
20180003 | Breakers > Bus tie breaker > Controls | BTB close | DO |  | BOOL_NUM | 0 | 1 | 0
20180027 | Breakers > Bus tie breaker > Controls | BTB trip | DO |  | BOOL_NUM | 0 | 1 | 0
20180014 | Breakers > Bus tie breaker > State | BTB is open | DO |  | BOOL_NUM | 0 | 1 | 0
20180015 | Breakers > Bus tie breaker > State | BTB is closed | DO |  | BOOL_NUM | 0 | 1 | 0
20180024 | Breakers > Bus tie breaker > State | BTB is synchronising | DO |  | BOOL_NUM | 0 | 1 | 0
20180025 | Breakers > Bus tie breaker > State | BTB is de-loading | DO |  | BOOL_NUM | 0 | 1 | 0
20180026 | Breakers > Bus tie breaker > State | BTB is preparing | DO |  | BOOL_NUM | 0 | 1 | 0
110705002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110705003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110715003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110725003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110735003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110741003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110743003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110745003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110747003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110749003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110751003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110753003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110755003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110757003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110759003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110761003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110763003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110765003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110767003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110769003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771002 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
110771003 | Breakers > [User defined] > State | [User defined] | DO |  | BOOL_NUM | 0 | 1 | 0 | X
60035005 | Alarm system > State | Any warning alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035006 | Alarm system > State | Any block alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035012 | Alarm system > State | Any BTB trip alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035014 | Alarm system > State | Any alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035015 | Alarm system > State | Any unacknowledged alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035016 | Alarm system > State | Any latched alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035017 | Alarm system > State | Any shelved alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60035018 | Alarm system > State | Any out of service alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165000 | Alarm system > Severity | Any high severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165001 | Alarm system > Severity | Any medium severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60165002 | Alarm system > Severity | Any low severity alarm | DO |  | BOOL_NUM | 0 | 1 | 0
60010040 | Local > Alarm horn | Horn 1 | DO |  | BOOL_NUM | 0 | 1 | 0
60010140 | Local > Alarm horn | Horn 2 | DO |  | BOOL_NUM | 0 | 1 | 0
60010240 | Local > Alarm horn | Horn 3 | DO |  | BOOL_NUM | 0 | 1 | 0
60010300 | Local > System OK | Status OK | DO |  | BOOL_NUM | 0 | 1 | 0
60000507 | Local > Mode | Under local control | DO |  | BOOL_NUM | 0 | 1 | 0
60000508 | Local > Mode | Under remote control | DO |  | BOOL_NUM | 0 | 1 | 0
203001000 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001001 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001002 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001003 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001004 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001005 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001006 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001007 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001008 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001009 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001010 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001011 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001012 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001013 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001014 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001015 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001016 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001017 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001018 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001019 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001020 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001021 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001022 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001023 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001024 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001025 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001026 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001027 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001028 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001029 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001030 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001031 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001032 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001033 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001034 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001035 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001036 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001037 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001038 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001039 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001040 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001041 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001042 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001043 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001044 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001045 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001046 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001047 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001048 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001049 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001050 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001051 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001052 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001053 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001054 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001055 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001056 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001057 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001058 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001059 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001060 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001061 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001062 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001063 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001064 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001065 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001066 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001067 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001068 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001069 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001070 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001071 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001072 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001073 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001074 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001075 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001076 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001077 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001078 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203001079 | Local > CustomLogic > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
60065000 | Local > CustomLogic > State | Is enabled | DO |  | BOOL_NUM | 0 | 1 | 0
203101000 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101001 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101002 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101003 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101004 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101005 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101006 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101007 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101008 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101009 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101010 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101011 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101012 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101013 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101014 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101015 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101016 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101017 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101018 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101019 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101020 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101021 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101022 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101023 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101024 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101025 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101026 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101027 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101028 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101029 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101030 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101031 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101032 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101033 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101034 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101035 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101036 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101037 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101038 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101039 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101040 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101041 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101042 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101043 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101044 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101045 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101046 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101047 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101048 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101049 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101050 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101051 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101052 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101053 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101054 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101055 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101056 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101057 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101058 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101059 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101060 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101061 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101062 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101063 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101064 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101065 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101066 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101067 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101068 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101069 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101070 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101071 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101072 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101073 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101074 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101075 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101076 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101077 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101078 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101079 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101080 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101081 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101082 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101083 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101084 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101085 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101086 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101087 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101088 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101089 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101090 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101091 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101092 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101093 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101094 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101095 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101096 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101097 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101098 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
203101099 | Local > CODESYS > Outputs | Custom digital output | DO |  | BOOL_NUM | 0 | 1 | 0
160005000 | Local > CODESYS > State | CODESYS application OK | DO |  | BOOL_NUM | 0 | 1 | 0
60010350 | Local > Alive | Alive | DO |  | BOOL_NUM | 0 | 1 | 0
40002004 | Local > Nominal settings > Controller nominal setting | Nominal settings 1 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002005 | Local > Nominal settings > Controller nominal setting | Nominal settings 2 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002006 | Local > Nominal settings > Controller nominal setting | Nominal settings 3 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40002007 | Local > Nominal settings > Controller nominal setting | Nominal settings 4 selected | DO |  | BOOL_NUM | 0 | 1 | 0
40140000 | Busbar B > Analogue | P total | AI | kW | FLOAT | 0 | 1500000 | 1 | X
40140001 | Busbar B > Analogue | Q total | AI | kvar | FLOAT | 0 | 1500000 | 1 | X
40140002 | Busbar B > Analogue | S total | AI | kVA | FLOAT | 0 | 1500000 | 1 | X
203002000 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002001 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002002 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002003 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002004 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002005 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002006 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002007 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002008 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002009 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002010 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002011 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002012 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002013 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002014 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002015 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002016 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002017 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002018 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203002019 | Local > CustomLogic > Inputs | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102000 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102001 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102002 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102003 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102004 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102005 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102006 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102007 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102008 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102009 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102010 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102011 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102012 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102013 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102014 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102015 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102016 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102017 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102018 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102019 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102020 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102021 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102022 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102023 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102024 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102025 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102026 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102027 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102028 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102029 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102030 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102031 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102032 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102033 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102034 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102035 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102036 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102037 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102038 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102039 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102040 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102041 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102042 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102043 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102044 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102045 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102046 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102047 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102048 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102049 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102050 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102051 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102052 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102053 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102054 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102055 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102056 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102057 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102058 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102059 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102060 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102061 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102062 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102063 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102064 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102065 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102066 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102067 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102068 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102069 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102070 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102071 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102072 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102073 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102074 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102075 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102076 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102077 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102078 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102079 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102080 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102081 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102082 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102083 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102084 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102085 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102086 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102087 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102088 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102089 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102090 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102091 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102092 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102093 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102094 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102095 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102096 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102097 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102098 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203102099 | Local > CODESYS | Custom analogue input | AI |  | FLOAT | 0 | 0 | 0
203600000 | Thermocouple cold junction | Compensation 1 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600001 | Thermocouple cold junction | Compensation 2 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600002 | Thermocouple cold junction | Compensation 3 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600003 | Thermocouple cold junction | Compensation 4 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600004 | Thermocouple cold junction | Compensation 5 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600005 | Thermocouple cold junction | Compensation 6 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600006 | Thermocouple cold junction | Compensation 7 | AI | °C | FLOAT | -50 | 200 | 0 | X
203600007 | Thermocouple cold junction | Compensation 8 | AI | °C | FLOAT | -50 | 200 | 0 | X
40110000 | Busbar A > Voltage (V) | Busbar A ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40110001 | Busbar A > Voltage (V) | Busbar A ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40110002 | Busbar A > Voltage (V) | Busbar A ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40110003 | Busbar A > Voltage (V) | Busbar A ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40110004 | Busbar A > Voltage (V) | Busbar A ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40110005 | Busbar A > Voltage (V) | Busbar A ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40110006 | Busbar A > Voltage (V) | Busbar A ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110007 | Busbar A > Voltage (V) | Busbar A ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40110008 | Busbar A > Voltage (V) | Busbar A ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40110009 | Busbar A > Voltage (V) | Busbar A ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40110010 | Busbar A > Voltage (V) | Busbar A ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40110011 | Busbar A > Voltage (V) | Busbar A ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40110012 | Busbar A > Voltage (V) | Busbar A ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40110057 | Busbar A > Voltage (V) | Busbar A ¦ Positive sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110059 | Busbar A > Voltage (V) | Busbar A ¦ Negative sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110061 | Busbar A > Voltage (V) | Busbar A ¦ Zero sequence | AO | V | FLOAT | 0 | 1500000 | 1
40110013 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110014 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110015 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110016 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110017 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110072 | Busbar A > Frequency (f) (from voltage) | Busbar A ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110018 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110019 | Busbar A > Frequency (f) (from current) | Busbar A ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40110034 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110035 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110036 | Busbar A > Frequency (f) (from current) | Busbar A ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40110026 | Busbar A > Current (I) | Busbar A ¦ L1 | AO | A | FLOAT | 0 | 1500000 | 1
40110027 | Busbar A > Current (I) | Busbar A ¦ L2 | AO | A | FLOAT | 0 | 1500000 | 1
40110028 | Busbar A > Current (I) | Busbar A ¦ L3 | AO | A | FLOAT | 0 | 1500000 | 1
40110029 | Busbar A > Current (I) | Busbar A ¦ N | AO | A | FLOAT | 0 | 1500000 | 1
40110030 | Busbar A > Current (I) | Busbar A ¦ Min. | AO | A | FLOAT | 0 | 1500000 | 1
40110031 | Busbar A > Current (I) | Busbar A ¦ Max. | AO | A | FLOAT | 0 | 1500000 | 1
40110032 | Busbar A > Current (I) | Busbar A ¦ Unbalanced nominal | AO | A | FLOAT | 0 | 1500000 | 1
40110033 | Busbar A > Current (I) | Busbar A ¦ Unbalanced average | AO | A | FLOAT | 0 | 1500000 | 1
40110058 | Busbar A > Current (I) | Busbar A ¦ Positive sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110060 | Busbar A > Current (I) | Busbar A ¦ Negative sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110062 | Busbar A > Current (I) | Busbar A ¦ Zero sequence | AO | A | FLOAT | 0 | 1500000 | 1
40110037 | Busbar A > Power (P) | Busbar A ¦ L1 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110038 | Busbar A > Power (P) | Busbar A ¦ L2 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110039 | Busbar A > Power (P) | Busbar A ¦ L3 | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110040 | Busbar A > Power (P) | Busbar A ¦ Min. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110041 | Busbar A > Power (P) | Busbar A ¦ Max. | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110042 | Busbar A > Power (P) | Busbar A ¦ Total | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110063 | Busbar A > Power (P) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110066 | Busbar A > Power (P) | Busbar A ¦ Available | AO | kW | FLOAT | -1500000 | 1500000 | 1
40110069 | Busbar A > Power (P) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110043 | Busbar A > Reactive power (Q) | Busbar A ¦ L1 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110044 | Busbar A > Reactive power (Q) | Busbar A ¦ L2 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110045 | Busbar A > Reactive power (Q) | Busbar A ¦ L3 | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110046 | Busbar A > Reactive power (Q) | Busbar A ¦ Min. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110047 | Busbar A > Reactive power (Q) | Busbar A ¦ Max. | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110048 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110064 | Busbar A > Reactive power (Q) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110067 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | kvar | FLOAT | -1500000 | 1500000 | 1
40110070 | Busbar A > Reactive power (Q) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110049 | Busbar A > Apparent power (S) | Busbar A ¦ L1 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110050 | Busbar A > Apparent power (S) | Busbar A ¦ L2 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110051 | Busbar A > Apparent power (S) | Busbar A ¦ L3 | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110052 | Busbar A > Apparent power (S) | Busbar A ¦ Min. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110053 | Busbar A > Apparent power (S) | Busbar A ¦ Max. | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110054 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110065 | Busbar A > Apparent power (S) | Busbar A ¦ Total | AO | % | FLOAT | 0 | 100 | 0
40110068 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | kVA | FLOAT | -1500000 | 1500000 | 1
40110071 | Busbar A > Apparent power (S) | Busbar A ¦ Available | AO | % | FLOAT | -100 | 100 | 0
40110055 | Busbar A > Power factor (PF) | Busbar A ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40110056 | Busbar A > Power factor (PF) | Busbar A ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40110020 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40110021 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40110022 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40110023 | Busbar A > Phase angle | Busbar A ¦ Phase angle L1 | AO | ° | FLOAT | -180 | 180 | 1
40110024 | Busbar A > Phase angle | Busbar A ¦ Phase angle L2 | AO | ° | FLOAT | -180 | 180 | 1
40110025 | Busbar A > Phase angle | Busbar A ¦ Phase angle L3 | AO | ° | FLOAT | -180 | 180 | 1
40100000 | Busbar B > Voltage (V) | Busbar B ¦ L1-N | AO | V | FLOAT | 0 | 1500000 | 1
40100001 | Busbar B > Voltage (V) | Busbar B ¦ L2-N | AO | V | FLOAT | 0 | 1500000 | 1
40100002 | Busbar B > Voltage (V) | Busbar B ¦ L3-N | AO | V | FLOAT | 0 | 1500000 | 1
40100003 | Busbar B > Voltage (V) | Busbar B ¦ N | AO | V | FLOAT | 0 | 1500000 | 1
40100004 | Busbar B > Voltage (V) | Busbar B ¦ L-N min. | AO | V | FLOAT | 0 | 1500000 | 1
40100005 | Busbar B > Voltage (V) | Busbar B ¦ L-N max. | AO | V | FLOAT | 0 | 1500000 | 1
40100006 | Busbar B > Voltage (V) | Busbar B ¦ L-N unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100007 | Busbar B > Voltage (V) | Busbar B ¦ L1-L2 | AO | V | FLOAT | 0 | 1500000 | 1
40100008 | Busbar B > Voltage (V) | Busbar B ¦ L2-L3 | AO | V | FLOAT | 0 | 1500000 | 1
40100009 | Busbar B > Voltage (V) | Busbar B ¦ L3-L1 | AO | V | FLOAT | 0 | 1500000 | 1
40100010 | Busbar B > Voltage (V) | Busbar B ¦ L-L min. | AO | V | FLOAT | 0 | 1500000 | 1
40100011 | Busbar B > Voltage (V) | Busbar B ¦ L-L max. | AO | V | FLOAT | 0 | 1500000 | 1
40100012 | Busbar B > Voltage (V) | Busbar B ¦ L-L unbalanced | AO | V | FLOAT | 0 | 1500000 | 1
40100021 | Busbar B > Voltage (V) | Busbar B ¦ Positive sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100022 | Busbar B > Voltage (V) | Busbar B ¦ Negative sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100023 | Busbar B > Voltage (V) | Busbar B ¦ Zero sequence | AO | V | FLOAT | -1500000 | 1500000 | 1
40100013 | Busbar B > Frequency (f) | Busbar B ¦ L1 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100014 | Busbar B > Frequency (f) | Busbar B ¦ L2 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100015 | Busbar B > Frequency (f) | Busbar B ¦ L3 | AO | Hz | FLOAT | 0 | 1500000 | 2
40100016 | Busbar B > Frequency (f) | Busbar B ¦ Min. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100017 | Busbar B > Frequency (f) | Busbar B ¦ Max. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100033 | Busbar B > Frequency (f) | Busbar B ¦ Avg. | AO | Hz | FLOAT | 0 | 1500000 | 2
40100018 | Busbar B > Phase angle | Busbar B ¦ Phase angle L1-L2 | AO | ° | FLOAT | -180 | 180 | 1
40100019 | Busbar B > Phase angle | Busbar B ¦ Phase angle L2-L3 | AO | ° | FLOAT | -180 | 180 | 1
40100020 | Busbar B > Phase angle | Busbar B ¦ Phase angle L3-L1 | AO | ° | FLOAT | -180 | 180 | 1
40130000 | Local > 4th current input > Current (I) | L4 | AO | A | FLOAT | 0 | 1500000 | 1
40130004 | Local > 4th current input > Frequency (f) | L4 | AO | Hz | FLOAT | 0 | 1500000 | 2
40130001 | Local > 4th current input > Power (P) | L4 | AO | kW | FLOAT | 0 | 1500000 | 1
40130002 | Local > 4th current input > Reactive power (Q) | L4 | AO | kvar | FLOAT | 0 | 1500000 | 1
40130003 | Local > 4th current input > Apparent power (S) | L4 | AO | kVA | FLOAT | 0 | 1500000 | 1
40130009 | Local > 4th current input > Power factor (PF) | L4 ¦ cos phi | AO |  | FLOAT | -1 | 1 | 4
40130010 | Local > 4th current input > Power factor (PF) | L4 ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
40130008 | Local > 4th current input > Phase angle | L4 | AO | ° | FLOAT | -180 | 180 | 1
203003000 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003001 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003002 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003003 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003004 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003005 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003006 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003007 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003008 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003009 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003010 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003011 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003012 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003013 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003014 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003015 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003016 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003017 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003018 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203003019 | Local > CustomLogic > Outputs | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103000 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103001 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103002 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103003 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103004 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103005 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103006 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103007 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103008 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103009 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103010 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103011 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103012 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103013 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103014 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103015 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103016 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103017 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103018 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103019 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103020 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103021 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103022 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103023 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103024 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103025 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103026 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103027 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103028 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103029 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103030 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103031 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103032 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103033 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103034 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103035 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103036 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103037 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103038 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103039 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103040 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103041 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103042 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103043 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103044 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103045 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103046 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103047 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103048 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103049 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103050 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103051 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103052 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103053 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103054 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103055 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103056 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103057 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103058 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103059 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103060 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103061 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103062 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103063 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103064 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103065 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103066 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103067 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103068 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103069 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103070 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103071 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103072 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103073 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103074 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103075 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103076 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103077 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103078 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103079 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103080 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103081 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103082 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103083 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103084 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103085 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103086 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103087 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103088 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103089 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103090 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103091 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103092 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103093 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103094 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103095 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103096 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103097 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103098 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
203103099 | Local > CODESYS | Custom analogue output | AO |  | FLOAT | 0 | 0 | 0
40002008 | Local > Nominal settings > Controller nominal setting | Nominal setting selected | AO |  | INT32 | 0 | 3 | 0
110100210 | System power management > Monitoring > Plant | Plant ¦ P produced | AO | kW | FLOAT | 0 | 0 | 0
110100211 | System power management > Monitoring > Plant | Plant ¦ Q produced | AO | kvar | FLOAT | 0 | 0 | 0
110100212 | System power management > Monitoring > Plant | Plant ¦ S produced | AO | kVA | FLOAT | 0 | 0 | 0
110100213 | System power management > Monitoring > Plant | Plant ¦ Power factor | AO |  | FLOAT | 0 | 1 | 4
100041000 | Hardware > Power supply > PSM3.1 1 | PSM3.1 1 supply voltage | AO | V | FLOAT | 0 | 60 | 1
82000000 | Hardware > CPU > Load | Currently | AO | % | FLOAT | 0 | 100 | 1
82000010 | Hardware > CPU > Load | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000020 | Hardware > CPU > Load | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000030 | Hardware > CPU > Load | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000040 | Hardware > CPU > Core 1 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000050 | Hardware > CPU > Core 1 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000060 | Hardware > CPU > Core 1 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000070 | Hardware > CPU > Core 1 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000080 | Hardware > CPU > Core 2 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000090 | Hardware > CPU > Core 2 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000100 | Hardware > CPU > Core 2 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000110 | Hardware > CPU > Core 2 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000120 | Hardware > CPU > Core 3 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000130 | Hardware > CPU > Core 3 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000140 | Hardware > CPU > Core 3 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000150 | Hardware > CPU > Core 3 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1
82000160 | Hardware > CPU > Core 4 | Currently | AO | % | FLOAT | 0 | 100 | 1
82000170 | Hardware > CPU > Core 4 | Average over 10 seconds | AO | % | FLOAT | 0 | 100 | 1
82000180 | Hardware > CPU > Core 4 | Average over 1 minute | AO | % | FLOAT | 0 | 100 | 1
82000190 | Hardware > CPU > Core 4 | Average over 10 minutes | AO | % | FLOAT | 0 | 100 | 1